## Adaire
Sheet Last Modified: | 2021-03-22
School: | Alexander Adaire Elementary School |  |  | House Fan Abated/Final Report | [5 empty] | Min | 0
Vendor: | Chadwick | Devine | Devine Retest | [6 empty] | Max | 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | Average | 1.5172
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | cu-ft 8 ft ceiling | AUC | Cert Level
- | Auditorium | 2417 | 161 |  | 3234 | 73 | 73 | Air Handling Unit | 25872 | 5.6053 | 2
- | Gym/Cafeteria | 322 | 21 |  | 3432 | 78 | 21 | Air Handling Unit | 27456 | 0.70367 | 0
- | Main Ofiice | 161 | 10 |  | 468 | 10 | 10 | Unit Ventilator | 3744 | 2.5801 | 1
100 | Classroom | 452 | 30 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.5312 | 1
101 | Classroom | 480 | 32 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.75 | 1
102 | Classroom | 509 | 33 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.9766 | 1
103 | Classroom | 409 | 27 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.1953 | 1
104 | Classroom | 514 | 34 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.0156 | 2
105 | Classroom | 523 | 34 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.0859 | 2
106 | Classroom | 125 | 8 | Yes | 782 | 17 | 17 | Unit Ventilator | 6256 | 1.1988 | 1
107 | Classroom | 272 | 18 |  | 380 | 8 | 8 | Unit Ventilator | 3040 | 5.3684 | 2
108 | Faculty Room | 0 | 0 |  | 104 | 2 | 0 | Unit Ventilator | 832 | 0 | 0
109 | Classroom | 485 | 32 |  | 1470 | 33 | 32 | Unit Ventilator | 11760 | 2.4745 | 1
200 | Classroom | 546 | 36 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 4.4901 | 2
201 | Classroom | 607 | 40 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 4.9918 | 2
202 | Classroom | 613 | 40 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 4.9119 | 2
203 | Library | 593 | 39 |  | 1080 | 24 | 24 | Unit Ventilator | 8640 | 4.1181 | 2
204 | Classroom | 480 | 32 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 3.9474 | 1
205 | Classroom | 182 | 12 | Yes | 960 | 21 | 21 | Unit Ventilator | 7680 | 1.4219 | 1
206 | Classroom | 317 | 21 |  | 984 | 22 | 21 | Unit Ventilator | 7872 | 2.4162 | 1
207 | Classroom | 798 | 53 |  | 456 | 10 | 10 | Unit Ventilator | 3648 | 13.125 | 3
208 | Classroom | 577 | 38 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.5078 | 2
209 | Classroom | 458 | 30 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.5781 | 1
210 | Classroom | 519 | 34 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.0547 | 2
211 | Classroom | 534 | 35 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 3.9732 | 1
212 | Classroom | 1568 | 104 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 12.25 | 3
214 | Classroom | 340 | 22 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 2.6562 | 1
216 | Classroom | 617 | 41 |  | 456 | 10 | 10 | Unit Ventilator | 3648 | 10.148 | 3
218 | Classroom | 424 | 28 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 4.0665 | 2
1.5172

## Allen, Ethan
Sheet Last Modified: | 2021-03-24
School: | Ethan Allen Elementary-Middle School | [8 empty] | Min | 0
Vendor: | Devine | Devine Retest | [7 empty] | Max | 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | Average | 1.6667
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | cu-ft 8 ft ceiling | AUC | Cert Level
B1 | Classroom | 545 | 36 |  | 736 | 16 | 16 | House Fan | 5888 | 5.5537 | 2
B2 | Classroom | 708 | 47 |  | 352 | 8 | 8 | House Fan | 2816 | 15.0852 | 3
B3 | Classroom | 421 | 28 |  | 506 | 11 | 11 | House Fan | 4048 | 6.2401 | 2
B4 | Classroom | 453 | 30 |  | 452 | 10 | 10 | House Fan | 3616 | 7.5166 | 2
- | Auditorium | 2183 | 145 |  | 3432 | 78 | 78 | House Fan | 27456 | 4.7705 | 2
- | Boys Basement Restroom | 130 | 8 |  | 383 | 8 | 8 | AC Bathroom | 3064 | 2.5457 | 1
- | Girls Basement Restroom | 787 | 52 |  | 524 | 11 | 11 | AC Bathroom | 4192 | 11.2643 | 3
101 | Classroom | 600 | 40 |  | 920 | 20 | 20 | House Fan | 7360 | 4.8913 | 2
102 | Classroom | 405 | 27 |  | 690 | 15 | 15 | House Fan | 5520 | 4.4022 | 2
103 | Classroom | 190 | 12 | Yes | 736 | 16 | 16 | House Fan | 5888 | 1.9361 | 1
104 | Classroom | 505 | 33 |  | 690 | 15 | 15 | House Fan | 5520 | 5.4891 | 2
105 | Classroom | 1216 | 81 |  | 690 | 15 | 15 | House Fan | 5520 | 13.2174 | 3
106 | Classroom | 1055 | 70 |  | 690 | 15 | 15 | House Fan | 5520 | 11.4674 | 3
107 | Classroom | 1312 | 87 |  | 690 | 15 | 15 | House Fan | 5520 | 14.2609 | 3
108 | Classroom | 1307 | 87 |  | 736 | 16 | 16 | House Fan | 5888 | 13.3186 | 3
109 | Classroom | 874 | 58 |  | 690 | 15 | 15 | House Fan | 5520 | 9.5 | 2
110 | Classroom | 1349 | 89 |  | 736 | 16 | 16 | House Fan | 5888 | 13.7466 | 3
210 | Classroom | 1375 | 91 |  | 736 | 16 | 16 | House Fan | 5888 | 14.0115 | 3
202 | Classroom | 298 | 19 |  | 690 | 15 | 15 | House Fan | 5520 | 3.2391 | 1
203 | Classroom | 209 | 13 |  | 736 | 16 | 13 | House Fan | 5888 | 2.1298 | 1
204 | Classroom | 373 | 24 |  | 690 | 15 | 15 | House Fan | 5520 | 4.0543 | 2
205 | Classroom | 574 | 38 |  | 690 | 15 | 15 | House Fan | 5520 | 6.2391 | 2
206 | Classroom | 580 | 38 |  | 690 | 15 | 15 | House Fan | 5520 | 6.3043 | 2
207 | Classroom | 919 | 61 |  | 690 | 15 | 15 | House Fan | 5520 | 9.9891 | 2
208 | Classroom | 1175 | 78 |  | 736 | 16 | 16 | House Fan | 5888 | 11.9735 | 3
209 | Classroom | 753 | 50 |  | 690 | 15 | 15 | House Fan | 5520 | 8.1848 | 2
210 | Classroom | 1638 | 109 |  | 736 | 16 | 16 | House Fan | 5888 | 16.6916 | 3
214 | Classroom |  | 0 | Yes | 341 | 7 | 7 | House Fan | 2728 | 0 | 0
301 | Classroom | 880 | 58 |  | 736 | 16 | 16 | House Fan | 5888 | 8.9674 | 2
302 | Classroom | 319 | 21 |  | 690 | 15 | 15 | House Fan | 5520 | 3.4674 | 1
303 | Classroom | 74 | 4 |  | 736 | 16 | 4 | House Fan | 5888 | 0.75408 | 0
304 | Classroom | 141 | 9 |  | 690 | 15 | 9 | House Fan | 5520 | 1.5326 | 1
305 | Classroom | 151 | 10 |  | 690 | 15 | 10 | House Fan | 5520 | 1.6413 | 1
306 | Classroom | 268 | 17 |  | 690 | 15 | 15 | House Fan | 5520 | 2.913 | 1
307 | Classroom | 921 | 61 |  | 690 | 15 | 15 | House Fan | 5520 | 10.0109 | 3
308 | Classroom | 520 | 34 |  | 736 | 16 | 16 | House Fan | 5888 | 5.2989 | 2
309 | Classroom | 121 | 8 |  | 690 | 15 | 8 | House Fan | 5520 | 1.3152 | 1
310 | Classroom | 290 | 19 |  | 736 | 16 | 16 | House Fan | 5888 | 2.9552 | 1
314 | Classroom | 421 | 28 |  | 720 | 16 | 16 | House Fan | 5760 | 4.3854 | 2
- | Main Office |  | 0 | Yes | 309 | 7 | 7 | House Fan | 2472 | 0 | 0
- | Prinicipal Office |  | 0 | Yes | 177 | 4 | 4 | House Fan | 1416 | 0 | 0
- | Nurse Office |  | 0 | Yes | 186 | 4 | 4 | House Fan | 1488 | 0 | 0
- | Conselor Office |  | 0 | Yes | 177 | 4 | 4 | House Fan | 1416 | 0 | 0
- | Pyschologist Office |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | 0 | 0
- | Gym |  | 0 | Yes | 3422 | 77 | 77 | Hydroxyl Unit | 27376 | 0 | 0

## Allen, Ethel
Sheet Last Modified: | 2021-03-16
School: | Dr. Ethel Allen Elementary School | [8 empty] | Min | 0
Vendor: | Chadwick | Chadwick Retest | [7 empty] | Max | 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | Average | 0.45161
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | cu-ft 8 ft ceiling | AUC | Cert Level
101-A | Classroom | 528 | 35 |  | 896 | 20 | 20 | Unit Ventilator | 7168 | 4.4196 | 2
101-B | Classroom | 100 | 6 |  | 1036 | 23 | 6 | Unit Ventilator | 8288 | 0.72394 | 0
102-A | Classroom | 70 | 4 |  | 1110 | 25 | 4 | Unit Ventilator | 8880 | 0.47297 | 0
102-B | Classroom | 485 | 32 |  | 1110 | 25 | 25 | Unit Ventilator | 8880 | 3.277 | 1
102-C | Classroom | 0 | 0 |  | 1110 | 25 | 0 | Unit Ventilator | 8880 | 0 | 0
102-D | Classroom |  | 0 |  | 1110 | 25 | 0 | Unit Ventilator | 8880 | 0 | 0
103 | Classroom | 1233 | 82 | Yes | 2277 | 51 | 51 | Unit Ventilator | 18216 | 4.0613 | 2
103-A | Classroom | 76 | 5 |  |  | 0 | 0 | Unit Ventilator | 0
104 | Classroom | 419 | 27 |  | 1260 | 28 | 27 | Unit Ventilator | 10080 | 2.494 | 1
105 | Classroom | 472 | 31 |  | 1260 | 28 | 28 | Unit Ventilator | 10080 | 2.8095 | 1
106 | Classroom | 152 | 10 |  | 1184 | 26 | 10 | Unit Ventilator | 9472 | 0.96284 | 0
107 | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | 0 | 0
109 | Classroom | 172 | 11 | Yes | 1260 | 28 | 28 | Unit Ventilator | 10080 | 1.0238 | 1
110 | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | 0 | 0
112 | Classroom | 29 | 1 |  | 1056 | 24 | 1 | Unit Ventilator | 8448 | 0.20597 | 0
113 | Classroom | 26 | 1 |  | 1056 | 24 | 1 | Unit Ventilator | 8448 | 0.18466 | 0
114 | Classroom | 380 | 25 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.6989 | 1
200 | Classroom | 511 | 34 |  | 1500 | 34 | 34 | Unit Ventilator | 12000 | 2.555 | 1
200C | Classroom | 0 | 0 | Yes | 784 | 17 | 17 | Unit Ventilator | 6272 | 0 | 0
201B | Classroom |  | 0 |  | 840 | 19 | 0 | Unit Ventilator | 6720 | 0 | 0
202 | Classroom | 367 | 24 |  | 983 | 22 | 22 | Unit Ventilator | 7864 | 2.8001 | 1
202 | Classroom |  | 0 |  |  | 0 | 0 | Unit Ventilator | 0
203A | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | 0 | 0
203B | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | 0 | 0
203C | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | 0 | 0
203D | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | 0 | 0
204 | Classroom | 525 | 35 |  | 980 | 22 | 22 | Unit Ventilator | 7840 | 4.0179 | 2
206 | Classroom | 194 | 12 |  | 1200 | 27 | 12 | Unit Ventilator | 9600 | 1.2125 | 1
206 | Classroom | 170 | 11 |  |  | 0 | 0 | Unit Ventilator | 0
207A | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | 0 | 0
207B | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | 0 | 0
208A | Classroom | 108 | 7 |  | 1260 | 28 | 7 | Unit Ventilator | 10080 | 0.64286 | 0
208B | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | 0 | 0
208C | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | 0 | 0
209 | Classroom | 907 | 60 |  |  | 0 | 0 | Unit Ventilator | 0

## Anderson
Sheet Last Modified: | 2021-04-29
School: | Add B. Anderson Elementary School | [8 empty] | Min | 0
Vendor: | Devine Brothers | Part 2 | [7 empty] | Max | 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | Average | 1.0238
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | cu-ft 8 ft ceiling | AUC | Cert Level
- | Auditorium | 5840 | 389 |  | 2589 | 58 | 58 | Air Handling Unit | 20712 | 16.9177 | 3
- | Gym | 2392 | 159 |  | 2200 | 50 | 50 | Air Handling Unit | 17600 | 8.1545 | 2
- | Main Office | 84 | 5 | Yes | 451 | 10 | 10 | Unit Ventilator | 3608 | 1.3969 | 1
- | Principal's Office |  | 0 | Yes | 350 | 7 | 7 | Convector | 2800 | 0 | 0
- | Nurse's Office |  | 0 | Yes | 350 | 7 | 7 | Convector | 2800 | 0 | 0
- | Stage | 2534 | 168 |  | 1008 | 22 | 22 | Air Handling Unit | 8064 | 18.8542 | 3
100 | Classroom | 281 | 18 |  | 467 | 10 | 10 | Unit Ventilator | 3736 | 4.5128 | 2
101 | Classroom | 32 | 2 |  | 355 | 8 | 2 | Unit Ventilator | 2840 | 0.67606 | 0
102 | Classroom | 102 | 6 | Yes | 540 | 12 | 12 | Unit Ventilator | 4320 | 1.4167 | 1
103 | Classroom | 40 | 2 | Yes | 628 | 14 | 14 | Unit Ventilator | 5024 | 0.47771 | 0
104 | Classroom | 287 | 19 |  | 395 | 8 | 8 | Unit Ventilator | 3160 | 5.4494 | 2
105 | Classroom | 295 | 19 |  | 521 | 11 | 11 | Unit Ventilator | 4168 | 4.2466 | 2
106 | Classroom | 290 | 19 |  | 446 | 10 | 10 | Unit Ventilator | 3568 | 4.8767 | 2
108 | Classroom | 283 | 18 |  | 405 | 9 | 9 | Unit Ventilator | 3240 | 5.2407 | 2
200 | Classroom | 82 | 5 | Yes | 476 | 10 | 10 | Unit Ventilator | 3808 | 1.292 | 1
201 | Classroom | 128 | 8 | Yes | 627 | 14 | 14 | Unit Ventilator | 5016 | 1.5311 | 1
202 | Classroom | 408 | 27 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 5.3125 | 2
204 | Classroom | 323 | 21 |  | 683 | 15 | 15 | Unit Ventilator | 5464 | 3.5469 | 1
205 | Classroom | 80 | 5 | Yes | 658 | 14 | 14 | Unit Ventilator | 5264 | 0.91185 | 0
206 | Classroom | 329 | 21 |  | 637 | 14 | 14 | Unit Ventilator | 5096 | 3.8736 | 1
207 | Classroom | 82 | 5 | Yes | 587 | 13 | 13 | Unit Ventilator | 4696 | 1.0477 | 1
208 | Classroom | 129 | 8 | Yes | 720 | 16 | 16 | Unit Ventilator | 5760 | 1.3438 | 1
209 | Classroom | 305 | 20 |  | 629 | 14 | 14 | Unit Ventilator | 5032 | 3.6367 | 1
210 | Classroom | 41 | 2 |  | 241 | 5 | 2 | Unit Ventilator | 1928 | 1.2759 | 1
211 | Classroom | 56 | 3 |  | 385 | 8 | 3 | Unit Ventilator | 3080 | 1.0909 | 1
212 | Classroom | 319 | 21 |  | 603 | 13 | 13 | Unit Ventilator | 4824 | 3.9677 | 1
213 | Classroom | 49 | 3 | Yes | 290 | 6 | 6 | Unit Ventilator | 2320 | 1.2672 | 1
214 | Classroom | 112 | 7 | Yes | 741 | 16 | 16 | Unit Ventilator | 5928 | 1.1336 | 1
300 | Classroom | 35 | 2 | Yes | 947 | 21 | 21 | Unit Ventilator | 7576 | 0.27719 | 0
301 | Classroom | 63 | 4 | Yes | 900 | 20 | 20 | Unit Ventilator | 7200 | 0.525 | 0
302 | Classroom | 87 | 5 | Yes | 588 | 13 | 13 | Unit Ventilator | 4704 | 1.1097 | 1
303 | Classroom | 85 | 5 | Yes | 571 | 12 | 12 | Unit Ventilator | 4568 | 1.1165 | 1
304 | Classroom | 293 | 19 |  | 431 | 9 | 9 | Unit Ventilator | 3448 | 5.0986 | 2
305 | Classroom | 58 | 3 | Yes | 504 | 11 | 11 | Unit Ventilator | 4032 | 0.8631 | 0
306 | Classroom | 286 | 19 |  | 415 | 9 | 9 | Unit Ventilator | 3320 | 5.1687 | 2
307 | Classroom | 97 | 6 | Yes | 501 | 11 | 11 | Unit Ventilator | 4008 | 1.4521 | 1
308 | Classroom | 79 | 5 | Yes | 686 | 15 | 15 | Unit Ventilator | 5488 | 0.8637 | 0
310 | Classroom | 106 | 7 | Yes | 592 | 13 | 13 | Unit Ventilator | 4736 | 1.3429 | 1
311 | Classroom | 53 | 3 | Yes | 441 | 10 | 10 | Unit Ventilator | 3528 | 0.90136 | 0
312 | Classroom | 18 | 1 | Yes | 465 | 10 | 10 | Unit Ventilator | 3720 | 0.29032 | 0
313 | Classroom | 72 | 4 | Yes | 463 | 10 | 10 | Unit Ventilator | 3704 | 1.1663 | 1
314 | Classroom | 61 | 4 | Yes | 533 | 12 | 12 | Unit Ventilator | 4264 | 0.85835 | 0

## Arthur
Sheet Last Modified: | 2021-04-30
School: | Chester A. Arthur Elementary School
Vendor: | Devine Retest | Devine 3rd Retest | [7 empty] | Min | 0
| Devine 4th Retest | Devine 5th Retest | [7 empty] | Max | 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | Average | 0.91429
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | cu-ft 8 ft ceiling | AUC | Cert Level
B001 | Classroom | 380 | 25 |  | 551 | 12 | 12 | Unit Ventilator | 4408 | 5.1724 | 2
B002 | Classroom | 0 | 0 |  | 100 | 2 | 0 | N/A | 800 | 0 | 0
100 | Classroom | 309 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.9261 | 1
102 | Classroom | 335 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1723 | 1
104 | Classroom | 295 | 19 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.7936 | 1
106 | Classroom | 346 | 23 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.2765 | 1
107A | Teacher's Lounge |  | 0 | Yes | 448 | 10 | 10 | Unit Ventilator | 3584 | 0 | 0
200 | Classroom | 335 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1723 | 1
201 | Classroom | 304 | 20 |  | 364 | 8 | 8 | Unit Ventilator | 2912 | 6.2637 | 2
202 | Classroom | 320 | 21 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.0303 | 1
203 | Classroom | 299 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5955 | 1
204 | Classroom | 333 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1534 | 1
205 | Classroom | 374 | 24 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.2465 | 1
206 | Classroom | 280 | 18 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.6515 | 1
207 | Classroom | 341 | 22 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.9601 | 1
207A | Classroom |  | 0 | Yes | 425 | 9 | 9 | Unit Ventilator | 3400 | 0 | 0
209 | Classroom | 311 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.9451 | 1
300 | Classroom | 293 | 19 |  | 857 | 19 | 19 | Unit Ventilator | 6856 | 2.5642 | 1
301 | Classroom | 273 | 18 |  | 364 | 8 | 8 | Unit Ventilator | 2912 | 5.625 | 2
302 | Classroom | 355 | 23 |  | 857 | 19 | 19 | Unit Ventilator | 6856 | 3.1068 | 1
303 | Classroom | 328 | 21 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.8472 | 1
304 | Classroom | 350 | 23 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.3144 | 1
305 | Classroom | 274 | 18 |  | 900 | 20 | 18 | Unit Ventilator | 7200 | 2.2833 | 1
306 | Classroom | 304 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.8788 | 1
307 | Classroom | 350 | 23 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.0382 | 1
307A | Classroom |  | 0 | Yes | 425 | 9 | 9 | Unit Ventilator | 3400 | 0 | 0
309 | Classroom | 331 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1345 | 1
- | Auditorium | 753 | 50 |  | 4335 | 98 | 50 | HV Unit | 34680 | 1.3028 | 1
- | Gym | 2466 | 164 |  | 3055 | 69 | 69 | HV Unit | 24440 | 6.054 | 2
- | IMC | 383 | 25 |  | 1472 | 33 | 25 | Unit Ventilator | 11776 | 1.9514 | 1
- | Resource Room/Storage | 0 | 0 | Yes | 300 | 6 | 6 | Unit Ventilator | 2400 | 0 | 0
- | Main Office | 401 | 26 |  | 1104 | 25 | 25 | Unit Ventilator | 8832 | 2.7242 | 1
- | BE Office | 63 | 4 |  | 240 | 5 | 4 | Unit Ventilator | 1920 | 1.9688 | 1
- | Nurse Office | 0 | 0 | Yes | 276 | 6 | 6 |  | 2208 | 0 | 0
- | Principal's Office |  | 0 | Yes | 240 | 5 | 5 |  | 1920 | 0 | 0

## Bache-Martin
Sheet Last Modified: | 2021-04-26
School: | Alexander D. Bache Elementary School |  | Bache Part 2
School: | W.E. Martin Building |  | Martin Part 2 | [6 empty] | Min | 0
Vendor: | EMCOR Fluidics | [8 empty] | Max | 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | Average | 1.0462
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | cu-ft 8 ft ceiling | AUC | Cert Level
Bache Building
1 | Classroom | 274 | 18 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.6758 | 1
2 | Classroom | 295 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8809 | 1
3 | Classroom | 305 | 20 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.9785 | 1
4 | Classroom | 289 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8223 | 1
5 | Classroom | 330 | 22 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.2227 | 1
6 | Classroom | 273 | 18 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.666 | 1
7 | Classroom | 312 | 20 |  | 528 | 12 | 12 | Unit Ventilator | 4224 | 4.4318 | 2
8 | Classroom | 406 | 27 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.9648 | 1
9 | Classroom | 455 | 30 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.4434 | 2
10 | Classroom | 400 | 26 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.9062 | 1
11 | Classroom | 346 | 23 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.3789 | 1
12 | Classroom | 388 | 25 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.7891 | 1
13 | Teacher's Lounge | 339 | 22 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.3105 | 1
14 | Classroom | 288 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8125 | 1
15 | Classroom | 424 | 28 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.1406 | 2
16 | Library | 296 | 19 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.0833 | 1
17 | Library | 294 | 19 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.0625 | 1
18 | Classroom | 338 | 22 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.3008 | 1
19 | Classroom | 114 | 7 | Yes | 768 | 17 | 17 | Unit Ventilator | 6144 | 1.1133 | 1
20 | Classroom | 302 | 20 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.1458 | 1
21 | Classroom | 278 | 18 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 2.9616 | 1
22 | Classroom | 328 | 21 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.7273 | 1
23 | Classroom | 360 | 24 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.8352 | 1
24 | Classroom | 347 | 23 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.9432 | 1
25 | Classroom | 377 | 25 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.6816 | 1
26 | Classroom | 381 | 25 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.9688 | 1
27 | Classroom | 436 | 29 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.2578 | 2
- | Cafeteria | 0 | 0 | Yes | 1891 | 42 | 42 | Unit Ventilator | 15128 | 0 | 0
Martin Building | [8 empty] | 0
101 | Classroom | 405 | 27 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 4.2602 | 2
102 | Classroom | 415 | 27 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 4.3654 | 2
103 | Classroom | 308 | 20 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.5 | 1
104 | Classroom | 289 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8223 | 1
105 | Classroom | 355 | 23 |  | 570 | 12 | 12 | Unit Ventilator | 4560 | 4.6711 | 2
106 | Classroom | 339 | 22 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 3.9851 | 1
107A | Classroom | 317 | 21 |  | 900 | 20 | 20 | Unit Ventilator | 7200 | 2.6417 | 1
107B | Classroom | 0 | 0 | Yes | 736 | 16 | 16 | Unit Ventilator | 5888 | 0 | 0
108 | Classroom |  | 0 | Yes | 420 | 9 | 9 |  | 3360 | 0 | 0
110 | Classroom | 518 | 34 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 4.968 | 2
111 | Classroom | 354 | 23 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 3.9805 | 1
112 | Classroom | 328 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5652 | 1
113 | Classroom | 389 | 25 |  | 1092 | 24 | 24 | Unit Ventilator | 8736 | 2.6717 | 1
114 | Classroom | 663 | 44 |  | 1036 | 23 | 23 | Unit Ventilator | 8288 | 4.7997 | 2
115 | Classroom | 422 | 28 |  | 814 | 18 | 18 | Unit Ventilator | 6512 | 3.8882 | 1
117 | Classroom | 536 | 35 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 5.1407 | 2
119 | Classroom | 480 | 32 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 5.0491 | 2
120 | Classroom | 277 | 18 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.0109 | 1
121 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | Unit Ventilator | 5760 | 0 | 0
122 | Classroom | 0 | 0 |  | 744 | 16 | 0 | Unit Ventilator | 5952 | 0 | 0
124 | Classroom | 273 | 18 |  | 759 | 17 | 17 | Unit Ventilator | 6072 | 2.6976 | 1
127 | Classroom |  | 0 | Yes | 690 | 15 | 15 | N/A | 5520 | 0 | 0
128 | Homemaking | 288 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8125 | 1
129 | Classroom | 280 | 18 |  | 500 | 11 | 11 | Unit Ventilator | 4000 | 4.2 | 2
130 | Classroom | 321 | 21 |  | 644 | 14 | 14 | Unit Ventilator | 5152 | 3.7384 | 1
131 | Classroom | 283 | 18 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 3.3268 | 1
133 | Classroom | 337 | 22 |  | 403 | 9 | 9 | Unit Ventilator | 3224 | 6.2717 | 2
134 | Counselor office | 279 | 18 |  | 512 | 11 | 11 | Unit Ventilator | 4096 | 4.0869 | 2
135 | Custodial supply room | 0 | 0 |  | 512 | 11 | 0 | Unit Ventilator | 4096 | 0 | 0
136 | Classroom | 276 | 18 |  | 403 | 9 | 9 | Unit Ventilator | 3224 | 5.1365 | 2
- | Main Office |  | 0 | Yes | 529 | 12 | 12 |  | 4232 | 0 | 0
- | Principals Office |  | 0 | Yes | 221 | 5 | 5 |  | 1768 | 0 | 0
- | Nurses Office |  | 0 | Yes | 308 | 7 | 7 |  | 2464 | 0 | 0
- | Auditorium | 109 | 7 |  | 1702 | 38 | 7 | Unit Ventilator | 13616 | 0.48032 | 0
- | Cafe | 642 | 42 |  | 2451 | 55 | 42 | Unit Ventilator | 19608 | 1.9645 | 1
- | Gym | 364 | 24 |  | 1914 | 43 | 24 | Unit Ventilator | 15312 | 1.4263 | 1
- | Hallway | 157 | 10 |  |  | 0 | 0 | Unit Ventilator | 0
- | Staff Lounge |  | 0 |  | 525 | 11 | 0 |  | 4200 | 0 | 0

## Baldi
Sheet Last Modified: | 2021-04-28
School: | Charles Carmine Antonio Baldi Middle School | [8 empty] | Min | 0
Vendor: | Goldner | [8 empty] | Max | 4
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | Average | 0.75962
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | cu-ft 8 ft ceiling | AUC | Cert Level
22 | Classroom | 903 | 60 |  | 799 | 18 | 18 | Air Handling Unit | 6392 | 8.4762 | 2
23 | Classroom | 552 | 36 |  | 844 | 19 | 19 | Unit Ventilator | 6752 | 4.9052 | 2
24 | Classroom | 670 | 44 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 5.891 | 2
26B | Classroom | 383 | 25 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.5116 | 1
27A | Classroom | 444 | 29 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 4.0709 | 2
28 | Science Lab | 1347 | 89 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 8.3285 | 2
29 | Room | 733 | 48 |  | 1280 | 29 | 29 | Unit Ventilator | 10240 | 4.2949 | 2
30 | Science Lab | 1295 | 86 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 8.007 | 2
31A | Classroom | 696 | 46 |  | 831 | 18 | 18 | Unit Ventilator | 6648 | 6.2816 | 2
31B | Classroom | 772 | 51 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 7.0782 | 2
32A | Classroom | 1064 | 70 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 9.3662 | 2
32B | Classroom | 395 | 26 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.6216 | 1
33A | Classroom | 1195 | 79 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 10.507 | 3
34a | Classroom | 310 | 20 |  | 844 | 19 | 19 | Unit Ventilator | 6752 | 2.7547 | 1
34b | Classroom | 232 | 15 |  | 799 | 18 | 15 | Unit Ventilator | 6392 | 2.1777 | 1
35 | Science Lab | 433 | 28 |  | 1227 | 27 | 27 | Unit Ventilator | 9816 | 2.6467 | 1
35 | Lounge | 133 | 8 |  | 435 | 9 | 8 | Unit Ventilator | 3480 | 2.2931 | 1
38 | Lounge | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
39 | Lounge | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
40 | Seminar Room | 1766 | 117 |  | 411 | 9 | 9 | Unit Ventilator | 3288 | 32.2263 | 4
40 | Classroom | 353 | 23 |  | 411 | 9 | 9 | Unit Ventilator | 3288 | 6.4416 | 2
42 | SGI Room | 205 | 13 |  | 435 | 9 | 9 | Unit Ventilator | 3480 | 3.5345 | 1
43 | SGI Room | 226 | 15 |  | 485 | 11 | 11 | Unit Ventilator | 3880 | 3.4948 | 1
44A | Classroom | 243 | 16 |  | 854 | 19 | 16 | Unit Ventilator | 6832 | 2.1341 | 1
44B | Classroom | 194 | 12 |  | 847 | 19 | 12 | Unit Ventilator | 6776 | 1.7178 | 1
45 | Teachers IPO Room | 0 | 0 |  | 980 | 22 | 0 | Unit Ventilator | 7840 | 0 | 0
46 | Conf. Room | 56 | 3 |  | 980 | 22 | 3 | Unit Ventilator | 7840 | 0.42857 | 0
46 | IPO Materials Room | 76 | 5 |  | 980 | 22 | 5 | Unit Ventilator | 7840 | 0.58163 | 0
47 | Faculty Lounge Room | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
47a | Classroom | 195 | 13 |  | 841 | 19 | 13 | Air Handling Unit | 6728 | 1.739 | 1
47b | Classroom | 191 | 12 |  | 844 | 19 | 12 | Air Handling Unit | 6752 | 1.6973 | 1
48 | Science Lab | 858 | 57 |  | 1227 | 27 | 27 | Unit Ventilator | 9816 | 5.2445 | 2
B4 | Room |  | 0 |  | 853 | 19 | 0 |  | 6824 | 0 | 0
G5 | Room |  | 0 |  | 853 | 19 | 0 |  | 6824 | 0 | 0
G100 | Classroom |  | 0 | Yes | 565 | 12 | 12 |  | 4520 | 0 | 0
G101 | Classroom |  | 0 |  | 1227 | 27 | 0 |  | 9816 | 0 | 0
G102 | Classroom |  | 0 |  | 799 | 18 | 0 |  | 6392 | 0 | 0
G103 | Classroom |  | 0 |  | 844 | 19 | 0 |  | 6752 | 0 | 0
G104 | Classroom |  | 0 |  | 853 | 19 | 0 |  | 6824 | 0 | 0
G105 | Classroom |  | 0 |  | 853 | 19 | 0 |  | 6824 | 0 | 0
Y3 | Room |  | 0 |  | 818 | 18 | 0 |  | 6544 | 0 | 0
Y5 | Room |  | 0 |  | 852 | 19 | 0 |  | 6816 | 0 | 0
Y104 | Room |  | 0 |  | 818 | 18 | 0 |  | 6544 | 0 | 0
Y105 | Room |  | 0 |  | 852 | 19 | 0 |  | 6816 | 0 | 0
100 | Common Area | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
127 | Art Lab | 0 | 0 | Yes | 2279 | 51 | 51 | Unit Ventilator | 18232 | 0 | 0
128 | Art Lab | 0 | 0 | Yes | 2184 | 49 | 49 | Unit Ventilator | 17472 | 0 | 0
129 | Faculty Dining Room | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
137 | Classroom | 1440 | 96 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 13.2029 | 3
138 | Classroom | 1218 | 81 |  | 831 | 18 | 18 | Unit Ventilator | 6648 | 10.9928 | 3
139 | Lab | 2473 | 164 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 15.2906 | 3
140 | Large Group Room | 1508 | 100 |  | 1280 | 29 | 29 | Unit Ventilator | 10240 | 8.8359 | 2
141 | Science Lab | 1291 | 86 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 7.9823 | 2
142 | Classroom | 1844 | 122 |  | 831 | 18 | 18 | Unit Ventilator | 6648 | 16.6426 | 3
143 | Classroom | 1560 | 104 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 14.3032 | 3
144 | Classroom | 391 | 26 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.585 | 1
145 | Classroom | 619 | 41 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 5.4489 | 2
146 | Classroom | 265 | 17 |  | 853 | 19 | 17 | Unit Ventilator | 6824 | 2.33 | 1
147 | Classroom | 562 | 37 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 4.9414 | 2
148 | Classroom | 592 | 39 |  | 844 | 19 | 19 | Unit Ventilator | 6752 | 5.2607 | 2
149 | Classroom | 385 | 25 |  | 799 | 18 | 18 | Unit Ventilator | 6392 | 3.6139 | 1
150 | Science Lab | 611 | 40 |  | 1233 | 28 | 28 | Unit Ventilator | 9864 | 3.7165 | 1
200 | Classroom |  | 0 | Yes | 566 | 12 | 12 |  | 4528 | 0 | 0
200 Office | Office |  | 0 | Yes | 374 | 8 | 8 |  | 2992 | 0 | 0
201 | Classroom |  | 0 | Yes | 1085 | 24 | 24 |  | 8680 | 0 | 0
202 | Classroom |  | 0 | Yes | 893 | 20 | 20 |  | 7144 | 0 | 0
203 | Classroom |  | 0 |  | 1029 | 23 | 0 |  | 8232 | 0 | 0
205 | Classroom |  | 0 | Yes | 1575 | 35 | 35 |  | 12600 | 0 | 0
211 | Classroom |  | 0 | Yes | 930 | 21 | 21 |  | 7440 | 0 | 0
212 | Classroom |  | 0 | Yes | 600 | 13 | 13 |  | 4800 | 0 | 0
213 | Classroom |  | 0 | Yes | 870 | 19 | 19 |  | 6960 | 0 | 0
214 | Classroom |  | 0 | Yes | 1326 | 30 | 30 |  | 10608 | 0 | 0
215 | Classroom |  | 0 |  | 980 | 22 | 0 |  | 7840 | 0 | 0
225 | Library | 0 | 0 |  | 1230 | 27 | 0 | Unit Ventilator | 9840 | 0 | 0
226 | Study Area | 0 | 0 |  | 3510 | 79 | 0 | Unit Ventilator | 28080 | 0 | 0
227 | Computer Lab | 0 | 0 |  | 980 | 22 | 0 | Unit Ventilator | 7840 | 0 | 0
228 | Mech. Room | 0 | 0 |  | 411 | 9 | 0 | Unit Ventilator | 3288 | 0 | 0
155A | Teachers Office | 0 | 0 |  | 948 | 21 | 0 | Unit Ventilator | 7584 | 0 | 0
156A | Teachers Office | 0 | 0 |  | 948 | 21 | 0 | Unit Ventilator | 7584 | 0 | 0
225A | Office | 0 | 0 |  | 948 | 21 | 0 | Unit Ventilator | 7584 | 0 | 0
225B | Office | 0 | 0 |  | 1029 | 23 | 0 | Unit Ventilator | 8232 | 0 | 0
225C | Storage | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator | 8000 | 0 | 0
225D | Office | 0 | 0 |  | 299 | 6 | 0 | Unit Ventilator | 2392 | 0 | 0
Computer Lab A | Lab |  | 0 |  | 2640 | 60 | 0 |  | 21120 | 0 | 0
Computer Lab B | Lab |  | 0 |  | 2067 | 46 | 0 |  | 16536 | 0 | 0
Computer Lab C | Lab |  | 0 |  | 2262 | 51 | 0 |  | 18096 | 0 | 0
Main Office | Office |  | 0 | Yes | 875 | 19 | 19 |  | 7000 | 0 | 0
Principal | Office |  | 0 | Yes | 270 | 6 | 6 | Mobile Mini | 2160 | 0 | 0
Vice Principal | Office |  | 0 | Yes | 144 | 3 | 3 | Mobile Mini | 1152 | 0 | 0
Vice Principal | Office |  | 0 | Yes | 144 | 3 | 3 | Mobile Mini | 1152 | 0 | 0
Vice Principal | Office |  | 0 | Yes | 153 | 3 | 3 | Mobile Mini | 1224 | 0 | 0
- | Boys Gym | 0 | 0 |  | 5418 | 123 | 0 | Unit Ventilator | 43344 | 0 | 0
- | Boys Locker Room | 0 | 0 |  | 1824 | 41 | 0 | Unit Ventilator | 14592 | 0 | 0
- | Corridor/Hall | 1107 | 73 |  | 435 | 9 | 9 | Unit Ventilator | 3480 | 19.0862 | 3
Cafeteria 1 | Dining | 0 | 0 |  | 2179 | 49 | 0 | Unit Ventilator | 17432 | 0 | 0
Cafeteria 2 | Dining |  | 0 |  | 2179 | 49 | 0 |  | 17432 | 0 | 0
Cafeteria 3 | Dining |  | 0 |  | 2179 | 49 | 0 |  | 17432 | 0 | 0
Cafeteria 4 | Dining |  | 0 |  | 2179 | 49 | 0 |  | 17432 | 0 | 0
- | Girls Gym | 4087 | 272 | Yes | 5418 | 123 | 123 | Air Handling Unit | 43344 | 5.6575 | 2
- | IPO Bathrooms | 129 | 8 |  | 411 | 9 | 8 | Unit Ventilator | 3288 | 2.354 | 1
- | IPO Office 1 |  | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
- | IPO Office 1 | 40 | 2 |  | 435 | 9 | 2 | Unit Ventilator | 3480 | 0.68966 | 0
- | IPO Office 3 | 46 | 3 |  | 435 | 9 | 3 | Unit Ventilator | 3480 | 0.7931 | 0
- | Lounge | 104 | 6 |  | 485 | 11 | 6 | Unit Ventilator | 3880 | 1.6082 | 1

## Barry
Sheet Last Modified: | 2021-03-12
School: | New Commodore John Barry Elementary School
Vendor: | EMCOR |  | Exhaust
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Room |  | 0 | Yes | 425 | 9 | 9 | Rooftop Unit
104 | Room | 116 | 7 | Yes | 1008 | 22 | 22 | Rooftop Unit
105 | Room | 133 | 8 | Yes | 1134 | 25 | 25 | Rooftop Unit
106 | Room |  | 0 | Yes | 1140 | 25 | 25 | Rooftop Unit
107 | Room | 308 | 20 |  | 1118 | 25 | 20 | Rooftop Unit
108 | Room | 303 | 20 |  | 1140 | 25 | 20 | Rooftop Unit
109 | Room | 1254 | 83 |  | 2100 | 47 | 47 | Rooftop Unit
116 | Room | 125 | 8 |  |  | 0 | 0 | Rooftop Unit
202 | Room | 147 | 9 | Yes | 551 | 12 | 12 | Rooftop Unit
203 | Room | 148 | 9 | Yes | 551 | 12 | 12 | Rooftop Unit
204 | Room | 139 | 9 | Yes | 418 | 9 | 9 | Rooftop Unit
205 | Room | 202 | 13 | Yes | 551 | 12 | 12 | Rooftop Unit
206 | Room | 145 | 9 | Yes | 728 | 16 | 16 | Rooftop Unit
207 | Room | 185 | 12 | Yes | 728 | 16 | 16 | Rooftop Unit
208 | Room | 139 | 9 | Yes | 728 | 16 | 16 | Rooftop Unit
209 | Room | 313 | 20 |  | 728 | 16 | 16 | Rooftop Unit
210 | Room | 272 | 18 |  | 630 | 14 | 14 | Rooftop Unit
211 | Room | 192 | 12 |  | 756 | 17 | 12 | Rooftop Unit
212 | Room | 154 | 10 | Yes | 900 | 20 | 20 | Rooftop Unit
213 | Room | 130 | 8 | Yes | 900 | 20 | 20 | Rooftop Unit
214 | Room | 268 | 17 |  | 812 | 18 | 17 | Rooftop Unit
215 | Room | 219 | 14 | Yes | 756 | 17 | 17 | Rooftop Unit
216 | Room | 223 | 14 | Yes | 756 | 17 | 17 | Rooftop Unit
301 | Room | 210 | 14 |  | 630 | 14 | 14 | Rooftop Unit
302A | Room |  | 0 |  | 104 | 2 | 0 | Rooftop Unit
302B | Room |  | 0 |  | 117 | 2 | 0 | Rooftop Unit
302C | Room |  | 0 |  | 104 | 2 | 0 | Rooftop Unit
303 | Room | 99 | 6 |  | 651 | 14 | 6 | Rooftop Unit
304 | Room |  | 0 |  | 110 | 2 | 0 | Rooftop Unit
305 | Room | 237 | 15 |  | 756 | 17 | 15 | Rooftop Unit
306 | Room | 156 | 10 |  | 756 | 17 | 10 | Rooftop Unit
307 | Room | 265 | 17 |  | 784 | 17 | 17 | Rooftop Unit
308 | Room | 192 | 12 | Yes | 864 | 19 | 19 | Rooftop Unit
309 | Room | 208 | 13 |  | 810 | 18 | 13 | Rooftop Unit
310 | Room | 296 | 19 |  | 810 | 18 | 18 | Rooftop Unit
311 | Room | 249 | 16 |  | 812 | 18 | 16 | Rooftop Unit
312 | Room | 210 | 14 |  | 840 | 19 | 14 | Rooftop Unit
313 | Room | 96 | 6 |  | 810 | 18 | 6 | Rooftop Unit
314 | Room | 219 | 14 |  | 810 | 18 | 14 | Rooftop Unit
315 | Room | 105 | 7 |  | 812 | 18 | 7 | Rooftop Unit
316 | Room | 143 | 9 |  | 812 | 18 | 9 | Rooftop Unit
320 | Room | 212 | 14 |  | 620 | 14 | 14 | Rooftop Unit
323 | Room | 230 | 15 |  | 620 | 14 | 14 | Rooftop Unit
401 | Room | 215 | 14 | Yes | 1260 | 28 | 28 | Rooftop Unit
403A | Room |  | 0 |  | 240 | 5 | 0 | Rooftop Unit
403B | Room |  | 0 |  | 210 | 4 | 0 | Rooftop Unit
403C | Room |  | 0 |  | 240 | 5 | 0 | Rooftop Unit
404 | Room |  | 0 | Yes | 1024 | 23 | 23 | Rooftop Unit
405 | Room | 382 | 25 |  | 1476 | 33 | 25 | Rooftop Unit
406 | Room |  | 0 |  | 1462 | 33 | 0 | Rooftop Unit
407 | Room |  | 0 |  | 1054 | 23 | 0 | Rooftop Unit
408 | Room | 561 | 37 |  | 1280 | 29 | 29 | Rooftop Unit
409 | Room | 213 | 14 |  | 1160 | 26 | 14 | Rooftop Unit
- | Café | 593 | 39 |  | 4800 | 109 | 39 | Rooftop Unit
- | Gym |  | 0 | Yes | 6240 | 141 | 141 | Rooftop Unit
- | Library |  | 0 | Yes | 1961 | 44 | 44 | Rooftop Unit
- | Main Office |  | 0 |  | 924 | 21 | 0 | Rooftop Unit
- | Nurse's Office |  | 0 |  | 143 | 3 | 0 | Rooftop Unit

## Barton
Sheet Last Modified: | 2021-03-16
School: | Clara Barton
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B7 | Classroom | 0 | 0 | Yes | 601 | 13 | 13 | House Fan
B8 | Classroom | 0 | 0 | Yes | 848 | 19 | 19 | House Fan
B10 | Classroom | 0 | 0 |  | 686 | 15 | 0 | House Fan
B11 | Classroom | 0 | 0 |  | 806 | 18 | 0 | House Fan
100 | Classroom | 0 | 0 | Yes | 742 | 16 | 16 | House Fan
101 | Classroom | 0 | 0 | Yes | 650 | 14 | 14 | House Fan
102 | Office | 0 | 0 | Yes | 452 | 10 | 10 | House Fan
102 A | Classroom | 0 | 0 |  | 70 | 1 | 0 | House Fan
102 B | Office | 0 | 0 |  | 122 | 2 | 0 | House Fan
103 C | Office | 0 | 0 |  | 90 | 2 | 0 | House Fan
103 | Classroom | 0 | 0 | Yes | 626.707 | 14 | 14 | House Fan
104 | Library | 0 | 0 | Yes | 645 | 14 | 14 | House Fan
105 | Library | 0 | 0 | Yes | 658 | 14 | 14 | House Fan
106 | Library | 0 | 0 | Yes | 653 | 14 | 14 | House Fan
107 | Classroom | 0 | 0 | Yes | 632 | 14 | 14 | House Fan
108 | Classroom | 0 | 0 | Yes | 640 | 14 | 14 | House Fan
109 | Classroom | 0 | 0 | Yes | 694.486 | 15 | 15 | House Fan
110 | Classroom | 0 | 0 | Yes | 683.103 | 15 | 15 | House Fan
111 | Classroom | 0 | 0 | Yes | 649.73 | 14 | 14 | House Fan
112 | Nurse's Office | 0 | 0 | Yes | 117.665 | 2 | 2 | House Fan
- | Main Office | 0 | 0 | Yes | 297 | 6 | 6 | House Fan
- | Principal's Office | 0 | 0 | Yes | 159 | 3 | 3 | House Fan
200 | Classroom | 0 | 0 | Yes | 663 | 15 | 15 | House Fan
200 A | Office | 0 | 0 | Yes | 226 | 5 | 5 | House Fan
200 B | Classroom | 0 | 0 | Yes | 158 | 3 | 3 | House Fan
201 | Classroom | 0 | 0 | Yes | 635 | 14 | 14 | House Fan
202 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan
203 | Classroom | 0 | 0 | Yes | 645 | 14 | 14 | House Fan
204 | Classroom | 0 | 0 | Yes | 624 | 14 | 14 | House Fan
205 | Classroom | 0 | 0 | Yes | 624 | 14 | 14 | House Fan
206 | Classroom | 0 | 0 | Yes | 653 | 14 | 14 | House Fan
207 | Classroom | 0 | 0 | Yes | 663.612 | 15 | 15 | House Fan
208 | Classroom | 0 | 0 | Yes | 638 | 14 | 14 | House Fan
209 | Classroom | 0 | 0 | Yes | 662 | 15 | 15 | House Fan
210 | Classroom | 0 | 0 | Yes | 694 | 15 | 15 | House Fan
211 | Classroom | 0 | 0 | Yes | 616 | 14 | 14 | House Fan
211 A | Office | 0 | 0 |  | 115 | 2 | 0 | House Fan
- | Teacher Lounge | 0 | 0 | Yes | 340 | 7 | 7 | House Fan
215 | Classroom |  | 0 | Yes | 345 | 7 | 7 | house Fan
300 | Classroom | 0 | 0 | Yes | 640 | 14 | 14 | House Fan
300A | Office |  | 0 | Yes | 264 | 6 | 6 | House Fan
301 | Classroom | 0 | 0 | Yes | 668 | 15 | 15 | House Fan
301 A | Office | 0 | 0 |  | 203 | 4 | 0 | House Fan
302 | Classroom | 0 | 0 | Yes | 639 | 14 | 14 | House Fan
303 | Classroom | 0 | 0 | Yes | 692 | 15 | 15 | House Fan
304 | Classroom | 0 | 0 | Yes | 627 | 14 | 14 | House Fan
305 | Classroom | 0 | 0 | Yes | 655 | 14 | 14 | House Fan
306 | Classroom | 0 | 0 | Yes | 664 | 15 | 15 | House Fan
307 | Classroom | 0 | 0 | Yes | 642 | 14 | 14 | House Fan
308 | Classroom | 0 | 0 | Yes | 663 | 15 | 15 | House Fan
309 | Classroom | 0 | 0 | Yes | 605 | 13 | 13 | House Fan
310 | Classroom | 0 | 0 | Yes | 673 | 15 | 15 | House Fan
311 | Classroom | 0 | 0 | Yes | 660 | 15 | 15 | House Fan
312 | Classroom | 0 | 0 |  | 634 | 14 | 0 | House Fan
312 A | Office | 0 | 0 |  | 112 | 2 | 0 | House Fan
- | Counselor Office |  | 0 | Yes | 152 | 3 | 3 | House Fan
- | Gym | 0 | 0 | Yes | 3436 | 78 | 78 | N/A
- | Kitchen | 0 | 0 | Yes | 1140 | 25 | 25 | House Fan
- | Cafeteria | 0 | 0 | Yes | 1478 | 33 | 33 | House Fan

## Bartram
Sheet Last Modified: | 2021-04-26
School: | John Bartram High School
Vendor: | Devine Brothers | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 590 | 39 |  | 1196 | 27 | 27 | Unit Ventilator
102 | Classroom | 359 | 23 |  | 851 | 19 | 19 | Unit Ventilator
103 | Classroom | 759 | 50 |  | 828 | 18 | 18 | Unit Ventilator
104 | Classroom | 646 | 43 |  | 920 | 20 | 20 | Unit Ventilator
105 | Classroom | 582 | 38 |  | 851 | 19 | 19 | Unit Ventilator
106 | Classroom | 696 | 46 |  | 989 | 22 | 22 | Unit Ventilator
107 | Classroom | 980 | 65 |  | 946 | 21 | 21 | Unit Ventilator
108 | Classroom | 575 | 38 |  | 1012 | 23 | 23 | Unit Ventilator
110 | Office | 0 | 0 |  | 238 | 5 | 0 | Unit Ventilator
111 | Classroom | 418 | 27 |  | 805 | 18 | 18 | Unit Ventilator
112 | Room | 416 | 27 |  | 920 | 20 | 20 | Unit Ventilator
113 | Classroom | 416 | 27 |  | 690 | 15 | 15 | Unit Ventilator
115 | Classroom | 343 | 22 |  | 690 | 15 | 15 | Unit Ventilator
116 | Classroom | 467 | 31 |  | 1357 | 30 | 30 | Unit Ventilator
117 | Classroom | 352 | 23 |  | 690 | 15 | 15 | Unit Ventilator
118 | Classroom | 325 | 21 |  | 690 | 15 | 15 | Unit Ventilator
119 | Classroom | 346 | 23 |  | 690 | 15 | 15 | Unit Ventilator
120 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Unit Ventilator
121 | Office | 0 | 0 | Yes | 227 | 5 | 5 | Unit Ventilator
123 | Room | 498 | 33 |  | 1242 | 28 | 28 | Unit Ventilator
124 | Office | 0 | 0 | Yes | 309 | 7 | 7 | Unit Ventilator
124A | Office | 0 | 0 | Yes | 218 | 4 | 4 | Unit Ventilator
125 | Room | 356 | 23 |  | 690 | 15 | 15 | Unit Ventilator
126 | Room | 339 | 22 |  | 276 | 6 | 6 | Unit Ventilator
127 | Room | 349 | 23 |  | 644 | 14 | 14 | Unit Ventilator
127a | Room | 331 | 22 |  | 345 | 7 | 7 | Unit Ventilator
128 | Office | 0 | 0 |  | 230 | 5 | 0 | Unit Ventilator
130 | Room | 288 | 19 |  | 375 | 8 | 8 | Unit Ventilator
130A | Office | 0 | 0 |  | 236 | 5 | 0 | Unit Ventilator
131 | Office | 0 | 0 | Yes | 237 | 5 | 5 | Unit Ventilator
133 | Office | 0 | 0 | Yes | 333 | 7 | 7 | Unit Ventilator
134 | Main Office | 593 | 39 |  | 1656 | 37 | 37 | Unit Ventilator
201 | Classroom | 617 | 41 |  | 989 | 22 | 22 | Unit Ventilator
202 | Classroom | 282 | 18 |  | 805 | 18 | 18 | Unit Ventilator
203 | Classroom | 632 | 42 |  | 989 | 22 | 22 | Unit Ventilator
204 | Classroom | 309 | 20 |  | 690 | 15 | 15 | Unit Ventilator
205 | Classroom | 516 | 34 |  | 989 | 22 | 22 | Unit Ventilator
206 | Classroom | 324 | 21 |  | 690 | 15 | 15 | Unit Ventilator
207 | Classroom | 363 | 24 |  | 989 | 22 | 22 | Unit Ventilator
208 | Classroom | 291 | 19 |  | 690 | 15 | 15 | Unit Ventilator
209 | Classroom | 0 | 0 | Yes | 309 | 7 | 7 | Unit Ventilator
210 | Classroom | 297 | 19 |  | 690 | 15 | 15 | Unit Ventilator
211 | Room | 0 | 0 | Yes | 321 | 7 | 7 | Unit Ventilator
211A | copy Room | 0 | 0 |  | 227 | 5 | 0 | Unit Ventilator
214 | Classroom | 370 | 24 |  | 690 | 15 | 15 | Unit Ventilator
215 | Classroom | 337 | 22 |  | 690 | 15 | 15 | Unit Ventilator
216 | Classroom | 327 | 21 |  | 690 | 15 | 15 | Unit Ventilator
217 | Classroom | 282 | 18 |  | 690 | 15 | 15 | Unit Ventilator
218 | Classroom | 563 | 37 |  | 690 | 15 | 15 | Unit Ventilator
219 | Office | 0 | 0 | Yes | 272 | 6 | 6 | Unit Ventilator
220A | Office | 0 | 0 | Yes | 169 | 3 | 3 | Unit Ventilator
221 | Classroom | 97 | 6 | Yes | 851 | 19 | 19 | Unit Ventilator
222 | Classroom | 320 | 21 |  | 851 | 19 | 19 | Unit Ventilator
223 | Classroom | 329 | 21 |  | 690 | 15 | 15 | Unit Ventilator
224 | Classroom | 302 | 20 |  | 690 | 15 | 15 | Unit Ventilator
225 | Classroom | 437 | 29 |  | 690 | 15 | 15 | Unit Ventilator
226 | Classroom | 315 | 21 |  | 690 | 15 | 15 | Unit Ventilator
227 | Classroom | 299 | 19 |  | 690 | 15 | 15 | Unit Ventilator
228 | Classroom | 302 | 20 |  | 690 | 15 | 15 | Unit Ventilator
229 | Classroom | 407 | 27 |  | 690 | 15 | 15 | Unit Ventilator
230 | Classroom | 290 | 19 |  | 690 | 15 | 15 | Unit Ventilator
231 | Classroom | 331 | 22 |  | 322 | 7 | 7 | Unit Ventilator
232 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | Unit Ventilator
234 | Office | 0 | 0 | Yes | 298 | 6 | 6 | Unit Ventilator
236 | Office | 0 | 0 | Yes | 299 | 6 | 6 | Unit Ventilator
236A | Copy room | 0 | 0 |  | 203 | 4 | 0 | Unit Ventilator
301 | Classroom |  | 0 |  | 816 | 18 | 0 | Air Handling Unit
302 | Classroom |  | 0 |  | 816 | 18 | 0 | Air Handling Unit
305 | Classroom |  | 0 |  | 1000 | 22 | 0 | Air Handling Unit
306 | Classroom |  | 0 |  | 136 | 3 | 0 | Air Handling Unit
307 | Classroom |  | 0 |  | 696 | 15 | 0 | Air Handling Unit
309 | Classroom |  | 0 |  | 225 | 5 | 0 | Air Handling Unit
313 | Faculty | 309 | 20 |  | 832 | 18 | 18 | Unit Ventilator
320 | Classroom | 618 | 41 |  | 1080 | 24 | 24 | Unit Ventilator
321 | Classroom | 574 | 38 |  | 1100 | 25 | 25 | Unit Ventilator
324 | Classroom | 553 | 36 |  | 945 | 21 | 21 | Unit Ventilator
325 | Classroom | 394 | 26 |  | 1080 | 24 | 24 | Unit Ventilator
328 | Room | 0 | 0 | Yes | 169 | 3 | 3 | Unit Ventilator
331 | Classroom | 351 | 23 |  | 805 | 18 | 18 | Unit Ventilator
332 | Classroom | 361 | 24 |  | 1081 | 24 | 24 | Unit Ventilator
333 | Classroom | 321 | 21 |  | 690 | 15 | 15 | Unit Ventilator
334 | Classroom | 284 | 18 |  | 690 | 15 | 15 | Unit Ventilator
335 | Classroom | 286 | 19 |  | 667 | 15 | 15 | Unit Ventilator
336 | Classroom | 295 | 19 |  | 690 | 15 | 15 | Unit Ventilator
337 | Classroom | 86 | 5 | Yes | 690 | 15 | 15 | Unit Ventilator
338 | Classroom | 280 | 18 |  | 667 | 15 | 15 | Unit Ventilator
339 | Classroom | 366 | 24 |  | 506 | 11 | 11 | Unit Ventilator
340 | Classroom | 274 | 18 |  | 484 | 11 | 11 | Unit Ventilator
341 | Classroom | 356 | 23 |  | 484 | 11 | 11 | Unit Ventilator
342 | Classroom | 289 | 19 |  | 529 | 12 | 12 | Unit Ventilator
344 | Room | 0 | 0 | Yes | 233 | 5 | 5 | Unit Ventilator
346 | Classroom | 291 | 19 |  | 675 | 15 | 15 | Unit Ventilator
B12 | Room | 0 | 0 |  | 383 | 8 | 0 | Unit Ventilator
B13 | BE Office | 0 | 0 |  | 238 | 5 | 0 | Unit Ventilator
B17 | Room | 0 | 0 |  | 209 | 4 | 0 | Unit Ventilator
Bc | Room | 0 | 0 | Yes | 244 | 5 | 5 | Unit Ventilator
C1 | Classroom | 398 | 26 |  | 1000 | 22 | 22 | Unit Ventilator
C2 | Classroom | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator
C3 | Classroom | 1212 | 80 |  | 1000 | 22 | 22 | Unit Ventilator
C4 | Classroom | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator
C5 | Classroom | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator
C7 | Classroom | 881 | 58 |  | 968 | 22 | 22 | Unit Ventilator
C7A | Classroom | 0 | 0 |  | 909 | 20 | 0 | Unit Ventilator
- | School police | 0 | 0 | Yes | 192 | 4 | 4 | Unit Ventilator
- | 3rd Floor C Wing | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Auditorium | 0 | 0 |  | 11625 | 264 | 0 | Air Handling Unit
- | Boys Gym | 5931 | 395 |  | 5280 | 120 | 120 | Air Handling Unit
- | Library | 866 | 57 |  | 4526 | 102 | 57 | Unit Ventilator
- | Corridor | 0 | 0 |  |  | 0 | 0 | Unit Ventilator
- | Girls Gym | 6806 | 453 |  | 5280 | 120 | 120 | Air Handling Unit
- | Nurse Area | 255 | 17 |  | 936 | 21 | 17 | Unit Ventilator
- | Cafeteria | 0 | 0 | Yes | 6262 | 142 | 142 | Unit Ventilator

## Bethune
Sheet Last Modified: | 2021-04-05
School: | Mary McLeod Bethune School
Vendor: | Capital | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 300 | 20 |  | 1350 | 30 | 20 | Unit Ventilator
2 | Classroom | 278 | 18 |  | 1350 | 30 | 18 | Unit Ventilator
3 | Classroom | 395 | 26 |  | 1350 | 30 | 26 | Unit Ventilator
4 | Classroom | 425 | 28 |  | 1296 | 29 | 28 | Unit Ventilator
5 | Classroom | 314 | 20 |  | 1296 | 29 | 20 | Unit Ventilator
100 | Classroom | 614 | 40 |  | 960 | 21 | 21 | Unit Ventilator
101 | Classroom | 597 | 39 |  | 1024 | 23 | 23 | Unit Ventilator
101A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV
102 | Classroom | 560 | 37 |  | 690 | 15 | 15 | Unit Ventilator
103 | Classroom | 555 | 37 |  | 690 | 15 | 15 | Unit Ventilator
104 | Classroom | 575 | 38 |  | 690 | 15 | 15 | Unit Ventilator
105 | Classroom | 618 | 41 |  | 690 | 15 | 15 | Unit Ventilator
106 | Class Area | 163 | 10 |  | 625 | 14 | 10 | Unit Ventilator
106A | IT room | 280 | 18 |  | 304 | 6 | 6 | Unit Ventilator
107 | Class Area | 155 | 10 |  | 1050 | 23 | 10 | Unit Ventilator
108 | Class Area | 141 | 9 |  | 1050 | 23 | 9 | Unit Ventilator
109 | Class Area | 143 | 9 |  | 625 | 14 | 9 | Unit Ventilator
110 | Class Area | 159 | 10 |  | 690 | 15 | 10 | Unit Ventilator
111 | Class Area | 164 | 10 |  | 690 | 15 | 10 | Unit Ventilator
112 | Class Area | 142 | 9 |  | 690 | 15 | 9 | Unit Ventilator
113 | Class Area | 149 | 9 |  | 690 | 15 | 9 | Unit Ventilator
114 | Class Area | 137 | 9 |  | 690 | 15 | 9 | Unit Ventilator
114A | Team Planning | 0 | 0 |  | 360 | 8 | 0 | HUV
115 | Class | 141 | 9 |  | 690 | 15 | 9 | Unit Ventilator
118D | Main Office | 0 | 0 |  | 150 | 3 | 0 | Unit Ventilator
119A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV
119B | Building Engineer's Office | 305 | 20 |  | 450 | 10 | 10 | Unit Ventilator
120 | Instructional Materials Center | 303 | 20 |  | 2520 | 57 | 20 | Unit Ventilator
122 | Main Office | 394 | 26 |  | 600 | 13 | 13 | Unit Ventilator
122C | Main Office | 301 | 20 |  | 130 | 2 | 2 | Unit Ventilator
122D | Principal's Office | 383 | 25 |  | 216 | 4 | 4 | Unit Ventilator
123 | Teacher's Dining | 355 | 23 |  | 594 | 13 | 13 | Unit Ventilator
123A | Teacher's Lounge | 298 | 19 |  | 270 | 6 | 6 | Unit Ventilator
127 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV
150 | Storage | 163 | 10 |  | 360 | 8 | 8 | Unit Ventilator
153 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV
165 | Gym Office | 152 | 10 |  | 130 | 2 | 2 | Unit Ventilator
184 | Examination | 153 | 10 |  | 130 | 2 | 2 | Unit Ventilator
200 | Classroom | 622 | 41 |  | 1350 | 30 | 30 | Unit Ventilator
201 | Classroom | 530 | 35 |  | 690 | 15 | 15 | Unit Ventilator
201A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV
202 | Classroom | 519 | 34 |  | 690 | 15 | 15 | Unit Ventilator
203 | Classroom | 434 | 28 |  | 690 | 15 | 15 | Unit Ventilator
204 | Classroom | 550 | 36 |  | 690 | 15 | 15 | Unit Ventilator
205 | Classroom | 436 | 29 |  | 690 | 15 | 15 | Unit Ventilator
206 | Classroom | 500 | 33 |  | 690 | 15 | 15 | Unit Ventilator
206A | Team Planning | 149 | 9 |  | 270 | 6 | 6 | Unit Ventilator
207 | Classroom | 327 | 21 |  | 945 | 21 | 21 | Unit Ventilator
208 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV
208 | Classroom | 509 | 33 |  | 690 | 15 | 15 | Unit Ventilator
209 | Classroom | 552 | 36 |  | 625 | 14 | 14 | Unit Ventilator
210 | Classroom | 694 | 46 |  | 690 | 15 | 15 | Unit Ventilator
211 | Classroom | 531 | 35 |  | 690 | 15 | 15 | Unit Ventilator
212 | Classroom | 379 | 25 |  | 690 | 15 | 15 | Unit Ventilator
213 | Classroom | 688 | 45 |  | 690 | 15 | 15 | Unit Ventilator
214 | Classroom | 382 | 25 |  | 690 | 15 | 15 | Unit Ventilator
214A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV
215 | Classroom | 370 | 24 |  | 840 | 19 | 19 | Unit Ventilator
216 | Classroom | 388 | 25 |  | 805 | 18 | 18 | Unit Ventilator
217 | Classroom | 413 | 27 |  | 792 | 18 | 18 | Unit Ventilator
218 | Classroom | 328 | 21 |  | 625 | 14 | 14 | Unit Ventilator
218C | Classroom | 286 | 19 |  | 960 | 21 | 19 | Unit Ventilator
219 | Classroom | 862 | 57 |  | 1800 | 40 | 40 | Unit Ventilator
220 | Classroom | 980 | 65 |  | 1350 | 30 | 30 | Unit Ventilator
221 | Classroom | 342 | 22 |  | 625 | 14 | 14 | Unit Ventilator
234 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV
244 | Counselor | 0 | 0 |  |  | 0 | 0 | HUV
- | Nurse's Office | 279 | 18 |  | 150 | 3 | 3 | Unit Ventilator

## Blaine
Sheet Last Modified: | 2021-03-18
School: | James G. Blaine Elementary School
Vendor: | Devine Brothers Retest |  | 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Gym / Cafe. | 1104 | 73 |  | 3749 | 85 | 73 | Air Handling Unit
- | Auditorium | 577 | 38 |  | 3161 | 71 | 38 | Air Handling Unit
100 | Classroom | 437 | 29 |  | 1415 | 32 | 29 | Unit Ventilator
101 | Classroom | 684 | 45 |  | 1476 | 33 | 33 | Unit Ventilator
102 | Classroom | 625 | 41 |  | 1460 | 33 | 33 | Unit Ventilator
103 | Classroom | 461 | 30 |  | 1465 | 33 | 30 | Unit Ventilator
104 | Classroom | 319 | 21 |  | 856 | 19 | 19 | Unit Ventilator
105 | Classroom | 306 | 20 |  | 655 | 14 | 14 | Unit Ventilator
106 | Classroom | 452 | 30 |  | 921 | 20 | 20 | Unit Ventilator
107 | Classroom | 274 | 18 |  | 970 | 22 | 18 | Unit Ventilator
108 | Custodial | 251 | 16 |  | 835 | 18 | 16 | Unit Ventilator
110 | Nurse |  | 0 | Yes | 452.16 | 10 | 10 | Unit Ventilator
200 | Classroom | 297 | 19 |  | 947 | 21 | 19 | Unit Ventilator
201 | Classroom | 246 | 16 |  | 649 | 14 | 14 | Unit Ventilator
202 | Classroom | 414 | 27 |  | 936 | 21 | 21 | Unit Ventilator
203 | Classroom | 230 | 15 |  | 937 | 21 | 15 | Unit Ventilator
204 | Classroom | 359 | 23 |  | 958 | 21 | 21 | Unit Ventilator
205 | Classroom | 286 | 19 |  | 937 | 21 | 19 | Unit Ventilator
206 | Classroom | 447 | 29 |  | 952 | 21 | 21 | Unit Ventilator
207 | Classroom | 291 | 19 |  | 956 | 21 | 19 | Unit Ventilator
208 | Classroom | 314 | 20 |  | 968 | 22 | 20 | Unit Ventilator
209 | Classroom | 349 | 23 |  | 975 | 22 | 22 | Unit Ventilator
210 | Classroom | 236 | 15 |  | 931 | 21 | 15 | Unit Ventilator
211 | Classroom | 287 | 19 |  | 982 | 22 | 19 | Unit Ventilator
212 | Classroom | 362 | 24 |  | 953 | 21 | 21 | Unit Ventilator
213 | Classroom | 296 | 19 |  | 957 | 21 | 19 | Unit Ventilator
214 | Classroom | 378 | 25 |  | 956 | 21 | 21 | Unit Ventilator
215 | Classroom | 288 | 19 |  | 603 | 13 | 13 | Unit Ventilator
216 | Classroom | 406 | 27 |  | 942 | 21 | 21 | Unit Ventilator
217 | Classroom | 407 | 27 |  | 656 | 14 | 14 | Unit Ventilator
300 | Classroom | 332 | 22 |  | 956 | 21 | 21 | Unit Ventilator
301 | Classroom | 333 | 22 |  | 601 | 13 | 13 | Unit Ventilator
302 | Classroom | 249 | 16 |  | 864 | 19 | 16 | Unit Ventilator
303 | Classroom | 341 | 22 |  | 859 | 19 | 19 | Unit Ventilator
304 | Classroom | 270 | 18 |  | 863 | 19 | 18 | Unit Ventilator
305 | Classroom | 286 | 19 |  | 862 | 19 | 19 | Unit Ventilator
306 | Classroom | 254 | 16 |  | 861 | 19 | 16 | Unit Ventilator
307 | Classroom | 348 | 23 |  | 865 | 19 | 19 | Unit Ventilator
308 | Classroom | 334 | 22 |  | 859 | 19 | 19 | Unit Ventilator
309 | Classroom | 287 | 19 |  | 972 | 22 | 19 | Unit Ventilator
310 | Classroom | 324 | 21 |  | 852 | 19 | 19 | Unit Ventilator
311 | Classroom | 306 | 20 |  | 958 | 21 | 20 | Unit Ventilator
312 | Classroom | 483 | 32 |  | 950 | 21 | 21 | Unit Ventilator
313 | Classroom | 460 | 30 |  | 944 | 21 | 21 | Unit Ventilator
314 | Classroom | 238 | 15 |  | 951 | 21 | 15 | Unit Ventilator
315 | Classroom | 359 | 23 |  | 667 | 15 | 15 | Unit Ventilator
316 | Classroom | 315 | 21 |  | 952 | 21 | 21 | Unit Ventilator
317 | Classroom | 288 | 19 |  | 651 | 14 | 14 | Unit Ventilator
- | Main Office |  | 0 | Yes | 1235 | 28 | 28 | Unit Ventilator
- | Principal |  | 0 | Yes | 361 | 8 | 8 | Unit Ventilator

## Blankenburg
Sheet Last Modified: | 2021-04-20
School: | Randolph Blankenburg Elementary-Middle School |  |  |  | House fan Abated
Vendor: | Devine |  | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
K-1 | Classroom | 906 | 60 |  | 704 | 16 | 16 | House Fan
K-4 | Classroom | 828 | 55 |  | 704 | 16 | 16 | House Fan
B27 | Classroom | 517 | 34 |  | 1047 | 23 | 23 | House Fan
10A | Vice Principal | 0 | 0 | Yes | 176 | 4 | 4 | N/A
29 | Classroom | 594 | 39 |  | 704 | 16 | 16 | House Fan
30 | Classroom | 930 | 62 |  | 836 | 19 | 19 | House Fan
101 | Classroom | 890 | 59 |  | 704 | 16 | 16 | House Fan
102 | Classroom | 63 | 4 | Yes | 704 | 16 | 16 | House Fan
103 | Classroom | 954 | 63 |  | 704 | 16 | 16 | House Fan
105 | Classroom | 907 | 60 |  | 704 | 16 | 16 | House Fan
106 | Classroom | 988 | 65 |  | 704 | 16 | 16 | House Fan
107 | Classroom | 959 | 63 |  | 704 | 16 | 16 | House Fan
208 | Classroom | 620 | 41 |  | 704 | 16 | 16 | House Fan
208A | Nurse's Office | 0 | 0 |  | 176 | 4 | 0 | N/A
209 | Classroom | 695 | 46 |  | 704 | 16 | 16 | House Fan
210 | Classroom | 930 | 62 |  | 704 | 16 | 16 | House Fan
211 | Classroom | 887 | 59 |  | 704 | 16 | 16 | House Fan
212 | Classroom | 751 | 50 |  | 704 | 16 | 16 | House Fan
213 | Classroom | 955 | 63 |  | 704 | 16 | 16 | House Fan
214 | Classroom | 950 | 63 |  | 704 | 16 | 16 | House Fan
316 | Classroom | 0 | 0 | Yes | 880 | 20 | 20 | House Fan
317 | Classroom | 361 | 24 |  | 484 | 11 | 11 | House Fan
318 | Classroom | 588 | 39 |  | 704 | 16 | 16 | House Fan
319 | Classroom | 341 | 22 |  | 704 | 16 | 16 | House Fan
320 | Classroom | 483 | 32 |  | 704 | 16 | 16 | House Fan
321 | Classroom | 743 | 49 |  | 704 | 16 | 16 | House Fan
322 | Classroom | 877 | 58 |  | 704 | 16 | 16 | House Fan
323 | Classroom | 642 | 42 |  | 748 | 17 | 17 | House Fan
324 | Classroom | 818 | 54 |  | 704 | 16 | 16 | House Fan
325 | Classroom | 809 | 53 |  | 704 | 16 | 16 | House Fan
326 | Classroom | 565 | 37 |  | 704 | 16 | 16 | House Fan
327 | Classroom | 698 | 46 |  | 704 | 16 | 16 | House Fan
328 | Classroom | 151 | 10 | Yes | 704 | 16 | 16 | House Fan
329 | Classroom | 0 | 0 | Yes | 264 | 6 | 6 | House Fan
2121 | Storage | 0 | 0 | Yes | 399 | 9 | 9 | House Fan
- | Auditorium | 2451 | 163 |  | 3520 | 80 | 80 | House Fan
- | Counselor Office | 0 | 0 | Yes | 220 | 5 | 5 | N/A
- | Gym | 0 | 0 | Yes | 3872 | 88 | 88 | N/A
- | Kitchen | 634 | 42 |  | 880 | 20 | 20 | House Fan
- | Library | 865 | 57 |  | 1675 | 38 | 38 | House Fan
- | Main Office | 0 | 0 | Yes | 308 | 7 | 7 | N/A
- | Principal Office | 0 | 0 | Yes | 160 | 3 | 3 | N/A
- | SEL Classroom | 970 | 64 |  | 704 | 16 | 16 | House Fan
- | Staff Lounge | 0 | 0 | Yes | 399 | 9 | 9 | N/A

## Bodine
Sheet Last Modified: | 2021-03-17
School: | Bodine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
401 | Classroom |  | 0 |  | 660 | 15 | 0
402 | classroom |  | 0 |  | 616 | 14 | 0
403 | Classroom |  | 0 |  | 598 | 13 | 0
404 | Classroom |  | 0 |  | 644 | 14 | 0
405 A | Dept Head |  | 0 |  | 98 | 2 | 0
405 B | Counselor |  | 0 |  | 133 | 3 | 0
406 | Classroom |  | 0 |  | 672 | 15 | 0
407 | Classroom |  | 0 |  | 644 | 14 | 0
408 | Computer |  | 0 |  | 726 | 16 | 0
409 | Classroom |  | 0 |  | 638 | 14 | 0
301 | Classroom |  | 0 |  | 667 | 15 | 0
302 | Classroom |  | 0 |  | 638 | 14 | 0
303 | Classroom |  | 0 |  | 644 | 14 | 0
304 | Classroom |  | 0 |  | 621 | 14 | 0
305 | Faculty Area |  | 0 |  | 450 | 10 | 0
306 | Classroom |  | 0 |  | 644 | 14 | 0
307 | Classroom |  | 0 |  | 644 | 14 | 0
308 | Classrrom |  | 0 |  | 638 | 14 | 0
309 | Classroom |  | 0 |  | 638 | 14 | 0
201 | Classroom |  | 0 |  | 638 | 14 | 0
202 | Classroom |  | 0 |  | 660 | 15 | 0
203 | Library |  | 0 |  | 1058 | 24 | 0
203 | Library office |  | 0 |  | 140 | 3 | 0
205 | Classroom |  | 0 |  | 644 | 14 | 0
206 | Classroom |  | 0 |  | 621 | 14 | 0
207 | Classroom |  | 0 |  | 638 | 14 | 0
208 | Classroom |  | 0 |  | 638 | 14 | 0
102 | Classroom |  | 0 |  | 880 | 20 | 0
103 | Counselor |  | 0 |  | 110 | 2 | 0
104 | Teacher Lounge |  | 0 |  | 345 | 7 | 0
105 A | Office |  | 0 |  | 63 | 1 | 0
105 B | Office |  | 0 |  | 108 | 2 | 0
105 C | Office |  | 0 |  | 81 | 1 | 0
108 | Room |  | 0 |  | 638 | 14 | 0
109 | Room |  | 0 |  | 638 | 14 | 0
2 | Art Room |  | 0 |  | 484 | 11 | 0
- | Main Office |  | 0 |  | 322 | 7 | 0
- | Principal Office |  | 0 |  | 96 | 2 | 0
- | Conferance Room |  | 0 |  | 220 | 5 | 0
- | Gym / Lunchroom |  | 0 |  | 2760 | 62 | 0
- | Kitchen |  | 0 |  | 648 | 14 | 0

## Bregy
Sheet Last Modified: | 2021-04-28
School: | Amedee F. Bregy Elementary-Middle School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium | 6957 | 463 |  | 4017 | 91 | 91 | House Fan
- | Cafeteria | 934 | 62 |  | 1584 | 36 | 36 | House Fan
- | Gym | 0 | 0 | Yes | 3872 | 88 | 88 | House Fan
- | Library | 991 | 66 |  | 1739 | 39 | 39 | House Fan
- | Basement Science Classroom | 557 | 37 |  | 1064 | 24 | 24 | House Fan
- | Basement Storage | 143 | 9 |  | 396 | 9 | 9 | House Fan
- | Basement Boy's Bathroom | 471 | 31 |  | 528 | 12 | 12 | House Fan
- | Basement Girl's Bathroom | 434 | 28 |  | 528 | 12 | 12 | House Fan
101 | Classroom | 271 | 18 |  | 660 | 15 | 15 | House Fan
102 | Classroom | 312 | 20 |  | 660 | 15 | 15 | House Fan
1K1 | Classroom | 823 | 54 |  | 660 | 15 | 15 | House Fan
103 | Classroom | 51 | 3 |  | 650 | 14 | 3 | House Fan
104 | Classroom | 564 | 37 |  | 650 | 14 | 14 | House Fan
105 | Classroom | 255 | 17 |  | 616 | 14 | 14 | House Fan
106 | Classroom | 723 | 48 |  | 616 | 14 | 14 | House Fan
107 | Classroom | 664 | 44 |  | 616 | 14 | 14 | House Fan
208 | Classroom | 866 | 57 |  | 660 | 15 | 15 | House Fan
209 | Classroom | 751 | 50 |  | 660 | 15 | 15 | House Fan
210 | Classroom | 128 | 8 | Yes | 652 | 14 | 14 | House Fan
211 | Classroom | 663 | 44 |  | 616 | 14 | 14 | House Fan
212 | Classroom | 669 | 44 |  | 660 | 15 | 15 | House Fan
213 | Classroom | 694 | 46 |  | 660 | 15 | 15 | House Fan
214 | Classroom | 629 | 41 |  | 660 | 15 | 15 | House Fan
215 | Classroom | 279 | 18 |  | 660 | 15 | 15 | House Fan
316 | Classroom | 404 | 26 |  | 660 | 15 | 15 | House Fan
317 | Classroom | 0 | 0 | Yes | 656 | 14 | 14 | House Fan
318 | Classroom | 577 | 38 |  | 660 | 15 | 15 | House Fan
319 | Classroom | 231 | 15 |  | 660 | 15 | 15 | House Fan
320 | Classroom | 726 | 48 |  | 704 | 16 | 16 | House Fan
321 | Classroom | 298 | 19 |  | 704 | 16 | 16 | House Fan
322 | Classroom | 511 | 34 |  | 704 | 16 | 16 | House Fan
323 | Classroom | 702 | 46 |  | 660 | 15 | 15 | House Fan
324 | Classroom | 375 | 25 |  | 660 | 15 | 15 | House Fan
325 | Classroom | 623 | 41 |  | 616 | 14 | 14 | House Fan
326 | Classroom | 557 | 37 |  | 654 | 14 | 14 | House Fan
327 | Classroom | 525 | 35 |  | 654 | 14 | 14 | House Fan
328 | Classroom | 664 | 44 |  | 660 | 15 | 15 | House Fan
- | Principal Office |  | 0 | Yes | 108 | 2 | 2 | House Fan
- | Nurse Office |  | 0 | Yes | 220 | 5 | 5 | House Fan

## Bridesburg
Sheet Last Modified: | 2021-04-07
School: | Bridesburg Elementary School
Vendor: | Goldner | Goldner Part 2
Devine Annex Retest
School: | Bridesburg Elementary School Annex
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
102 | Classroom | 422 | 28 |  | 846 | 19 | 19 | Unit Ventilator
103 | Classroom | 377 | 25 |  | 686 | 15 | 15 | Unit Ventilator
104 | Classroom | 476 | 31 |  | 993 | 22 | 22 | Unit Ventilator
105 | Classroom | 300 | 20 |  | 672 | 15 | 15 | Unit Ventilator
106 | Classroom | 536 | 35 |  | 972 | 22 | 22 | Unit Ventilator
107 | Classroom | 334 | 22 |  | 737 | 16 | 16 | Unit Ventilator
108 | Classroom | 322 | 21 |  | 1030 | 23 | 21 | Unit Ventilator
109 | Classroom | 294 | 19 |  | 684 | 15 | 15 | Unit Ventilator
110A | Counselor's Office | 198 | 13 |  | 130 | 2 | 2 | Unit Ventilator
111 | Classroom | 372 | 24 |  | 253 | 5 | 5 | Unit Ventilator
112 | Nurse's Office | 272 | 18 |  | 369 | 8 | 8 | Unit Ventilator
112A | Classroom | 0 | 0 |  | 218 | 4 | 0 | Unit Ventilator
112B | Classroom | 0 | 0 |  | 218 | 4 | 0 | Unit Ventilator
113 | Classroom | 137 | 9 |  | 117 | 2 | 2 | Unit Ventilator
114 | Classroom | 327 | 21 |  | 930 | 21 | 21 | Unit Ventilator
115 | Classroom | 281 | 18 |  | 659 | 14 | 14 | Unit Ventilator
116 | Library | 1510 | 100 |  | 1700 | 38 | 38 | Unit Ventilator
200 | Classroom | 0 | 0 | Yes | 754 | 17 | 17 | Unit Ventilator
201 | Classroom | 136 | 9 |  | 609 | 13 | 9 | Unit Ventilator
202 | Classroom | 312 | 20 |  | 539 | 12 | 12 | Unit Ventilator
203 | Classroom | 377 | 25 |  | 714 | 16 | 16 | Unit Ventilator
204 | Classroom | 152 | 10 |  | 695 | 15 | 10 | Unit Ventilator
205 | Classroom | 1577 | 105 |  | 1129 | 25 | 25 | Unit Ventilator
206 | Classroom | 157 | 10 |  | 715 | 16 | 10 | Unit Ventilator
207 | Classroom | 247 | 16 |  | 725 | 16 | 16 | Unit Ventilator
208 | Classroom | 351 | 23 |  | 650 | 14 | 14 | Unit Ventilator
209 | Classroom | 0 | 0 | Yes | 709 | 16 | 16 | Unit Ventilator
210 | Classroom | 147 | 9 |  | 759 | 17 | 9 | Unit Ventilator
211 | Classroom | 147 | 9 |  | 735 | 16 | 9 | Unit Ventilator
212 | Classroom | 180 | 12 |  | 787 | 17 | 12 | Unit Ventilator
213 | Classroom | 283 | 18 |  | 665 | 15 | 15 | Unit Ventilator
214 | Classroom | 1248 | 83 |  | 845 | 19 | 19 | Unit Ventilator
215 | Classroom | 457 | 30 |  | 677 | 15 | 15 | Unit Ventilator
217 | Classroom | 282 | 18 |  | 735 | 16 | 16 | Unit Ventilator
218 | Classroom | 292 | 19 |  | 601 | 13 | 13 | Unit Ventilator
220 | Classroom | 287 | 19 |  | 706 | 16 | 16 | Unit Ventilator
- | Hallway |  | 0 |  |  | 0 | 0 | HRU
- | Hallway 2 |  | 0 |  |  | 0 | 0 | HRU
- | Hallway Right |  | 0 |  |  | 0 | 0 | HRU
- | Hallways 2 Center |  | 0 |  |  | 0 | 0 | HRU
- | Gym | 0 | 0 |  | 3925 | 89 | 0 | N/A
- | Cafeteria | 0 | 0 |  | 3080 | 70 | 0 | N/A
- | Kitchen | 0 | 0 |  | 697 | 15 | 0 | N/A
- | Main Office | 1167 | 77 |  | 752 | 17 | 17 | HRU
Bridesburg Elementary School Annex
1 | Classroom |  | 0 | Yes | 710 | 16 | 16 | N/A
2 | Staff Lounge |  | 0 | Yes | 504 | 11 | 11 | N/A
3 | Classroom |  | 0 | Yes | 575 | 13 | 13 | N/A
4 | Vice Principal |  | 0 | Yes | 245 | 5 | 5 | N/A
5 | Classroom |  | 0 | Yes | 693 | 15 | 15 | N/A
6 | Classroom |  | 0 | Yes | 732 | 16 | 16 | N/A
7 | Classroom |  | 0 | Yes | 773 | 17 | 17 | N/A
8 | Classroom |  | 0 | Yes | 589 | 13 | 13 | N/A
9 | Classroom |  | 0 | Yes | 610 | 13 | 13 | N/A
10 | Classroom |  | 0 | Yes | 623 | 14 | 14 | N/A
11 | Classroom |  | 0 | Yes | 581 | 13 | 13 | N/A
12 | Classroom |  | 0 | Yes | 569 | 12 | 12 | N/A
13 | Classroom |  | 0 | Yes | 625 | 14 | 14 | N/A
14 | Classroom |  | 0 | Yes | 576 | 13 | 13 | N/A
15 | Classroom |  | 0 | Yes | 547 | 12 | 12 | N/A
- | Support Room |  | 0 | Yes | 140 | 3 | 3 | N/A
- | Speech Room |  | 0 | Yes | 152 | 3 | 3 | N/A
- | Nurse Office |  | 0 | Yes | 144 | 3 | 3 | N/A
- | Main Office |  | 0 | Yes | 334 | 7 | 7 | N/A

## Brown, HA
Sheet Last Modified: | 2021-04-23
School: | Henry A. Brown Elementary School
Vendor: | Devine | Retest Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Admin | 418 | 27 |  | 1058 | 24 | 24 | FCU
- | Cafeteria | 2904 | 193 |  | 1994 | 45 | 45 | AHU
- | Gym | 1581 | 105 |  | 3360 | 76 | 76 | AHU
- | Library | 488 | 32 |  | 1486 | 33 | 32 | FCU
- | Nurses Room | 133 | 8 |  | 290 | 6 | 6 | FCU
- | Outside Library | 366 | 24 |  | 900 | 20 | 20 | FCU
100 | Classroom | 328 | 21 |  | 705 | 16 | 16 | Unit Ventilator
101 | Classroom | 395 | 26 |  | 730 | 16 | 16 | Unit Ventilator
113 | Classroom | 296 | 19 |  | 745 | 16 | 16 | Unit Ventilator
114 | Classroom | 309 | 20 |  | 700 | 15 | 15 | Unit Ventilator
151 | Classroom | 779 | 51 |  | 784 | 17 | 17 | FCU
153 | Classroom | 689 | 45 |  | 895 | 20 | 20 | FCU
154 | Classroom | 590 | 39 |  | 780 | 17 | 17 | FCU
156 | Classroom | 647 | 43 |  | 835 | 18 | 18 | FCU
200 | Classroom | 608 | 40 |  | 905 | 20 | 20 | Unit Ventilator
201 | Classroom | 633 | 42 |  | 900 | 20 | 20 | Unit Ventilator
202 | Classroom |  | 0 | Yes | 655 | 14 | 14
206 | Classroom |  | 0 | Yes | 795 | 18 | 18
209 | Classroom |  | 0 | Yes | 655 | 14 | 14
211 | Classroom | 470 | 31 |  | 895 | 20 | 20 | Unit Ventilator
212 | Classroom | 307 | 20 |  | 905 | 20 | 20 | Unit Ventilator
213 | Classroom | 782 | 52 |  | 875 | 19 | 19 | Unit Ventilator
214 | Classroom | 616 | 41 |  | 875 | 19 | 19 | Unit Ventilator
217 | Classroom | 250 | 16 |  | 665 | 15 | 15 | Unit Ventilator
226 South | Classroom | 405 | 27 |  | 777 | 17 | 17 | Unit Ventilator
226 West | Classroom | 458 | 30 |  | 777 | 17 | 17 | Unit Ventilator
227 | Classroom | 487 | 32 |  | 740 | 16 | 16 | Unit Ventilator
228 | Classroom | 685 | 45 |  | 775 | 17 | 17 | Unit Ventilator
229 | Computer Lab | 103 | 6 | Yes | 990 | 22 | 22 | FCU
300 | Classroom | 582 | 38 |  | 905 | 20 | 20 | Unit Ventilator
301 | Classroom | 535 | 35 |  | 890 | 20 | 20 | Unit Ventilator
302 | Classroom | 151 | 10 |  | 695 | 15 | 10 | Unit Ventilator
304 | Classroom | 445 | 29 |  | 825 | 18 | 18 | Unit Ventilator
310 | Classroom | 657 | 43 |  | 715 | 16 | 16 | Unit Ventilator
311 | Classroom | 241 | 16 |  | 935 | 21 | 16 | Unit Ventilator
312 | Classroom | 426 | 28 |  | 935 | 21 | 21 | Unit Ventilator
313 | Classroom | 327 | 21 |  | 920 | 20 | 20 | Unit Ventilator
314 | Classroom | 512 | 34 |  | 920 | 20 | 20 | Unit Ventilator
317 | Classroom | 165 | 11 |  | 660 | 15 | 11 | Unit Ventilator
318 | Classroom | 473 | 31 |  | 1090 | 24 | 24 | FCU
319 | Classroom | 284 | 18 |  | 1125 | 25 | 18 | FCU
322 South | Classroom | 174 | 11 |  | 745 | 16 | 11 | Unit Ventilator
322 West | Classroom | 107 | 7 |  | 745 | 16 | 7 | Unit Ventilator
323 | Classroom | 472 | 31 |  | 730 | 16 | 16 | Unit Ventilator
324 | Classroom | 784 | 52 |  | 765 | 17 | 17 | Unit Ventilator
325 West | Classroom | 533 | 35 |  | 890 | 20 | 20 | Unit Ventilator
325 North | Classroom | 581 | 38 |  | 890 | 20 | 20 | Unit Ventilator

## Brown, JH
Sheet Last Modified: | 2021-04-27
School: | Joseph H. Brown Elementary School
Vendor: | Emcor Mechanical Retest |  | Emcor Exhaust Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | GYM | 921 | 61 |  | 3510 | 79 | 61 | Unit Ventilator
- | CAFE | 921 | 61 |  | 1440 | 32 | 32 | Unit Ventilator
101 | classroom | 519 | 34 |  | 667 | 15 | 15 | Unit Ventilator
102 | classroom | 562 | 37 |  | 667 | 15 | 15 | Unit Ventilator
103 | classroom | 358 | 23 |  | 713 | 16 | 16 | Unit Ventilator
104 | classroom | 932 | 62 |  | 851 | 19 | 19 | Unit Ventilator
105 | classroom | 844 | 56 |  | 920 | 20 | 20 | Unit Ventilator
106 | classroom | 786 | 52 |  | 920 | 20 | 20 | Unit Ventilator
107 | classroom | 985 | 65 |  | 1104 | 25 | 25 | Unit Ventilator
108 | classroom | 836 | 55 |  | 851 | 19 | 19 | Unit Ventilator
109 | Counselor Office |  | 0 | Yes | 112 | 2 | 2
110 | Nurse Room |  | 0 |  | 224 | 5 | 0 | N/A
111 | Medical Waiting |  | 0 | Yes | 120 | 2 | 2
200 | Classroom |  | 0 | Yes | 667 | 15 | 15
201 | classroom | 394 | 26 |  | 690 | 15 | 15 | Unit Ventilator
202 | classroom | 0 | 0 | Yes | 667 | 15 | 15 | Unit Ventilator
203 | classroom | 417 | 27 |  | 667 | 15 | 15 | Unit Ventilator
204 | classroom | 408 | 27 |  | 690 | 15 | 15 | Unit Ventilator
205 | classroom | 550 | 36 |  | 690 | 15 | 15 | Unit Ventilator
206 | classroom | 750 | 50 |  | 950 | 21 | 21 | Unit Ventilator
206A | Room |  | 0 | Yes | 288 | 6 | 6
207 | classroom | 484 | 32 |  | 506 | 11 | 11 | Unit Ventilator
207A | Office |  | 0 | Yes | 168 | 3 | 3
208 | classroom | 513 | 34 |  | 690 | 15 | 15 | Unit Ventilator
209 | classroom | 723 | 48 |  | 713 | 16 | 16 | Unit Ventilator
210 | classroom | 495 | 33 |  | 713 | 16 | 16 | Unit Ventilator
211 | classroom | 376 | 25 |  | 667 | 15 | 15 | Unit Ventilator
300 | classroom |  | 0 | Yes | 150 | 3 | 3
301 | classroom | 605 | 40 |  | 667 | 15 | 15 | Unit Ventilator
302 | classroom | 457 | 30 |  | 690 | 15 | 15 | Unit Ventilator
303 | classroom | 389 | 25 |  | 690 | 15 | 15 | Unit Ventilator
304 | classroom | 469 | 31 |  | 713 | 16 | 16 | Unit Ventilator
305 | classroom | 0 | 0 | Yes | 713 | 16 | 16 | Unit Ventilator
306 | classroom | 0 | 0 | Yes | 874 | 19 | 19 | Unit Ventilator
307 | classroom | 419 | 27 |  | 690 | 15 | 15 | Unit Ventilator
308 | classroom |  | 0 | Yes | 713 | 16 | 16
Principal | Office |  | 0 | Yes | 160 | 3 | 3
- | Main Office |  | 0 | Yes | 368 | 8 | 8 | N/A

## Bryant
Sheet Last Modified: | 2021-04-29
School: | William C Bryant Elementary School |  |  | House fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Gym | 1521 | 101 |  | 2765 | 62 | 62 | House Fan
- | Shop Classroom | 795 | 53 |  | 740 | 16 | 16 | House Fan
- | Art Room | 0 | 0 |  | 740 | 16 | 0 | House Fan
- | Cafeteria/Auditorium | 1853 | 123 |  | 2479 | 56 | 56 | AHU
- | Principal's Office | 0 | 0 | Yes | 204 | 4 | 4 | House Fan
- | Office | 0 | 0 |  | 135 | 3 | 0 | House Fan
101 | Classroom | 1717 | 114 |  | 1013 | 23 | 23 | House Fan
102 | Classroom | 888 | 59 |  | 696 | 15 | 15 | House Fan
103 | Classroom | 853 | 56 |  | 690 | 15 | 15 | House Fan
104 | Classroom | 653 | 43 |  | 740 | 16 | 16 | House Fan
105 | Classroom | 0 | 0 | Yes | 700 | 15 | 15 | House Fan
106 | Classroom | 0 | 0 | Yes | 740 | 16 | 16 | House Fan
107 | Classroom | 0 | 0 | Yes | 718 | 16 | 16 | House Fan
108 | Classroom | 0 | 0 | Yes | 795 | 18 | 18 | House Fan
110 | Nurse Office | 0 | 0 | Yes | 219 | 4 | 4 | House Fan
111 | - |  | 0 |  | 731 | 16 | 0 | House Fan
112 | Main Office |  | 0 | Yes | 707 | 16 | 16 | House Fan
113 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | House Fan
114 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan
201 | Classroom | 1845 | 123 |  | 1013 | 23 | 23 | House Fan
202 | Classroom | 843 | 56 |  | 686 | 15 | 15 | House Fan
203 | Classroom | 108 | 7 | Yes | 690 | 15 | 15 | House Fan
204 | Classroom | 893 | 59 |  | 740 | 16 | 16 | House Fan
205 | Classroom | 0 | 0 | Yes | 700 | 15 | 15 | House Fan
206 | Classroom | 0 | 0 | Yes | 740 | 16 | 16 | House Fan
207 | Classroom | 0 | 0 | Yes | 718 | 16 | 16 | House Fan
208 | Classroom | 0 | 0 | Yes | 795 | 18 | 18 | House Fan
209 | Classroom | 0 | 0 |  | 753 | 17 | 0 | House Fan
210 | Classroom | 0 | 0 | Yes | 715 | 16 | 16 | House Fan
211 | Classroom | 0 | 0 |  | 731 | 16 | 0 | House Fan
212 | Classroom | 0 | 0 | Yes | 707 | 16 | 16 | House Fan
213 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | House Fan
214 | Classroom | 0 | 0 |  | 713 | 16 | 0 | House Fan
- | IMC - Library | 0 | 0 |  | 2788 | 63 | 0 | Roof Top Unit
- | 2nd Flr Teacher's Lounge | 0 | 0 |  | 349 | 7 | 0 | House Fan
301 | Classroom | 387 | 25 |  | 1013.111 | 23 | 23 | House Fan
302 | Classroom | 748 | 49 |  | 685.59 | 15 | 15 | House Fan
303 | Classroom | 68 | 4 | Yes | 689.813 | 15 | 15 | House Fan
304 | Classroom | 156 | 10 | Yes | 739.958 | 16 | 16 | House Fan
305 | Classroom | 0 | 0 | Yes | 699.639 | 15 | 15 | House Fan
306 | Classroom | 0 | 0 | Yes | 740.139 | 16 | 16 | House Fan
307 | Classroom | 0 | 0 |  | 717.889 | 16 | 0 | House Fan
308 | Classroom | 0 | 0 |  | 795.375 | 18 | 0 | House Fan
309 | Classroom | 0 | 0 |  | 753.194 | 17 | 0 | House Fan
310 | Classroom | 0 | 0 | Yes | 714.583 | 16 | 16 | House Fan
311 | Classroom | 0 | 0 | Yes | 731.354 | 16 | 16 | House Fan
312 | Classroom | 0 | 0 | Yes | 707.292 | 16 | 16 | House Fan
313 | Classroom | 0 | 0 | Yes | 674.09 | 15 | 15 | House Fan
314 | Classroom | 0 | 0 | Yes | 712.917 | 16 | 16 | House Fan
- | 3rd Flr Teacher's Lounge | 0 | 0 |  | 349 | 7 | 0 | House Fan

## Building 21 (Kinsey)
Sheet Last Modified: | 2021-03-17
School: | Building 21 (Kinsey)
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
600 | Classroom |  | 0 |  | 810 | 18 | 0
2 | Classroom |  | 0 |  | 1104 | 25 | 0
4 | Classroom |  | 0 |  | 884 | 20 | 0
5 | Kitchen |  | 0 |  | 910 | 20 | 0
112 | Classroom |  | 0 |  | 710 | 16 | 0
112A | Nurse |  | 0 |  | 99 | 2 | 0
111 | Office |  | 0 |  | 319 | 7 | 0
111A | Office |  | 0 |  | 140 | 3 | 0
111B | Office |  | 0 |  | 168 | 3 | 0
113 | Office |  | 0 |  | 475 | 10 | 0
113A | Office |  | 0 |  | 81 | 1 | 0
113B | Office |  | 0 |  | 81 | 1 | 0
110 | Main Office |  | 0 |  | 710 | 16 | 0
115 | Classroom |  | 0 |  | 140 | 3 | 0
114 | Classroom |  | 0 |  | 81 | 1 | 0
109 | Classroom |  | 0 |  | 710 | 16 | 0
108 | Classroom |  | 0 |  | 710 | 16 | 0
107 | Classroom |  | 0 |  | 710 | 16 | 0
106 | Classroom |  | 0 |  | 710 | 16 | 0
105 | Classroom |  | 0 |  | 710 | 16 | 0
104 | Classroom |  | 0 |  | 710 | 16 | 0
103 | Classroom |  | 0 |  | 710 | 16 | 0
102 | Classroom |  | 0 |  | 710 | 16 | 0
101 | Classroom |  | 0 |  | 710 | 16 | 0
116 | Aud |  | 0 |  | 5244 | 119 | 0
201 | Classroom |  | 0 |  | 710 | 16 | 0
202 | Classroom |  | 0 |  | 710 | 16 | 0
203 | Classroom |  | 0 |  | 710 | 16 | 0
204 | Classroom |  | 0 |  | 710 | 16 | 0
205 | Classroom |  | 0 |  | 710 | 16 | 0
206 | Classroom |  | 0 |  | 710 | 16 | 0
207 | Classroom |  | 0 |  | 710 | 16 | 0
208 | Classroom |  | 0 |  | 710 | 16 | 0
210 | Classroom |  | 0 |  | 710 | 16 | 0
211 | Classroom |  | 0 |  | 710 | 16 | 0
212 | Classroom |  | 0 |  | 710 | 16 | 0
213 | Nurse |  | 0 |  | 295 | 6 | 0
214 | Office |  | 0 |  | 140 | 3 | 0
209 | Classroom |  | 0 |  | 710 | 16 | 0
215 | Office |  | 0 |  | 140 | 3 | 0
301 | Classroom |  | 0 |  | 710 | 16 | 0
302 | Classroom |  | 0 |  | 710 | 16 | 0
303 | Classroom |  | 0 |  | 710 | 16 | 0
304 | Classroom |  | 0 |  | 710 | 16 | 0
305 | Classroom |  | 0 |  | 710 | 16 | 0
306 | Classroom |  | 0 |  | 710 | 16 | 0
307 | Classroom |  | 0 |  | 710 | 16 | 0
308 | Classroom |  | 0 |  | 710 | 16 | 0
309 | Classroom |  | 0 |  | 710 | 16 | 0
310 | Classroom |  | 0 |  | 710 | 16 | 0
311 | Classroom |  | 0 |  | 710 | 16 | 0

## Boone (Camelot)
Sheet Last Modified: | 2021-04-21
School: | Camelot Academy @ Boone
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
300 | Office | 292 | 19 |  | 369.81 | 8 | 8 | Univent
301 | Classroom | 335 | 22 |  | 803.41 | 18 | 18 | Univent
302 | Classroom | 281 | 18 |  | 816.25 | 18 | 18 | Univent
304 | Classroom | 292 | 19 |  | 1807.5 | 41 | 19 | Univent
305 (309) | Classroom | 330 | 22 |  | 850.95 | 19 | 19 | Univent
306 | Classroom | 364 | 24 |  | 966.46 | 21 | 21 | Univent
307 | Classroom | 348 | 23 |  | 1647.3 | 37 | 23 | Univent
308 | Office | 266 | 17 |  | 493.64 | 11 | 11 | Univent
310 | Office | 135 | 9 |  | 399.45 | 9 | 9 | Univent
312 | Classroom | 293 | 19 |  | 663.1 | 15 | 15 | Univent
314 | Classroom | 218 | 14 |  | 458.07 | 10 | 10 | Univent
316 | Classroom | 367 | 24 |  | 876.97 | 19 | 19 | Univent
- | Principal Office | 424 | 28 |  | 312.32 | 7 | 7 | ERU
200 | Classroom | 332 | 22 |  | 806.83 | 18 | 18 | Univent
201 | Classroom | 305 | 20 |  | 593.3 | 13 | 13 | Univent
202 | Classroom | 287 | 19 |  | 589.22 | 13 | 13 | Univent
204 | Classroom | 300 | 20 |  | 1083.8 | 24 | 20 | Univent
206 | Classroom | 434 | 28 |  | 961.67 | 21 | 21 | Univent
207 | Classroom | 326 | 21 |  | 880 | 20 | 20 | Univent
208 | Office | 239 | 15 |  | 493.64 | 11 | 11 | Univent
209 | Classroom | 349 | 23 |  | 878.57 | 19 | 19 | Univent
- | Academic Office | 308 | 20 |  | 311.45 | 7 | 7 | Univent
- | Operations Office | 348 | 23 |  | 395.34 | 8 | 8 | ERU
212 | Classroom | 380 | 25 |  | 566.59 | 12 | 12 | Univent
214 | Classroom | 397 | 26 |  | 651.81 | 14 | 14 | Univent
216 | Classroom | 408 | 27 |  | 651.14 | 14 | 14 | Univent
104 | Conference Room | 424 | 28 |  | 496.97 | 11 | 11 | Univent
- | Main Office | 372 | 24 |  | 1055.1 | 23 | 23 | Univent
102 | Computer Lab | 304 | 20 | Yes | 1019 | 23 | 23 | Univent
B5 | Classroom | 310 | 20 |  | 1248.01 | 28 | 20 | Univent
B6 | Cosmo Room 1 | 290 | 19 |  | 535.45 | 12 | 12 | Univent
B7 | Hair Salon | 443 | 29 |  | 692.67 | 15 | 15 | Univent
B8 | Barbershop | 275 | 18 |  | 539.35 | 12 | 12 | Univent

## CAPA High
Sheet Last Modified: | 2021-04-14
School: | Philadelphia High School for the Creative & Performing Arts
Vendor: | Chadwick | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
109 | Room | 714 | 47 |  | 1215.8 | 27 | 27
108 | Room | 0 | 0 |  | 872.49 | 19 | 0
107 | Room | 468 | 31 |  | 1182.7 | 26 | 26
105 | Room | 0 | 0 |  | 1171.6 | 26 | 0
110 | Office | 45 | 3 |  | 171.71 | 3 | 3
- | First Floor North Corridor | 290 | 19 |  | 3004.3 | 68 | 19
- | First Floor South Corridor | 118 | 7 |  | 1139.3 | 25 | 7
116 | Room | -100 | -6 |  | 216.61 | 4 | -6
106 | Editing Suite | 15 | 1 |  | 112.47 | 2 | 1
106 | Room |  | 0 |  | 1119.1 | 25 | 0
114 | Room | -61 | -4 |  | 845.65 | 19 | -4
116 | Control Room | 219 | 14 |  | 327.76 | 7 | 7
- | Second Floor South Corridor Outside Stair 4 | 45 | 3 |  | 2223.7 | 50 | 3
- | Second Floor South Corridor | 0 | 0 |  | 1642.3 | 37 | 0
- | Second Floor North Corridor | 301 | 20 |  | 1642.3 | 37 | 20
202 | Room | 78 | 5 |  | 275.81 | 6 | 5
203 | Room | 142 | 9 |  | 1209.4 | 27 | 9
204 | Room | 616 | 41 |  | 1059.9 | 24 | 24
205 | Room | 607 | 40 |  | 874.01 | 19 | 19
206 | Room | 0 | 0 |  | 1206.6 | 27 | 0
207 | Room | 613 | 40 |  | 891.99 | 20 | 20
208 | Room | 809 | 53 |  | 870.75 | 19 | 19
209 | Room | 584 | 38 |  | 871.76 | 19 | 19
210 | Room | 304 | 20 |  | 791.75 | 17 | 17
211 | Room | 420 | 28 |  | 1119.8 | 25 | 25
213 | Room | -85 | -5 |  | 815.15 | 18 | -5
214 | Room | 567 | 37 |  | 1351.8 | 30 | 30
304 | Room | 15 | 1 |  | 1059.9 | 24 | 1
305 | Room | 70 | 4 |  | 192.7 | 4 | 4
306 | Room | 122 | 8 |  | 888.58 | 20 | 8
307 | Room | 0 | 0 |  | 251.97 | 5 | 0
308 | Room | 533 | 35 |  | 1094.9 | 24 | 24
310 | Room | 527 | 35 |  | 877.6 | 19 | 19
311 | Room | 824 | 54 |  | 1209 | 27 | 27
312 | Room | 101 | 6 |  | 892.16 | 20 | 6
313 | Room | -121 | -8 |  | 870.18 | 19 | -8
314 | Room | 342 | 22 |  | 771.96 | 17 | 17
315 | Room | -455 | -30 |  | 888.8 | 20 | -30
316 | Room | 1080 | 72 |  | 1532.3 | 34 | 34
317 | Room | 754 | 50 |  | 850.53 | 19 | 19
318 | Room | 849 | 56 |  | 1015 | 23 | 23
320 | Room | -20 | -1 |  | 94.85 | 2 | -1
321 | Room | -15 | -1 |  | 77.87 | 1 | -1
322 | Room | -17 | -1 |  | 58.45 | 1 | -1
323 | Room | 35 | 2 |  | 1013.7 | 23 | 2
324 | Room | 30 | 2 |  | 257.05 | 5 | 2
326 | Room | -297 | -19 |  |  | 0 | -19
- | Third Floor North Corridor | 303 | 20 |  | 1655.3 | 37 | 20
- | Third Floor South Corridor | 0 | 0 |  | 1655.3 | 37 | 0
400 | Room | 932 | 62 |  | 1893.6 | 43 | 43
401 | Room | 302 | 20 |  | 1794.2 | 40 | 20
402 | Room | 615 | 41 |  | 2176.1 | 49 | 41
403 | Room | -67 | -4 |  | 216.87 | 4 | -4
403 | Print Room | 130 | 8 |  | 275.87 | 6 | 6
403 | Room | 52 | 3 |  | 2280.1 | 51 | 3
404 | Room | 226 | 15 |  | 1882.5 | 42 | 15
405 | Room | 390 | 26 |  | 1656.39 | 37 | 26
405 | Prep Room | 45 | 3 |  |  | 0 | 0
406 | Room | 710 | 47 |  |  | 0 | 0
407 | Room | 113 | 7 |  |  | 0 | 0
408 | Room | 0 | 0 |  | 217.94 | 4 | 0
- | 4th Floor Corridor South | 0 | 0 |  | 1677.4 | 38 | 0

## Carnell
Sheet Last Modified: | 2021-04-23
School: | Laura H. Carnell Elementary School
| Laura H. Carnell Little School House |  |  | House Fan Abated
Vendor: | Devine Brothers | LSH Retest
| EMCOR | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
- | Basement Corridor | 0 | 0 |  | 450 | 10 | 0 | Unit Ventilator
- | Gym Office | 0 | 0 |  | 144 | 3 | 0 | N/A
B-3 | Art | 0 | 0 |  | 920 | 20 | 0 | House Fan
B-4 | Music | 0 | 0 |  | 660 | 15 | 0 | House Fan
B1 | Counselors | 0 | 0 |  | 630 | 14 | 0 | House Fan
B2 | Family Resource | 0 | 0 |  | 1023 | 23 | 0 | House Fan
B5 | Classroom | 519 | 34 |  | 800 | 18 | 18 | Unit Ventilator
B6 | Classroom | 110 | 7 |  | 800 | 18 | 7 | Unit Ventilator
B7 | Classroom | 421 | 28 |  | 800 | 18 | 18 | Unit Ventilator
- | 1st flr Corridor |  | 0 |  | 828 | 18 | 0 | Unit Ventilator
- | Main Office | 0 | 0 |  | 483 | 10 | 0 | N/A
- | Principal's Office | 0 | 0 |  | 304 | 6 | 0 | N/A
- | 1st Flr Security | 0 | 0 |  | 81 | 1 | 0 | N/A
- | 1st Flr Counselors | 0 | 0 |  | 126 | 2 | 0 | N/A
- | 1st Flr Office |  | 0 |  | 216 | 4 | 0 | N/A
101 | Classroom | 0 | 0 | Yes | 957 | 21 | 21 | House Fan
102 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan
103 | Classroom | 0 | 0 |  | 899 | 20 | 0 | House Fan
104 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | House Fan
105 | Classroom | 0 | 0 |  | 900 | 20 | 0 | House Fan
106 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan
107 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan
108 | Classroom | 0 | 0 | Yes | 930 | 21 | 21 | House Fan
109 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan
110 | Classroom | 0 | 0 |  | 960 | 21 | 0 | House Fan
111 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan
112 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan
113 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan
- | 2nd flr Corridor |  | 0 |  | 828 | 18 | 0 | Unit Ventilator
- | 2nd Flr Nurse's | 0 | 0 |  | 216 | 4 | 0 | N/A
- | 2nd Flr. Office | 0 | 0 |  | 126 | 2 | 0 | N/A
- | Asst. Principal | 0 | 0 |  | 312 | 7 | 0 | N/A
201 | Classroom | 0 | 0 | Yes | 928 | 21 | 21 | House Fan
202 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan
203 | Classroom | 0 | 0 |  | 899 | 20 | 0 | House Fan
206 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan
207 | Classroom | 0 | 0 |  | 900 | 20 | 0 | House Fan
208 | Classroom | 0 | 0 | Yes | 930 | 21 | 21 | House Fan
209 | Computer Lab | 0 | 0 |  | 900 | 20 | 0 | House Fan
210 | Computer Lab | 0 | 0 |  | 960 | 21 | 0 | House Fan
211 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan
212 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan
213 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan
217 | Teachers Lounge | 0 | 0 |  | 552 | 12 | 0 | N/A
- | 3rd flr Corridor |  | 0 |  | 828 | 18 | 0 | Unit Ventilator
- | 3rd Flr. Office | 0 | 0 |  | 126 | 2 | 0 | N/A
300 East | Classroom | 0 | 0 |  | 720 | 16 | 0 | House Fan
300 West | Office | 0 | 0 |  | 99 | 2 | 0 | N/A
301 | Classroom | 0 | 0 | Yes | 928 | 21 | 21 | House Fan
302 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | House Fan
303 | Classroom | 0 | 0 |  | 899 | 20 | 0 | House Fan
304 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | House Fan
305 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan
306 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan
307 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan
308 | Classroom | 0 | 0 | Yes | 930 | 21 | 21 | House Fan
309 | Classroom | 0 | 0 |  | 900 | 20 | 0 | House Fan
310 | Classroom | 0 | 0 |  | 960 | 21 | 0 | House Fan
312 | Classroom | 544 | 36 |  | 768 | 17 | 17 | Unit Ventilator
313 | Classroom | 479 | 31 |  | 768 | 17 | 17 | Unit Ventilator
314 | Classroom | 65 | 4 |  | 768 | 17 | 4 | Unit Ventilator
317 | Speech | 0 | 0 |  | 117 | 2 | 0 | N/A
- | Auditorium | 0 | 0 |  | 3456 | 78 | 0 | House Fan
- | Cafeteria | 0 | 0 |  | 986 | 22 | 0 | N/A
- | Dean's Office | 0 | 0 |  | 108 | 2 | 0 | N/A
- | Gym | 0 | 0 |  | 3306 | 75 | 0 | N/A
- | IMC Classroom | 0 | 0 |  | 1363 | 30 | 0 | House Fan
- | IMC Office | 0 | 0 |  | 95 | 2 | 0 | House Fan
Little School House
A-1 | Classroom | 293 | 19 |  | 1056 | 24 | 19 | AHU
A-3 | Classroom | 296 | 19 |  | 1056 | 24 | 19 | AHU
A-2 | Classroom | 331 | 22 |  | 1056 | 24 | 22 | AHU
A-4 | Classroom | 343 | 22 |  | 1056 | 24 | 22 | AHU
A-5 | Classroom |  | 0 |  | 1056 | 24 | 0 | BCU
A-5 | Storage |  | 0 |  | 52 | 1 | 0 | BCU
A-7 | Classroom |  | 0 |  | 1056 | 24 | 0 | BCU
A-6 | Classroom | 321 | 21 |  | 1056 | 24 | 21 | AHU
A-8 | Classroom | 355 | 23 |  | 1056 | 24 | 23 | AHU
A-9 | Classroom | 364 | 24 |  | 1056 | 24 | 24 | AHU
A-11 | Classroom | 396 | 26 |  | 1056 | 24 | 24 | AHU
A-10 | Classroom | 292 | 19 |  | 1056 | 24 | 19 | AHU
A-12 | Classroom | 285 | 19 |  | 1056 | 24 | 19 | AHU
- | Corridor | 0 | 0 |  | 1056 | 24 | 0 | AHU
- | Cafeteria | 2789 | 185 |  | 1850 | 42 | 42 | AHU
- | BE Office | 76 | 5 |  | 88 | 2 | 2 | AHU
- | Main Office | 215 | 14 |  | 168 | 3 | 3 | AHU
- | Vice Principal | 93 | 6 |  | 100 | 2 | 2 | AHU
- | Counselor | 105 | 7 |  | 100 | 2 | 2 | AHU
- | Comm Closet | 54 | 3 |  | 50 | 1 | 1 | AHU
- | Storage | 73 | 4 |  | 250 | 5 | 4 | AHU
- | Lobby | 66 | 4 |  | 216 | 4 | 4 | AHU
- | Store Room 1 Ceiling | 43 | 2 |  | 250 | 5 | 2 | BCU
- | Store Room 2 | 26 | 1 |  | 70 | 1 | 1 | BCU
- | Store Room 3 | 27 | 1 |  | 70 | 1 | 1 | BCU
- | Janitors Closet | 20 | 1 |  | 32 | 0 | 0 | BCU
- | Storage next to B.E. | 22 | 1 |  | 99 | 2 | 1 | BCU

## Carver
Sheet Last Modified: | 2021-04-30
School: | George Washington Carver High School for Engineering and Science
Vendor: | Devine Brothers | Devine Retest | Devine 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 96 | 2 | 0
2 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 147 | 3 | 0
3 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 143 | 3 | 0
4 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 99 | 2 | 0
104 | Room | 783 | 52 |  | 625 | 14 | 14
107 | Room | 158 | 10 |  | 704.3 | 16 | 10
114 | Room | 0 | 0 |  | 840 | 19 | 0
115 | Room | 305 | 20 |  | 840 | 19 | 19
123 | Room | 181 | 12 |  | 920 | 20 | 12
124 | Room | 85 | 5 |  | 480 | 10 | 5
125 | Room | 643 | 42 |  | 1753.4 | 39 | 39
126 | Room | 399 | 26 |  | 750 | 17 | 17
134 | Room | 221 | 14 |  | 565.96 | 12 | 12
135 | Room | 0 | 0 |  | 400 | 9 | 0
136 | Room | 86 | 5 |  | 200 | 4 | 4
137 | Womens Room | 0 | 0 |  | 280 | 6 | 0
138 | Weight Room | 417 | 27 |  | 1500 | 34 | 27
139 | PE Office | 0 | 0 |  | 176 | 4 | 0
139 | Training Room | 0 | 0 |  | 139 | 3 | 0
139A | Lavatory | 0 | 0 |  | 96 | 2 | 0
144 | Room | 235 | 15 |  | 1310.6 | 29 | 15
145 | Env. Science Lab | 373 | 24 |  | 2348.8 | 53 | 24
147 | IMC | 1282 | 85 |  | 4086.5 | 92 | 85
201 | Room | 0 | 0 |  | 1200 | 27 | 0
202 | Room | 371 | 24 |  | 864 | 19 | 19
203 | Room | 294 | 19 |  | 864 | 19 | 19
209 | Room | 401 | 26 |  | 952 | 21 | 21
211 | Room | 367 | 24 |  | 960 | 21 | 21
212 | Room | 292 | 19 |  | 960 | 21 | 19
213 | Room | 295 | 19 |  | 960 | 21 | 19
214 | Room | 0 | 0 |  | 960 | 21 | 0
217 | Room | 271 | 18 |  | 1250 | 28 | 18
220 | Room | 0 | 0 |  | 1408 | 32 | 0
221 | Room | 95 | 6 |  | 1680 | 38 | 6
222 | Room | 201 | 13 |  | 1200 | 27 | 13
224 | Room | 392 | 26 |  | 1680 | 38 | 26
226 | Room | 309 | 20 |  | 1680 | 38 | 20
229 | Room | 0 | 0 |  | 1600 | 36 | 0
230 | Room | 162 | 10 |  | 1680 | 38 | 10
301 | Room | 0 | 0 |  | 1156.7 | 26 | 0
302 | Room | 834 | 55 |  | 864 | 19 | 19
303 | Room | 281 | 18 |  | 864 | 19 | 18
309 | Room | 462 | 30 |  | 864 | 19 | 19
311 | Room | 533 | 35 |  | 1041.4 | 23 | 23
312 | Room | 201 | 13 |  | 1118.4 | 25 | 13
313 | Room | 243 | 16 |  | 816 | 18 | 16
314 | Room | 389 | 25 |  | 816 | 18 | 18
317 | Room | 0 | 0 |  | 816 | 18 | 0
318 | Room | 170 | 11 |  | 768 | 17 | 11
320 | Room | 142 | 9 |  | 1056 | 24 | 9
321 | Room | 487 | 32 |  | 1200 | 27 | 27
322 | Room | 460 | 30 |  | 1200 | 27 | 27
324 | Room | 75 | 5 |  | 1200 | 27 | 5
327 | Room | 226 | 15 |  | 1519.1 | 34 | 15
329 | Room | 400 | 26 |  | 1440 | 32 | 26
- | Art Room | 756 | 50 |  | 2500 | 56 | 50
- | Auditorium | 4245 | 283 |  | 5612 | 127 | 127
- | Cafeteria | 6739 | 449 |  | 3826.2 | 86 | 86
- | Dance Area | 104 | 6 |  | 1920 | 43 | 6
- | Dance Studio | 1644 | 109 |  | 336 | 7 | 7
- | Gymnasium | 13040 | 869 |  | 8948.9 | 203 | 203
- | Female Student Locker Room | 579 | 38 |  | 1200 | 27 | 27
- | Male Student Locker Room | 176 | 11 |  | 1200 | 27 | 11
- | Female Staff Locker Room | 52 | 3 |  | 117 | 2 | 2
- | Male Staff Locker Room | 446 | 29 |  | 112 | 2 | 2
- | Male Staff Locker Room | 446 | 29 |  | 112 | 2 | 2

## Cassidy
Sheet Last Modified: | 2021-04-06
School: | Lewis C. Cassidy Elementary School
Vendor: | Devine | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Boy's Gang Bathroom | 560 | 37 |  | 575 | 13 | 13 | House Fan
- | Girl's Gang Bathroom | 326 | 21 |  | 396 | 9 | 9 | House Fan
B | Teachers Lounge | 384 | 25 |  | 308 | 7 | 7 | House Fan
B2 | Office | 0 | 0 | Yes | 748 | 17 | 17
B3 | Classroom | 741 | 49 |  | 742 | 16 | 16 | House Fan
B7 | Gym | 0 | 0 | Yes | 3872 | 88 | 88 | N/A
B8 | Classroom | 527 | 35 |  | 968 | 22 | 22 | House Fan
101 | Classroom | 542 | 36 |  | 660 | 15 | 15 | House Fan
102 | Classroom | 478 | 31 |  | 660 | 15 | 15 | House Fan
103 | Classroom | 538 | 35 |  | 660 | 15 | 15 | House Fan
104 | Classroom | 473 | 31 |  | 616 | 14 | 14 | House Fan
105 | Office | 0 | 0 |  | 132 | 3 | 0 | N/A
106 | Classroom | 682 | 45 |  | 704 | 16 | 16 | House Fan
107 | Classroom | 741 | 49 |  | 616 | 14 | 14 | House Fan
108 | Classroom | 812 | 54 |  | 660 | 15 | 15 | House Fan
109 | Classroom | 734 | 48 |  | 660 | 15 | 15 | House Fan
201 | Nurses Office | 0 | 0 | Yes | 176 | 4 | 4 | N/A
202 | Classroom | 551 | 36 |  | 792 | 18 | 18 | House Fan
203 | Classroom | 389 | 25 |  | 660 | 15 | 15 | House Fan
204 | Classroom | 471 | 31 |  | 660 | 15 | 15 | House Fan
205 | Teachers Lounge | 0 | 0 | Yes | 308 | 7 | 7 | N/A
206 | Asst Principal | 0 | 0 | Yes | 207 | 4 | 4 | N/A
207 | Classroom | 525 | 35 |  | 660 | 15 | 15 | House Fan
208 | Small Classroom | 0 | 0 | Yes | 220 | 5 | 5 | House Fan
209 | Classroom | 675 | 45 |  | 660 | 15 | 15 | House Fan
210 | Classroom | 551 | 36 |  | 616 | 14 | 14 | House Fan
211 | Classroom | 565 | 37 |  | 660 | 15 | 15 | House Fan
212 | Classroom | 611 | 40 |  | 660 | 15 | 15 | House Fan
213 | Office | 0 | 0 | Yes | 264 | 6 | 6 | N/A
301 | Office | 0 | 0 | Yes | 264 | 6 | 6 | N/A
302 | Classroom | 562 | 37 |  | 704 | 16 | 16 | House Fan
303 | Classroom | 430 | 28 |  | 704 | 16 | 16 | House Fan
304 | Classroom | 392 | 26 |  | 616 | 14 | 14 | House Fan
305 | Classroom | 507 | 33 |  | 616 | 14 | 14 | House Fan
306 | Classroom | 112 | 7 | Yes | 704 | 16 | 16 | House Fan
307 | Classroom | 465 | 31 |  | 748 | 17 | 17 | House Fan
308 | Classroom | 378 | 25 |  | 899 | 20 | 20 | House Fan
309 | Classroom | 378 | 25 |  | 704 | 16 | 16 | House Fan
310 | Classroom | 154 | 10 |  | 660 | 15 | 10 | House Fan
311 | Classroom | 518 | 34 |  | 616 | 14 | 14 | House Fan
312 | Classroom | 718 | 47 |  | 616 | 14 | 14 | House Fan
313 | Classroom | 550 | 36 |  | 660 | 15 | 15 | House Fan
314 | Classroom | 561 | 37 |  | 660 | 15 | 15 | House Fan
315 | Storage | 0 | 0 |  | 264 | 6 | 0 | N/A
- | Attwood Lunch Rm | 940 | 62 |  | 836 | 19 | 19 | House Fan
- | Auditorium | 1895 | 126 |  | 3608 | 82 | 82 | House Fan
- | Backstage Office | 0 | 0 |  | 132 | 3 | 0 | N/A
- | Lunch Room | 660 | 44 |  | 880 | 20 | 20 | House Fan
- | Library | 732 | 48 |  | 704 | 16 | 16 | House Fan
- | Main Office | 0 | 0 | Yes | 308 | 7 | 7 | N/A
- | Principal's Office | 0 | 0 | Yes | 132 | 3 | 3 | N/A

## Catharine
Sheet Last Modified: | 2021-04-19
School: | Joseph W. Catharine Elementary School
Vendor: | EMCOR | Main Building Part 2
School: | Joseph W. Catharine Elementary School Annex
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
- | Lunch | 503 | 33 |  | 1247 | 28 | 28 | Unit Ventilator
- | Gym | 976 | 65 |  | 4544 | 103 | 65 | Unit Ventilator
102 | Classroom | 270 | 18 |  | 681 | 15 | 15 | Unit Ventilator
103 | Classroom | 313 | 20 |  | 550 | 12 | 12 | Unit Ventilator
104 | Classroom | 670 | 44 |  | 953 | 21 | 21 | Unit Ventilator
105 | Classroom | 0 | 0 | Yes | 953 | 21 | 21 | Unit Ventilator
106 | Classroom | 0 | 0 | Yes | 842 | 19 | 19 | Unit Ventilator
107 | Classroom | 627 | 41 |  | 1062 | 24 | 24 | Unit Ventilator
108 | Classroom | 307 | 20 |  | 836 | 19 | 19 | Unit Ventilator
- | Office | 212 | 14 |  | 367 | 8 | 8 | Unit Ventilator
201 | Classroom | 407 | 27 |  | 676 | 15 | 15 | Unit Ventilator
202 | Classroom | 331 | 22 |  | 683 | 15 | 15 | Unit Ventilator
203 | Classroom | 306 | 20 |  | 673 | 15 | 15 | Unit Ventilator
204 | Classroom | 144 | 9 | Yes | 708 | 16 | 16 | Unit Ventilator
205 | Classroom | 300 | 20 |  | 678 | 15 | 15 | Unit Ventilator
206 | Classroom | 0 | 0 | Yes | 855 | 19 | 19 | Unit Ventilator
207 | Classroom | 0 | 0 | Yes | 504 | 11 | 11 | Unit Ventilator
208 | Classroom | 0 | 0 | Yes | 672 | 15 | 15 | Unit Ventilator
209 | Classroom | 0 | 0 | Yes | 709 | 16 | 16 | Unit Ventilator
210 | Classroom | 0 | 0 | Yes | 705 | 16 | 16 | Unit Ventilator
211 | Classroom | 0 | 0 | Yes | 673 | 15 | 15 | Unit Ventilator
301 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | Unit Ventilator
302 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | Unit Ventilator
303 | Classroom | 0 | 0 | Yes | 679 | 15 | 15 | Unit Ventilator
304 | Classroom | 173 | 11 | Yes | 708 | 16 | 16 | Unit Ventilator
305 | Classroom | 209 | 13 | Yes | 698 | 15 | 15 | Unit Ventilator
306 | Classroom | 0 | 0 | Yes | 872 | 19 | 19 | Unit Ventilator
307 | Classroom | 0 | 0 | Yes | 675 | 15 | 15 | Unit Ventilator
308 | Classroom | 198 | 13 | Yes | 674 | 15 | 15 | Unit Ventilator
309 | Classroom | 284 | 18 |  | 705 | 16 | 16 | Unit Ventilator
310 | Classroom | 297 | 19 |  | 707 | 16 | 16 | Unit Ventilator
311 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | Unit Ventilator
- | Principal's office | 0 | 0 | Yes | 359 | 8 | 8
- | Nurse office | 0 | 0 | Yes | 324 | 7 | 7
- | Counselor Office | 0 | 0 | Yes | 109 | 2 | 2
Joseph W. Catherine Elementary School Annex
100 | Office |  | 0 | Yes | 273 | 6 | 6 | N/A
102 | K-1 Room |  | 0 | Yes | 680 | 15 | 15 | N/A
104 | K-2 Room |  | 0 | Yes | 714 | 16 | 16 | N/A
213 | K-3 |  | 0 | Yes | 1056 | 24 | 24 | N/A

## Cayuga
Sheet Last Modified: | 2021-04-28
School: | Cayuga Elementary School (former St. Henry’s)
Vendor: | Chadwick | Devine Brothers Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | classroom | 355 | 23 |  | 830 | 18 | 18 | Unit Ventilator
102 | classroom | 375 | 25 |  | 740 | 16 | 16 | Unit Ventilator
103 | classroom | 315 | 21 |  | 795 | 18 | 18 | Unit Ventilator
104 | classroom | 280 | 18 |  | 796 | 18 | 18 | Unit Ventilator
105 | Nurse's Office |  | 0 | Yes | 330 | 7 | 7 | N/A
106 | classroom | 275 | 18 |  | 403 | 9 | 9 | Unit Ventilator
117 | classroom | 736 | 49 |  | 806 | 18 | 18 | Unit Ventilator
118 | classroom | 625 | 41 |  | 688 | 15 | 15 | Unit Ventilator
119 | classroom | 586 | 39 |  | 845 | 19 | 19 | Unit Ventilator
120 | classroom | 335 | 22 |  | 670 | 15 | 15 | Unit Ventilator
201 | classroom | 325 | 21 |  | 830 | 18 | 18 | Unit Ventilator
202 | classroom | 305 | 20 |  | 740 | 16 | 16 | Unit Ventilator
203 | classroom | 380 | 25 |  | 795 | 18 | 18 | Unit Ventilator
204 | classroom | 360 | 24 |  | 796 | 18 | 18 | Unit Ventilator
205 | classroom | 355 | 23 |  | 765 | 17 | 17 | Unit Ventilator
206 | classroom | 310 | 20 |  | 780 | 17 | 17 | Unit Ventilator
214 | classroom | 375 | 25 |  | 728 | 16 | 16 | Unit Ventilator
215 | classroom | 365 | 24 |  | 693 | 15 | 15 | Unit Ventilator
216 | classroom | 330 | 22 |  | 737 | 16 | 16 | Unit Ventilator
217 | classroom | 1606 | 107 |  | 822 | 18 | 18 | Unit Ventilator
301 | classroom | 345 | 23 |  | 830 | 18 | 18 | Unit Ventilator
302 | classroom | 275 | 18 |  | 740 | 16 | 16 | Unit Ventilator
303 | classroom | 380 | 25 |  | 795 | 18 | 18 | Unit Ventilator
304 | classroom | 380 | 25 |  | 796 | 18 | 18 | Unit Ventilator
305 | classroom | 553 | 36 |  | 765 | 17 | 17 | Unit Ventilator
306 | classroom | 315 | 21 |  | 790 | 17 | 17 | Unit Ventilator
- | Gym | 1213 | 80 |  | 2754 | 62 | 62 | AHU
- | Basement Corridor | 90 | 6 |  |  | 0 | 0 | AHU
- | Main Entrance Corridor | 46 | 3 |  |  | 0 | 0 | AHU
- | 1st Floor Corridor | 31 | 2 |  |  | 0 | 0 | AHU
- | Cafeteria | 936 | 62 |  | 3432 | 78 | 62 | AHU

## Central
Sheet Last Modified: | 2091-04-29
School: | Central High School
Vendor: | Devine Brothers | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Ceramic | 253 | 16 |  | 723 | 16 | 16
2 | Kiln | 58 | 3 |  | 128 | 2 | 2
3 | Drafting Studio | 403 | 26 |  | 1366 | 31 | 26
4 | Fashion | 40 | 2 |  | 290 | 6 | 2
5 | Office | 64 | 4 |  | 349 | 7 | 4
6 | Photography | 32 | 2 |  | 171 | 3 | 2
7 | Computer Lab | 31 | 2 |  | 148 | 3 | 2
8 | Art Studio | 356 | 23 |  | 1452 | 33 | 23
9 | Printing Studio | 70 | 4 |  | 390 | 8 | 4
12 | Classroom | 333 | 22 |  | 840 | 19 | 19
13 | Classroom | 388 | 25 |  | 709 | 16 | 16
82 | Classroom | 301 | 20 |  | 1714 | 38 | 20
84 | Classroom | 300 | 20 |  | 1531 | 34 | 20
85 | Classroom | 300 | 20 |  | 1594 | 36 | 20
89 | Classroom | 389 | 25 |  | 1327 | 30 | 25
95 | Classroom | 604 | 40 |  | 1307 | 29 | 29
97 | Classroom | 605 | 40 |  | 1216 | 27 | 27
98 | Classroom | 428 | 28 |  | 1374 | 31 | 28
99 | Classroom | 432 | 28 |  | 1258 | 28 | 28
101 | Classroom | 376 | 25 |  | 876 | 19 | 19
102 | Classroom | 370 | 24 |  | 852 | 19 | 19
103 | Classroom | 387 | 25 |  | 876 | 19 | 19
104 | Classroom | 316 | 21 |  | 700 | 15 | 15
105 | Classroom | 305 | 20 |  | 675 | 15 | 15
106 | Classroom | 283 | 18 |  | 687 | 15 | 15
107 | Classroom | 288 | 19 |  | 706 | 16 | 16
108 | Classroom | 329 | 21 |  | 700 | 15 | 15
109 | Classroom | 0 | 0 |  | 675 | 15 | 0
110 | Office | 248 | 16 |  | 339 | 7 | 7
111 | Classroom | 0 | 0 |  | 654 | 14 | 0
119 | Classroom | 0 | 0 |  | 470 | 10 | 0
120 | Classroom | 332 | 22 |  | 857 | 19 | 19
121 | Classroom | 366 | 24 |  | 694 | 15 | 15
122 | Classroom | 346 | 23 |  | 724 | 16 | 16
123 | Classroom | 297 | 19 |  | 694 | 15 | 15
124 | Classroom | 280 | 18 |  | 680 | 15 | 15
125 | Classroom | 427 | 28 |  | 683 | 15 | 15
126 | Classroom | 415 | 27 |  | 720 | 16 | 16
127 | Classroom | 290 | 19 |  | 722 | 16 | 16
136 | Classroom | 281 | 18 |  | 297 | 6 | 6
138 | Principal | 176 | 11 |  | 235 | 5 | 5
141 | Classroom | 293 | 19 |  | 690 | 15 | 15
142 | Office | 377 | 25 |  | 982 | 22 | 22
143 | Classroom | 405 | 27 |  | 700 | 15 | 15
144 | Roster Office | 179 | 11 |  | 652 | 14 | 11
201 | Classroom | 0 | 0 |  | 530 | 12 | 0
202 | Classroom | 288 | 19 |  | 834 | 18 | 18
203 | Classroom | 293 | 19 |  | 681 | 15 | 15
204 | Classroom | 288 | 19 |  | 692 | 15 | 15
205 | Classroom | 283 | 18 |  | 676 | 15 | 15
206 | Classroom | 344 | 22 |  | 681 | 15 | 15
207 | Classroom | 344 | 22 |  | 705 | 16 | 16
208 | Classroom | 286 | 19 |  | 682 | 15 | 15
209 | Classroom | 306 | 20 |  | 694 | 15 | 15
210 | Office | 226 | 15 |  | 336 | 7 | 7
211 | Classroom | 0 | 0 |  | 650 | 14 | 0
224 | Classroom | 646 | 43 |  | 831 | 18 | 18
225 | Classroom | 289 | 19 |  | 800 | 18 | 18
226 | Classroom | 286 | 19 |  | 700 | 15 | 15
227 | Classroom | 0 | 0 |  | 693 | 15 | 0
229 | Classroom | 377 | 25 |  | 676 | 15 | 15
230 | Classroom | 358 | 23 |  | 680 | 15 | 15
231 | Classroom | 0 | 0 |  | 680 | 15 | 0
232 | Classroom | 315 | 21 |  | 638 | 14 | 14
233 | Classroom | 246 | 16 |  | 597 | 13 | 13
244 | Classroom | 357 | 23 |  | 840 | 19 | 19
245 | Classroom | 316 | 21 |  | 840 | 19 | 19
246 | Classroom | 315 | 21 |  | 683 | 15 | 15
247 | Classroom | 368 | 24 |  | 686 | 15 | 15
248 | Classroom | 401 | 26 |  | 705 | 16 | 16
249 | Classroom | 379 | 25 |  | 694 | 15 | 15
250 | Classroom | 314 | 20 |  | 687 | 15 | 15
251 | Classroom | 458 | 30 |  | 705 | 16 | 16
252 | Classroom | 364 | 24 |  | 670 | 15 | 15
253 | Classroom | 314 | 20 |  | 330 | 7 | 7
302 | classroom | 483 | 32 |  | 1260 | 28 | 28
303 | Classroom | 331 | 22 |  | 1145 | 26 | 22
304 | Classroom | 291 | 19 |  | 670 | 15 | 15
305 | Theater | 250 | 16 |  | 480 | 10 | 10
306 | Classroom | 430 | 28 |  | 661 | 15 | 15
307 | Classroom | 478 | 31 |  | 657 | 14 | 14
308 | Classroom | 209 | 13 |  | 624 | 14 | 13
309 | Classroom | 200 | 13 |  | 700 | 15 | 13
311 | Computer Lab | 64 | 4 |  | 827 | 18 | 4
321C | Storage | 210 | 14 |  | 157 | 3 | 3
323 | Classroom | 256 | 17 |  | 1082 | 24 | 17
325 | Computer Lab | 314 | 20 |  | 654 | 14 | 14
326 | Classroom | 294 | 19 |  | 654 | 14 | 14
327 | Computer Lab | 356 | 23 |  | 654 | 14 | 14
328 | Music Room | 289 | 19 |  | 647 | 14 | 14
329 | Computer Lab | 205 | 13 |  | 296 | 6 | 6
402 | Classroom | 625 | 41 |  | 941 | 21 | 21
403 | Classroom | 391 | 26 |  | 779 | 17 | 17
406 | Classroom | 531 | 35 |  | 1102 | 25 | 25
407 | Classroom | 510 | 34 |  | 1102 | 25 | 25
Gym | Gym |  | 0 | Yes | 16550 | 376 | 376
- | Office Break Rm | 240 | 16 |  | 170 | 3 | 3

## Childs @ Barratt
Sheet Last Modified: | 2021-05-03
School: | George W. Childs Elementary School @ Barratt
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom |  | 0 | Yes | 1575 | 35 | 35
2 | Classroom |  | 0 | Yes | 1075 | 24 | 24
3 | Head Start Kitchen |  | 0 | Yes | 696 | 15 | 15 | House Fan
4 | - |  | 0 |  | 1224 | 27 | 0 | House Fan
5 | - |  | 0 | Yes | 1035 | 23 | 23 | House Fan
8 | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan
100B | VP's Office |  | 0 |  | 143 | 3 | 0 | House Fan
100C | Conference Room |  | 0 |  | 221 | 5 | 0 | House Fan
102 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan
103 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan
105 | Classroom |  | 0 | Yes | 851 | 19 | 19 | House Fan
105a | - |  | 0 | Yes | 575 | 13 | 13 | House Fan
106 | Classroom |  | 0 | Yes | 800 | 18 | 18 | House Fan
107 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
109A | Counsleor |  | 0 |  | 240 | 5 | 0 | House Fan
109C | Dicipline Room |  | 0 |  | 240 | 5 | 0
118 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
119 | Nurse |  | 0 | Yes | 420 | 9 | 9 | House Fan
121 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
201 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
203 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
205 | Classroom |  | 0 | Yes | 460 | 10 | 10 | House Fan
206 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
207 | Classroom |  | 0 | Yes | 504 | 11 | 11 | House Fan
208 | Classroom |  | 0 | Yes | 912 | 20 | 20 | House Fan
209 | Classroom |  | 0 | Yes | 828 | 18 | 18 | House Fan
210 | - |  | 0 | Yes | 912 | 20 | 20 | House Fan
212 | Classroom |  | 0 | Yes | 902 | 20 | 20 | House Fan
214 | Classroom |  | 0 | Yes | 966 | 21 | 21 | House Fan
215 | Classroom |  | 0 | Yes | 748 | 17 | 17 | House Fan
216 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan
217 | - |  | 0 | Yes | 1450 | 32 | 32 | House Fan
219 | Classroom |  | 0 |  | 1450 | 32 | 0 | House Fan
220 | Classroom |  | 0 | Yes | 1058 | 24 | 24 | House Fan
222 | - |  | 0 | Yes | 1058 | 24 | 24 | House Fan
224 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
224B | - |  | 0 | Yes | 689 | 15 | 15 | House Fan
226 | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan
2nd Floor | Special Needs Changing Room |  | 0 | Yes | 180 | 4 | 4
301 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan
302 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan
304 | - |  | 0 |  | 704 | 16 | 0 | House Fan
305 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan
306 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan
307 | Classroom |  | 0 | Yes | 552 | 12 | 12 | House Fan
308 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
309 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
310 | Classroom |  | 0 | Yes | 805 | 18 | 18 | House Fan
311 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
313 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
314 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
315 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
316 | Teacher's Lounge |  | 0 | Yes | 704 | 16 | 16 | House Fan
401 | - |  | 0 |  | 989 | 22 | 0 | House Fan
402 | - |  | 0 | Yes | 989 | 22 | 22 | House Fan
404 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan
405 | Classroom |  | 0 |  | 460 | 10 | 0 | House Fan
406 | - |  | 0 | Yes | 989 | 22 | 22 | House Fan
407 | - |  | 0 | Yes | 828 | 18 | 18 | House Fan
408 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan
409 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
411 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
412 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
| Auditorium |  | 0 |  | 4128 | 93 | 0
- | Cafeteria |  | 0 | Yes | 5512 | 125 | 125 | House Fan
- | Special Needs Classroom |  | 0 | Yes | 345 | 7 | 7 | House Fan
- | IMC |  | 0 | Yes | 1725 | 39 | 39 | House Fan
- | Main Office |  | 0 | Yes | 726 | 16 | 16 | House Fan
- | Music Room |  | 0 |  | 726 | 16 | 0 | House Fan
- | Principal |  | 0 | Yes | 312 | 7 | 7 | House Fan

## Clemente
Sheet Last Modified: | 2021-04-23
School: | Roberto Clemente Middle School and The LINC High School
Vendor: | Chadwick | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 126 | 8 |  | 664 | 15 | 8 | 1 Univent & 1 AHU
102 | Classroom | 54 | 3 |  | 664 | 15 | 3 | Univent
103 | Classroom | 95 | 6 |  | 664 | 15 | 6 | 1 Univent & 1 AHU
104 | Classroom | 54 | 3 |  | 664 | 15 | 3 | Univent
106 | Classroom | 24 | 1 |  | 312 | 7 | 1
107 | Classroom | 179 | 11 |  | 682 | 15 | 11 | 1 Unitvent & 2 AHU
108 | Classroom | 108 | 7 |  | 682 | 15 | 7 | 1 Univent & 1 AHU
109 | Classroom | 83 | 5 |  | 672 | 15 | 5 | 1 Univent & 1 AHU
110 | Classroom | 54 | 3 |  | 530 | 12 | 3 | 1 Univent & 1 AHU
111 | Classroom | 86 | 5 |  | 984 | 22 | 5 | 1 Univent & 1 AHU
112 | Classroom | 113 | 7 |  | 984 | 22 | 7 | 1 Univent & 1 AHU
113 | Classroom | 116 | 7 |  | 987 | 22 | 7 | 1 Univent & 1 AHU
114 | Classroom | 87 | 5 |  | 987 | 22 | 5 | 1 Univent & 1 AHU
115 | Classroom | 87 | 5 |  | 987 | 22 | 5 | 1 Univent & 1 AHU
116 | Classroom | 82 | 5 |  | 987 | 22 | 5 | 1 Univent & 1 AHU
121 | - | 24 | 1 |  | 264 | 6 | 1
125 | Classroom | 24 | 1 |  | 132 | 3 | 1
126 | Classroom | 24 | 1 |  | 132 | 3 | 1
128 | Classroom | 24 | 1 |  | 120 | 2 | 1
129 | Classroom | 24 | 1 |  | 120 | 2 | 1
131 | Classroom | 24 | 1 |  | 120 | 2 | 1
132 | Classroom | 24 | 1 |  | 120 | 2 | 1
144 | Classroom | 11 | 0 |  | 109 | 2 | 0
145 | Classroom | 11 | 0 |  | 70 | 1 | 0
146 | Classroom | 10 | 0 |  | 286 | 6 | 0
147 | Classroom | 10 | 0 |  | 160 | 3 | 0
148 | Classroom | 10 | 0 |  | 80 | 1 | 0
149 | Classroom | 10 | 0 |  | 90 | 2 | 0
150 | Classroom | 10 | 0 |  | 108 | 2 | 0
151 | Classroom | 10 | 0 |  | 70 | 1 | 0
152 | Classroom | 10 | 0 |  | 108 | 2 | 0
153 | Classroom | 10 | 0 |  | 108 | 2 | 0
201 | Classroom | 91 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU
202 | Classroom | 63 | 4 |  | 816 | 18 | 4 | 1 Univent & 1 AHU
203 | Classroom | 86 | 5 |  | 816 | 18 | 5 | 1 Univent & 1 AHU
204 | Classroom | 48 | 3 |  | 816 | 18 | 3 | 1 Univent & 1 AHU
205 | Classroom | 96 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU
206 | Classroom | 198 | 13 |  | 816 | 18 | 13 | 1 Univent & 1 AHU
207 | Classroom | 199 | 13 |  | 816 | 18 | 13 | 1 Univent & 1 AHU
208 | Classroom | 69 | 4 |  | 816 | 18 | 4 | 1 Univent & 1 AHU
209 | Classroom | 186 | 12 |  | 816 | 18 | 12 | 1 Univent & 1 AHU
210 | Classroom | 91 | 6 |  | 792 | 18 | 6 | 1 Univent & 1 AHU
211 | Classroom | 191 | 12 |  | 675 | 15 | 12 | 1 Univent & 1 AHU
212 | Classroom | 62 | 4 |  | 624 | 14 | 4 | 1 Univent & 1 AHU
213 | Classroom | 150 | 10 |  | 675 | 15 | 10 | 1 Univent & 1 AHU
214 | Classroom | 67 | 4 |  | 775 | 17 | 4 | 1 Univent & 1 AHU
215 | Classroom | 90 | 6 |  | 675 | 15 | 6 | 1 Univent & 1 AHU
216 | Classroom | 44 | 2 |  | 689 | 15 | 2 | 1 Univent & 1 AHU
217 | Classroom | 74 | 4 |  | 684 | 15 | 4 | 1 Univent & 1 AHU
218 | Classroom | 64 | 4 |  | 684 | 15 | 4 | 1 Univent & 1 AHU
219 | Classroom | 163 | 10 |  | 768 | 17 | 10 | 1 Univent & 1 AHU
220 | Classroom | 42 | 2 |  | 768 | 17 | 2 | 1 Univent & 1 AHU
221 | Classroom | 68 | 4 |  | 768 | 17 | 4 | 1 Univent & 1 AHU
222 | Classroom | 37 | 2 |  | 768 | 17 | 2 | Univent
223 | Classroom | 417 | 27 |  | 768 | 17 | 17 | 1 Univent & 1 AHU
224 | Classroom | 69 | 4 |  | 768 | 17 | 4 | 1 Univent & 1 AHU
225 | Classroom | 136 | 9 |  | 768 | 17 | 9 | 1 Univent & 1 AHU
226 | Classroom | 63 | 4 |  | 816 | 18 | 4 | 1 Univent & 1 AHU
227 | Classroom | 125 | 8 |  | 744 | 16 | 8 | 1 Univent & 1 AHU
228 | Classroom | 58 | 3 |  | 744 | 16 | 3 | 1 Univent & 1 AHU
301 | Classroom | 121 | 8 |  | 816 | 18 | 8 | 1 Univent & 1 AHU
302 | Classroom | 98 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU
303 | Classroom | 69 | 4 |  | 816 | 18 | 4 | Univent
304 | Classroom | 97 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU
305 | Classroom | 69 | 4 |  | 816 | 18 | 4 | Univent
306 | Classroom | 132 | 8 |  | 816 | 18 | 8 | 1 Univent & 1 AHU
307 | Classroom | 172 | 11 |  | 816 | 18 | 11 | 1 Univent & 1 AHU
308 | Classroom | 95 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU
309 | Classroom | 238 | 15 |  | 816 | 18 | 15 | 1 Univent & 1 AHU
310 | Classroom | 210 | 14 |  | 792 | 18 | 14 | 1 Univent & 1 AHU
311 | Classroom | 153 | 10 |  | 675 | 15 | 10 | 1 Univent & 1 AHU
312 | Classroom | 103 | 6 |  | 624 | 14 | 6 | 1 Univent & 1 AHU
313 | Classroom | 69 | 4 |  | 675 | 15 | 4 | Univent
314 | Classroom | 100 | 6 |  | 775 | 17 | 6 | 1 Univent & 1 AHU
315 | Classroom | 198 | 13 |  | 675 | 15 | 13 | 1 Univent & 1 AHU
316 | Classroom | 97 | 6 |  | 689 | 15 | 6 | 1 Univent & 1 AHU
317 | Classroom | 106 | 7 |  | 684 | 15 | 7 | 1 Univent & 1 AHU
318 | Classroom | 96 | 6 |  | 684 | 15 | 6 | 1 Univent & 1 AHU
319 | Classroom | 139 | 9 |  | 757 | 17 | 9 | 1 Univent & 1 AHU
320 | Classroom | 106 | 7 |  | 768 | 17 | 7 | 1 Univent & 1 AHU
321 | Classroom | 101 | 6 |  | 768 | 17 | 6 | 1 Univent & 1 AHU
322 | Classroom | 160 | 10 |  | 768 | 17 | 10 | 1 Univent & 1 AHU
323 | Classroom | 104 | 6 |  | 768 | 17 | 6 | 1 Univent & 1 AHU
324 | Classroom | 99 | 6 |  | 768 | 17 | 6 | 1 Univent & 1 AHU
325 | Classroom | 180 | 12 |  | 768 | 17 | 12 | 1 Univent & 1 AHU
326 | Classroom | 94 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU
327 | Classroom | 120 | 8 |  | 744 | 16 | 8 | 1 Univent & 1 AHU
328 | Classroom | 252 | 16 |  | 744 | 16 | 16 | 1 Univent & 1 AHU
503 | Classroom | 180 | 12 |  | 714 | 16 | 12 | 1 Univent & 1 AHU
504 | Classroom | 252 | 16 |  | 849 | 19 | 16 | AHU
505 | Classroom | 149 | 9 |  | 1456 | 33 | 9 | 1 Univent & 1 AHU
507 | Classroom | 217 | 14 |  | 1458 | 33 | 14 | 1 Univent & 1 AHU
508 | Classroom | 149 | 9 |  | 765 | 17 | 9 | Univent
509 | Classroom | 204 | 13 |  | 738 | 16 | 13 | 1 Univent & 1 AHU
510 | Classroom | 205 | 13 |  | 848 | 19 | 13 | 1 Univent & 1 AHU
511 | Classroom | 226 | 15 |  | 740 | 16 | 15 | 1 Univent & 1 AHU
512 | Classroom | 196 | 13 |  | 833 | 18 | 13 | 1 Univent & 1 AHU
- | Auditorium | 1643 | 109 |  | 8015 | 182 | 109
- | Basement / Cafe | 62 | 4 |  | 5900 | 134 | 4
- | cubicle-1 | 48 | 3 |  | 437 | 9 | 3
- | GYM | 2494 | 166 |  | 2633 | 59 | 59
- | library | 288 | 19 |  | 2675 | 60 | 19
- | mail room | 24 | 1 |  | 153 | 3 | 1
- | Link Main Office | 201 | 13 |  | 809 | 18 | 13
- | Clemente Main Office | 24 | 1 |  | 240 | 5 | 1

## Cleveland
Sheet Last Modified: | 2021-04-01
School: | Cleveland
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
109 | - |  | 0 | Yes | 850 | 19 | 19
110 | - |  | 0 | Yes | 840 | 19 | 19

## Comegys
Sheet Last Modified: | 2021-04-19
School: | Benjamin B. Comegys Elementary School |  |  | House fan Abated
Vendor: | Devine | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
K-1 | Classroom | 418 | 27 |  | 2240 | 50 | 27 | Unit Ventilator
K-2 | Classroom | 462 | 30 |  | 2240 | 50 | 30 | Unit Ventilator
100 | Classroom | 366 | 24 |  | 864 | 19 | 19 | Unit Ventilator
101 | Classroom | 369 | 24 |  | 832 | 18 | 18 | Unit Ventilator
103 | Classroom | 273 | 18 |  | 864 | 19 | 18 | Unit Ventilator
104 | Classroom | 0 | 0 | Yes | 576 | 13 | 13 | Unit Ventilator
105 | Classroom | 231 | 15 |  | 864 | 19 | 15 | Unit Ventilator
106 | Classroom | 710 | 47 |  | 672 | 15 | 15 | Unit Ventilator
200 | Classroom | 251 | 16 |  | 672 | 15 | 15 | Unit Ventilator
201 | Classroom | 0 | 0 | Yes | 365 | 8 | 8 | Radiator
202 | Classroom | 371 | 24 |  | 672 | 15 | 15 | Unit Ventilator
203 | Classroom | 1226 | 81 |  | 672 | 15 | 15 | Unit Ventilator
204 | Classroom | 426 | 28 |  | 672 | 15 | 15 | Unit Ventilator
205 | Classroom | 366 | 24 |  | 672 | 15 | 15 | Unit Ventilator
206 | Classroom | 320 | 21 |  | 672 | 15 | 15 | Unit Ventilator
207 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | Unit Ventilator
208 | Classroom | 283 | 18 |  | 728 | 16 | 16 | Unit Ventilator
209 | Classroom | 288 | 19 |  | 728 | 16 | 16 | Unit Ventilator
210 | Classroom | 303 | 20 |  | 728 | 16 | 16 | Unit Ventilator
211 | Classroom | 272 | 18 |  | 728 | 16 | 16 | Unit Ventilator
212 | Classroom | 135 | 9 |  | 728 | 16 | 9 | Unit Ventilator
213 | Classroom | 913 | 60 |  | 728 | 16 | 16 | Unit Ventilator
214 | Classroom | 446 | 29 |  | 728 | 16 | 16 | Unit Ventilator
300 | Classroom | 226 | 15 |  | 728 | 16 | 15 | Unit Ventilator
301 | Classroom | 254 | 16 |  | 728 | 16 | 16 | Unit Ventilator
302 | Classroom | 322 | 21 |  | 728 | 16 | 16 | Unit Ventilator
303 | Classroom | 213 | 14 |  | 728 | 16 | 14 | Unit Ventilator
304 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | Unit Ventilator
305 | Classroom | 858 | 57 |  | 728 | 16 | 16 | Unit Ventilator
306 | Classroom | 883 | 58 |  | 728 | 16 | 16 | Unit Ventilator
307 | Classroom | 209 | 13 |  | 728 | 16 | 13 | Unit Ventilator
- | Art Classroom | 385 | 25 |  | 616 | 14 | 14 | Unit Ventilator
- | Main Office |  | 0 | Yes | 936 | 21 | 21 | Radiator
- | Principal Office |  | 0 | Yes | 360 | 8 | 8 | Radiator
- | Counselor Office |  | 0 | Yes | 391 | 8 | 8 | Radiator
- | Nurse Office |  | 0 | Yes | 280 | 6 | 6 | Radiator
- | Auditorium | 271 | 18 |  | 4320 | 98 | 18 | AHU
- | Gym / Cafe | 477 | 31 |  | 3672 | 83 | 31 | AHU

## Comly
Sheet Last Modified: | 2021-04-29
School: | Watson Comly Elementary School |  |  | House fan Abated
Vendor: | Emcor Fluidics | 2nd Retest | 3rd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
102A | Classroom |  | 0 |  | 155 | 3 | 0 | House Fan
103 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
103A | Classroom |  | 0 |  | 164 | 3 | 0 | House Fan
104 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
105 | Classroom | 555 | 37 |  | 910 | 20 | 20 | Unit Ventilator
106 | Classroom | 581 | 38 |  | 910 | 20 | 20 | Unit Ventilator
107 | Classroom | 609 | 40 |  | 910 | 20 | 20 | Unit Ventilator
108 | Classroom |  | 0 | Yes | 910 | 20 | 20 | Unit Ventilator
110 (ESOL) | Classroom |  | 0 | Yes | 439 | 9 | 9
201 | Classroom |  | 0 | Yes | 435 | 9 | 9
201A | Classroom |  | 0 | Yes | 306 | 6 | 6 | House Fan
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
203 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
204 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
205 | Classroom |  | 0 | Yes | 690 | 15 | 15 | Unit Ventilator
206 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator
207 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator
208 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator
209 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator
210 | Classroom |  | 0 | Yes | 812 | 18 | 18 | Unit Ventilator
211 | Classroom | 147 | 9 |  | 812 | 18 | 9 | Unit Ventilator
212 | Classroom | 199 | 13 | Yes | 812 | 18 | 18 | Unit Ventilator
213 | Classroom | 197 | 13 |  | 812 | 18 | 13 | Unit Ventilator
214 | Classroom | 156 | 10 | Yes | 812 | 18 | 18 | Unit Ventilator
215 | Classroom | 510 | 34 |  | 812 | 18 | 18 | Unit Ventilator
216 | Classroom | 385 | 25 |  | 812 | 18 | 18 | Unit Ventilator
Art | 1st Fl Art Room | 342 | 22 |  | 1672 | 38 | 22 | Unit Ventilator
- | Art Teacher Office | 205 | 13 |  | 308 | 7 | 7 | MUA
- | Special Needs Room | 335 | 22 |  | 812 | 18 | 18 | Unit Ventilator
- | Music Room | 383 | 25 |  | 594 | 13 | 13 | Unit Ventilator
- | Office - Main | 183 | 12 |  | 169 | 3 | 3 | Unit Ventilator
- | Office-2 |  | 0 |  | 176 | 4 | 0
- | 2nd Floor Counselors Office |  | 0 | Yes | 182 | 4 | 4
- | Counslor waiting rm |  | 0 |  | 104 | 2 | 0
- | Conference room 1st floor |  | 0 |  | 338 | 7 | 0
- | Amy's Room |  | 0 |  | 156 | 3 | 0
- | Principals Office | 0 | 0 | Yes | 196 | 4 | 4 | N/A
- | Break Room | 0 | 0 |  | 390 | 8 | 0 | N/A
- | 2nd Floor Staff room |  | 0 |  | 170 | 3 | 0
- | Nurse 1st Floor | 90 | 6 |  | 150 | 3 | 3 | MUA
- | Nurse Office | 125 | 8 |  | 344 | 7 | 7 | MUA
- | Nurse waiting |  | 0 | Yes | 202 | 4 | 4
- | Cafeteria |  | 0 | Yes | 3321 | 75 | 75
- | Gym |  | 0 |  | 4838 | 109 | 0

## Conwell
Sheet Last Modified: | 2021-04-20
School: | Russell Conwell Middle School / Conwell Annex
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Conwell Main Building
B1 | - |  | 0 |  | 1575 | 35 | 0
B2 | - |  | 0 |  | 782 | 17 | 0
Main Office | Office |  | 0 | Yes | 396 | 9 | 9
Nurse | Office |  | 0 | Yes | 473 | 10 | 10
102 | - |  | 0 |  | 575 | 13 | 0
107 | - |  | 0 |  | 120 | 2 | 0
108 | - |  | 0 | Yes | 816 | 18 | 18
109 | - |  | 0 | Yes | 850 | 19 | 19
111 | - |  | 0 | Yes | 1200 | 27 | 27
103/104/ IMC | - |  | 0 |  | 4300 | 97 | 0
201 | - |  | 0 |  | 850 | 19 | 0
202 | - |  | 0 |  | 840 | 19 | 0
204 | - |  | 0 |  | 625 | 14 | 0
205 | - |  | 0 |  | 550 | 12 | 0
206 | - |  | 0 |  | 875 | 19 | 0
207 | - |  | 0 |  | 900 | 20 | 0
208 | - |  | 0 |  | 805 | 18 | 0
209 | - |  | 0 | Yes | 850 | 19 | 19
301 | - |  | 0 | Yes | 720 | 16 | 16
302 | - |  | 0 |  | 805 | 18 | 0
303 | - |  | 0 |  | 550 | 12 | 0
304 | - |  | 0 |  | 625 | 14 | 0
305 | - |  | 0 |  | 506 | 11 | 0
306 | - |  | 0 |  | 875 | 19 | 0
307 | - |  | 0 |  | 900 | 20 | 0
308 | - |  | 0 |  | 805 | 18 | 0
309 | - |  | 0 | Yes | 575 | 13 | 13
Conwell Annex
1 | - |  | 0 |  | 1276 | 29 | 0
9 | - |  | 0 |  | 1200 | 27 | 0
102 | - |  | 0 |  | 2318 | 52 | 0
104 | - |  | 0 |  | 870 | 19 | 0
203 | - |  | 0 |  | 4800 | 109 | 0
200 | - |  | 0 |  | 512 | 11 | 0
301 | - |  | 0 |  | 840 | 19 | 0
305 | - |  | 0 |  | 630 | 14 | 0
306 | - |  | 0 |  | 768 | 17 | 0

## Cook-Wissahickon
Sheet Last Modified: | 2021-04-29
School: | Cook-Wissahickon Elementary-Middle School
Vendor: | Devine | Devine Retest | Capital
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 310 | 20 |  | 695 | 15 | 15 | Unit Ventilator
2 | Classroom | 280 | 18 |  | 950 | 21 | 18 | Unit Ventilator
3 | Classroom | 443 | 29 |  | 513 | 11 | 11 | Unit Ventilator
15 | - | 131 | 8 |  |  | 0 | 0 | Unit Ventilator
016A | - | 131 | 8 |  |  | 0 | 0 | Unit Ventilator
101 | Classroom | 341 | 22 |  | 717 | 16 | 16 | Unit Ventilator
102 | Classroom | 694 | 46 |  | 700 | 15 | 15 | Unit Ventilator
103 | Classroom | 0 | 0 |  | 1495 | 33 | 0 | Unit Ventilator
105 | Classroom | 337 | 22 |  | 1005 | 22 | 22 | Unit Ventilator
106 | Classroom | 342 | 22 |  | 924 | 21 | 21 | Unit Ventilator
107 | Classroom | 327 | 21 |  | 630 | 14 | 14 | Unit Ventilator
108 | Classroom | 352 | 23 |  | 441 | 10 | 10 | Unit Ventilator
109 | Classroom | 585 | 39 |  | 851 | 19 | 19 | Unit Ventilator
110 | Classroom | 280 | 18 |  | 674 | 15 | 15 | Unit Ventilator
111 | Classroom | 285 | 19 |  | 386 | 8 | 8 | Unit Ventilator
200 | Classroom | 366 | 24 |  | 636 | 14 | 14 | Unit Ventilator
200A | Classroom | 324 | 21 |  | 485 | 11 | 11 | Unit Ventilator
201 | Classroom | 310 | 20 |  | 447 | 10 | 10 | Unit Ventilator
202 | Classroom | 418 | 27 |  | 730 | 16 | 16 | Unit Ventilator
203 | Classroom | 0 | 0 |  | 813 | 18 | 0 | Unit Ventilator
204 | Classroom | 326 | 21 |  | 867 | 19 | 19 | Unit Ventilator
205 | Classroom | 401 | 26 |  | 716 | 16 | 16 | Unit Ventilator
206 | Classroom | 0 | 0 |  | 810 | 18 | 0 | Unit Ventilator
207 | Classroom | 284 | 18 |  | 456 | 10 | 10 | Unit Ventilator
208 | Classroom | 336 | 22 |  | 422 | 9 | 9 | Unit Ventilator
209 | Classroom | 300 | 20 |  | 731 | 16 | 16 | Unit Ventilator
210 | Classroom | 315 | 21 |  | 731 | 16 | 16 | Unit Ventilator
211 | Classroom | 0 | 0 |  | 872 | 19 | 0 | Unit Ventilator
212 | Classroom | 440 | 29 |  | 365 | 8 | 8 | Unit Ventilator
213 | Room | 310 | 20 |  | 525 | 11 | 11 | Air Handling Unit
- | Cafeteria | 2213 | 147 |  |  | 0 | 0 | Air Handling Unit
- | Copy Room | 340 | 22 |  | 199 | 4 | 4 | Air Handling Unit
- | Gymnasium | 1486 | 99 |  | 4325 | 98 | 98 | Air Handling Unit
- | Library | 1180 | 78 |  | 2998 | 68 | 68 | Air Handling Unit
- | Main Office | 789 | 52 |  | 396 | 9 | 9 | Air Handling Unit
- | Pricipal's office | 498 | 33 |  | 358 | 8 | 8 | Air Handling Unit
- | Speech Room | 330 | 22 |  | 358 | 8 | 8 | Air Handling Unit
- | Prep and lounge |  | 0 |  | 602 | 13 | 0

## Cooke
Sheet Last Modified: | 2021-04-26
School: | Jay Cooke Elementary School |  |  | House Fan Abated
Vendor: | Devine | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100C | Classroom | 293 | 19 |  | 506 | 11 | 11 | House Fan
101C | Classroom | 411 | 27 |  | 543 | 12 | 12 | House Fan
102C | Classroom | 284 | 18 |  | 833 | 18 | 18 | House Fan
103 | Classroom | 531 | 35 |  | 1082 | 24 | 24 | House Fan
104 | Classroom | 279 | 18 |  | 809 | 18 | 18 | House Fan
105 | Classroom | 369 | 24 |  | 695 | 15 | 15 | House Fan
108 | Classroom | 328 | 21 |  | 858 | 19 | 19 | House Fan
109 | Office | 313 | 20 |  | 548 | 12 | 12 | House Fan
110 | Classroom | 422 | 28 |  | 665 | 15 | 15 | House Fan
110A | Office | 335 | 22 |  | 333 | 7 | 7 | House Fan
201 | Classroom | 335 | 22 |  | 711 | 16 | 16 | House Fan
202 | Classroom | 515 | 34 |  | 674 | 15 | 15 | House Fan
202A | Classroom | 347 | 23 |  | 1015 | 23 | 23 | House Fan
203 | Classroom | 388 | 25 |  | 717 | 16 | 16 | House Fan
205 | Office | 0 | 0 |  | 304 | 6 | 0 | House Fan(partial Duct)
206 | Office | 0 | 0 | Yes | 240 | 5 | 5 | House Fan(partial Duct)
207 | Classroom | 435 | 29 |  | 726 | 16 | 16 | House Fan
207A | Classroom | 330 | 22 |  | 334 | 7 | 7 | House Fan
208 | Classroom | 433 | 28 |  | 673 | 15 | 15 | House Fan
208A | Storage | 279 | 18 |  | 720 | 16 | 16
209 | Classroom | 363 | 24 |  | 693 | 15 | 15 | House Fan
210 | Classroom | 378 | 25 |  | 650 | 14 | 14 | House Fan
211 | Classroom | 748 | 49 |  | 211 | 4 | 4 | House Fan
212 | Classroom | 736 | 49 |  | 774 | 17 | 17 | House Fan
213 | Classroom | 807 | 53 |  | 720 | 16 | 16 | House Fan
214 | Classroom | 846 | 56 |  | 727 | 16 | 16 | House Fan
215 | Classroom | 797 | 53 |  | 748 | 17 | 17 | House Fan
216 | Classroom | 811 | 54 |  | 762 | 17 | 17 | House Fan
217 | Classroom | 496 | 33 |  | 670 | 15 | 15 | House Fan
301 | Classroom | 278 | 18 |  | 711 | 16 | 16 | House Fan
302 | Classroom | 522 | 34 |  | 690 | 15 | 15 | House Fan
302A | Classroom | 273 | 18 |  | 405 | 9 | 9 | House Fan
303 | Classroom | 581 | 38 |  | 714 | 16 | 16 | House Fan
303A | Classroom | 284 | 18 | Yes | 405 | 9 | 9 | House Fan
303B | Classroom | 0 | 0 | Yes | 216 | 4 | 4
304 | Classroom | 633 | 42 |  | 882 | 20 | 20 | House Fan
305 | Classroom | 437 | 29 |  | 907 | 20 | 20 | House Fan
306 | Classroom | 456 | 30 |  | 815 | 18 | 18 | House Fan
307 | Classroom | 541 | 36 |  | 798 | 18 | 18 | House Fan
308 | Classroom | 469 | 31 |  | 1031 | 23 | 23 | House Fan
309 | Classroom | 456 | 30 |  | 896 | 20 | 20 | House Fan
310 | Classroom | 441 | 29 |  | 769 | 17 | 17 | House Fan
311 | Classroom | 617 | 41 |  | 985 | 22 | 22 | House Fan
312 | Classroom | 333 | 22 |  | 713 | 16 | 16 | House Fan
312A | Classroom | 325 | 21 |  | 332 | 7 | 7 | House Fan
313 | Classroom | 393 | 26 |  | 666 | 15 | 15 | House Fan
313A | Classroom | 307 | 20 |  | 703 | 15 | 15 | House Fan
314 | Classroom | 365 | 24 |  | 709 | 16 | 16 | House Fan
315 | Classroom | 271 | 18 |  | 650 | 14 | 14 | House Fan
316 | Classroom | 673 | 44 |  | 765 | 17 | 17 | House Fan
317 | Classroom | 278 | 18 |  | 729 | 16 | 16 | House Fan
318 | Classroom | 744 | 49 |  | 730 | 16 | 16 | House Fan
319 | Classroom | 656 | 43 |  | 719 | 16 | 16 | House Fan
320 | Classroom | 764 | 50 |  | 700 | 15 | 15 | House Fan
321 | Classroom | 480 | 32 |  | 787 | 17 | 17 | House Fan
322 | Classroom | 353 | 23 |  | 653 | 14 | 14 | House Fan
- | Asst. Principal Waiting Room | 125 | 8 |  | 118 | 2 | 2 | House Fan
- | Asst. Principal Office |  | 0 | Yes | 110 | 2 | 2
- | Auditorium | 3875 | 258 |  | 3793 | 86 | 86 | House Fan
- | Boy's Cafeteria | 1403 | 93 |  | 2254 | 51 | 51 | House Fan
- | Boy's Gym | 1455 | 97 |  | 2806 | 63 | 63 | House Fan
- | Counselor Waiting Room | 134 | 8 |  | 123 | 2 | 2 | House Fan
- | Counselor Office 1 | 0 | 0 | Yes | 92 | 2 | 2 | House Fan
- | Counselor Office 2 | 0 | 0 |  | 101 | 2 | 0 | House Fan
- | Counselor Office 3 | 0 | 0 |  | 156 | 3 | 0
- | Girl's Cafeteria | 1178 | 78 |  | 1944 | 44 | 44 | House Fan
- | Girl's Gym | 1461 | 97 |  | 2806 | 63 | 63 | House Fan
- | Kitchen | 321 | 21 |  | 409 | 9 | 9 | House Fan
- | Library | 1042 | 69 |  | 2053 | 46 | 46 | House Fan
- | Nurse Office | 53 | 3 | Yes | 186 | 4 | 4 | House Fan
- | Principal Office | 141 | 9 |  | 336 | 7 | 7 | House Fan
- | Weight Room | 842 | 56 |  | 1027 | 23 | 23 | House Fan
- | CASST Office | 0 | 0 | Yes | 264 | 6 | 6
- | SPECM Speech Therapy Office | 0 | 0 |  | 112 | 2 | 0

## Cramp
Sheet Last Modified: | 2021-04-29
School: | William Cramp Elementary School
Vendor: | Devine Brothers | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
102 | Office | 27 | 1 |  | 133 | 3 | 1
102A | Office | 20 | 1 |  | 133 | 3 | 1
103 | Small Classroom | 103 | 6 |  | 533 | 12 | 6
106 | Classroom | 387 | 25 |  | 1033 | 23 | 23 | Unit Ventilator
107 | Counselor | 137 | 9 |  | 385 | 8 | 8
108 | Classroom | 148 | 9 | Yes | 1220 | 27 | 27 | Unit Ventilator
109 | Classroom | 405 | 27 |  | 1120 | 25 | 25 | Unit Ventilator
110 | Classroom | 277 | 18 |  | 1543 | 35 | 18 | Unit Ventilator
111 | Classroom | 318 | 21 |  | 1228 | 27 | 21 | Unit Ventilator
112 | Classroom | 498 | 33 |  | 1170 | 26 | 26
112E | Office | 29 | 1 |  | 200 | 4 | 1
113 | Classroom | 338 | 22 |  | 1311 | 29 | 22 | Unit Ventilator
13A | Classroom | 307 | 20 |  | 1073 | 24 | 20
13B | Classroom | 500 | 33 |  | 1294 | 29 | 29 | Unit Ventilator
114 | Art | 385 | 25 |  | 876 | 19 | 19 | AHU
115 | Classroom | 283 | 18 |  | 1559 | 35 | 18
119 | Office | 0 | 0 |  | 459 | 10 | 0
200 | Classroom | 763 | 50 |  | 967 | 21 | 21 | Unit Ventilator
201 | Classroom | 605 | 40 |  | 825 | 18 | 18 | Unit Ventilator
202 | Counselor | 26 | 1 |  | 151 | 3 | 1
203/212 | Speech | 27 | 1 |  | 151 | 3 | 1
204 | Classroom | 527 | 35 |  | 1050 | 23 | 23 | Unit Ventilator
205 | Classroom | 128 | 8 |  | 902 | 20 | 8 | Unit Ventilator
206 | Classroom | 437 | 29 |  | 1030 | 23 | 23 | Unit Ventilator
207 | Classroom | 440 | 29 |  | 971 | 22 | 22 | Unit Ventilator
208 | Classroom | 544 | 36 |  | 950 | 21 | 21 | Unit Ventilator
209 | Classroom | 438 | 29 |  | 897 | 20 | 20 | Unit Ventilator
210 | Classroom | 462 | 30 |  | 967 | 21 | 21 | Unit Ventilator
211 | Classroom | 118 | 7 |  | 976 | 22 | 7 | Unit Ventilator
300 | Classroom | 782 | 52 |  | 866 | 19 | 19 | Unit Ventilator
301 | Classroom | 675 | 45 |  | 982 | 22 | 22 | Unit Ventilator
302 | Counselor | 42 | 2 |  | 151 | 3 | 2
303/312 | Office | 48 | 3 |  | 151 | 3 | 3
304 | Classroom | 133 | 8 |  | 1050 | 23 | 8 | Unit Ventilator
304 | Classroom | 330 | 22 |  | 1050 | 23 | 22
305 | Classroom | 393 | 26 |  | 968 | 22 | 22 | Unit Ventilator
306 | Classroom | 122 | 8 |  | 855 | 19 | 8 | Unit Ventilator
306 | Classroom | 501 | 33 |  | 855 | 19 | 19
307 | Classroom | 713 | 47 |  | 965 | 21 | 21 | Unit Ventilator
308 | Classroom | 320 | 21 |  | 772 | 17 | 17 | Unit Ventilator
309 | Classroom | 471 | 31 |  | 941 | 21 | 21 | Unit Ventilator
310 | Classroom | 327 | 21 |  | 972 | 22 | 21 | Unit Ventilator
311 | Classroom | 421 | 28 |  | 896 | 20 | 20 | Unit Ventilator
313 | Classroom | 329 | 21 |  | 368 | 8 | 8 | Unit Ventilator
- | Gym | 42 | 2 |  | 4800 | 109 | 2 | AHU
- | LGI | 736 | 49 |  | 697 | 15 | 15 | AHU
- | Admin Office | 827 | 55 |  | 251 | 5 | 5 | AHU
- | Cafeteria | 630 | 42 |  | 7287 | 165 | 42 | AHU
- | Computer Lab | 498 | 33 |  | 2840 | 64 | 33 | Unit Ventilator
- | Computer Room | 1015 | 67 |  | 2437 | 55 | 55 | AHU
- | Conference/Storage | 110 | 7 |  | 199 | 4 | 4
- | IMC Office | 40 | 2 |  | 141 | 3 | 2
- | IMC Library | 36 | 2 |  | 2456 | 55 | 2
- | Kitchen | 1510 | 100 |  | 972 | 22 | 22
- | Library North Classroom | 537 | 35 |  | 2635 | 59 | 35 | Unit Ventilator
- | Library South Classroom | 443 | 29 |  | 362 | 8 | 8 | Unit Ventilator
- | Mail Room | 47 | 3 |  | 133 | 3 | 3
- | Main Office | 113 | 7 |  | 571 | 12 | 7
- | Nurse Office | 109 | 7 |  | 374 | 8 | 7
- | Nurse Exam Room | 44 | 2 |  | 128 | 2 | 2
- | Principals Office | 60 | 4 |  | 258 | 5 | 4
- | Teachers Lounge | 354 | 23 |  | 775 | 17 | 17
- | Vice Principal's Office | 64 | 4 |  | 213 | 4 | 4

## Crossan
Sheet Last Modified: | 2021-04-05
School: | Kenneth C. Crossan Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Kindergarten Classroom | 580 | 38 |  | 1088 | 24 | 24 | House Fan
2 | Classroom | 555 | 37 |  | 900 | 20 | 20 | House Fan
3 | Classroom | 522 | 34 |  | 930 | 21 | 21 | House Fan
4 | Classroom | 299 | 19 |  | 840 | 19 | 19 | House Fan
5 | Kindergarten Classroom |  | 0 | Yes | 900 | 20 | 20
5 | Classroom | 505 | 33 |  | 600 | 13 | 13 | House Fan
6 | Classroom | 820 | 54 |  | 805 | 18 | 18 | House Fan
7 | Computer Classrm. | 437 | 29 |  | 900 | 20 | 20 | House Fan
8 | Classroom | 580 | 38 |  | 1094 | 24 | 24 | House Fan
9 | Classrom | 444 | 29 |  | 840 | 19 | 19 | House Fan
9A | Teachers Rm. | 0 | 0 | Yes | 450 | 10 | 10 | N/A
10 | Classroom | 822 | 54 |  | 600 | 13 | 13
11 | Classroom | 466 | 31 |  | 720 | 16 | 16 | House Fan
12 | Classroom | 606 | 40 |  | 720 | 16 | 16 | House Fan
13 | Classroom | 626 | 41 |  | 720 | 16 | 16 | House Fan
- | Auditorium | 1107 | 73 |  | 2760 | 62 | 62 | House Fan
- | Cafeteria/Gym | 0 | 0 |  | 2300 | 52 | 0 | N/A
- | Counselors Rm. | 0 | 0 | Yes | 450 | 10 | 10 | N/A
- | Grnd. Fl. Boys Bathrm. | 568 | 37 |  | 736 | 16 | 16 | House Fan
- | Grnd. Fl. Girls Bathrm. | 620 | 41 |  | 775 | 17 | 17 | House Fan
- | Ind. Arts Classroom | 0 | 0 |  | 600 | 13 | 0 | N/A
- | Library | 525 | 35 |  | 1152 | 26 | 26 | House Fan
- | Main Office | 0 | 0 | Yes | 460 | 10 | 10 | N/A
- | Nurse Office |  | 0 | Yes | 450 | 10 | 10
- | Art Room |  | 0 | Yes | 600 | 13 | 13
- | Principal's Ofice | 0 | 0 |  | 450 | 10 | 0 | N/A

## Day
Sheet Last Modified: | 2021-04-29
School: | Anne Blakiston Day Elementary School
Vendor: | EMCOR / Chadwick
School: | Anne Blakiston Day Elementary School- Little School House
Vendor: | Chadwick | Part 2 and Exhaust | Exhaust
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Anna Blakiston Day Elementary School- Main Building
101 | classroom | 186 | 12 | Yes | 880 | 20 | 20 | Unit Ventilator
102 | classroom | 194 | 12 | Yes | 880 | 20 | 20 | Unit Ventilator
103 | classroom | 45 | 3 | Yes | 880 | 20 | 20 | Unit Ventilator
104 | classroom | 75 | 5 | Yes | 1440 | 32 | 32 | Unit Ventilator
105 | classroom | 126 | 8 | Yes | 880 | 20 | 20 | Unit Ventilator
106 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator
107 | classroom | 210 | 14 | Yes | 880 | 20 | 20 | Unit Ventilator
108 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator
109 | classroom |  | 0 | Yes | 880 | 20 | 20
111 | Classroom |  | 0 | Yes | 880 | 20 | 20
112 | Classroom |  | 0 | Yes | 260 | 5 | 5
201 | classroom | 255 | 17 | Yes | 875 | 19 | 19 | Unit Ventilator
202 | classroom | 257 | 17 | Yes | 880 | 20 | 20 | Unit Ventilator
203 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator
204 | classroom | 365 | 24 | Yes | 880 | 20 | 20 | Unit Ventilator
205 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator
206 | classroom | 84 | 5 | Yes | 880 | 20 | 20 | Unit Ventilator
207 | classroom | 0 | 0 | Yes | 575 | 13 | 13 | Unit Ventilator
208 | classroom | 47 | 3 | Yes | 880 | 20 | 20 | Unit Ventilator
209 | classroom | 235 | 15 | Yes | 880 | 20 | 20 | Unit Ventilator
210 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator
211 | classroom | 244 | 16 | Yes | 880 | 20 | 20 | Unit Ventilator
214 | Classroom |  | 0 | Yes | 228 | 5 | 5
- | Auditorium | 0 | 0 |  | 3300 | 75 | 0 | AHU
- | GYM | 573 | 38 |  | 5000 | 113 | 38 | AHU
- | Library | 0 | 0 |  | 2700 | 61 | 0 | RTU
Anna Blakiston Day Elementary School- Little School House
1 | classroom | 322 | 21 |  | 1056 | 24 | 21 | AHU
2 | classroom | 274 | 18 |  | 1056 | 24 | 18 | AHU
3 | classroom | 322 | 21 |  | 1056 | 24 | 21 | AHU
4 | classroom | 510 | 34 |  | 1056 | 24 | 24 | AHU
5 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU
6 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU
7 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU
8 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU
9 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU
10 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU
11 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU
12 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU
- | Lunchroom | 1136 | 75 |  | 1750 | 39 | 39 | AHU
- | Staff Bathroom Staff Toilet | 159 | 10 |  | 120 | 2 | 2 | N/A
- | Staff Bathroom Staff Toilet | 277 | 18 |  | 120 | 2 | 2 | N/A
- | Various Office | 392 | 26 |  |  | 0 | 0 | AHU
- | Corridor | 224 | 14 |  |  | 0 | 0 | FCU
- | Various Storage | 374 | 24 |  |  | 0 | 0 | AHU

## DeBurgos
Sheet Last Modified: | 2021-04-21
School: | Julia deBurgos Elementary School
Vendor: | Chadwick | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
108 | storage |  | 0 |  | 100 | 2 | 0 | AHU-1
111 | work rm |  | 0 |  | 100 | 2 | 0 | AHU-1
115 | office | 100 | 6 |  | 150 | 3 | 3 | AHU-1
116 | classroom | 281 | 18 |  | 658 | 14 | 14 | Univent
118 | classroom |  | 0 |  | 400 | 9 | 0 | AHU-1
120 | classroom | 380 | 25 |  | 759 | 17 | 17 | Univent
121 | classroom | 288 | 19 |  | 759 | 17 | 17 | Univent
123 | classroom | 486 | 32 |  | 759 | 17 | 17 | Univent
125 | classroom | 307 | 20 |  | 759 | 17 | 17 | Univent
129 | classroom | 335 | 22 |  | 640 | 14 | 14 | Univent
130 | classroom | 295 | 19 |  | 672 | 15 | 15 | Univent
132 | classroom | 470 | 31 |  | 704 | 16 | 16 | Univent
133 | classroom | 345 | 23 |  | 880 | 20 | 20 | Univent
134 | classroom | 301 | 20 |  | 667 | 15 | 15 | AHU-5
135 | classroom | 552 | 36 |  | 750 | 17 | 17 | Univent
136 | classroom | 291 | 19 |  | 750 | 17 | 17 | Univent
138 | classroom | 734 | 48 |  | 748 | 17 | 17 | AHU-5
139 | classroom | 0 | 0 | Yes | 704 | 16 | 16 | AHU-5
139B | PRACTICE RM | 0 | 0 |  | 100 | 2 | 0 | AHU-5
139C | PRACTICE RM | 0 | 0 |  | 100 | 2 | 0 | AHU-5
148 | office | 244 | 16 |  | 350 | 7 | 7 | AHU-5
148A | office | 130 | 8 |  | 100 | 2 | 2 | AHU-5
148B | office | 54 | 3 |  | 110 | 2 | 2 | AHU-5
148C | office | 37 | 2 |  | 100 | 2 | 2 | AHU-5
148D | office | 51 | 3 |  | 100 | 2 | 2 | AHU-5
148E | office | 67 | 4 |  | 100 | 2 | 2 | AHU-5
148F | office | 89 | 5 |  | 100 | 2 | 2 | AHU-5
148G | office | 44 | 2 |  | 100 | 2 | 2 | AHU-5
148H | office | 26 | 1 |  | 100 | 2 | 1 | AHU-5
148I | office | 64 | 4 |  | 100 | 2 | 2 | AHU-5
148L | office | 126 | 8 |  | 242 | 5 | 5 | AHU-5
149 | office | 59 | 3 |  | 100 | 2 | 2 | AHU-5
- | Nurse Office |  | 0 | Yes | 180 | 4 | 4 | AHU-5
151 | WAITING RM | 22 | 1 | Yes | 180 | 4 | 4 | AHU-5
151A | OFFICE | 0 | 0 |  | 110 | 2 | 0 | AHU-5
151B | OFFICE | 17 | 1 |  | 150 | 3 | 1 | AHU-5
151C | OFFICE | 17 | 1 |  | 80 | 1 | 1 | AHU-5
151E | OFFICE | 0 | 0 |  | 100 | 2 | 0 | AHU-5
152f | office | 39 | 2 |  | 99 | 2 | 2 | AHU-5
152g | office | 47 | 3 |  | 99 | 2 | 2 | AHU-5
152h | office | 0 | 0 |  | 208 | 4 | 0 | AHU-5
152j | office | 178 | 11 |  | 288 | 6 | 6 | AHU-5
152k | office | 160 | 10 |  | 368 | 8 | 8 | AHU-5
202 | classroom | 608 | 40 |  | 759 | 17 | 17 | Univent
203 | classroom | 481 | 32 |  | 759 | 17 | 17 | Univent
207 | classroom | 310 | 20 |  | 1081 | 24 | 20 | Univent
208 | classroom | 331 | 22 |  | 621 | 14 | 14 | Univent
211 | classroom | 300 | 20 |  | 759 | 17 | 17 | Univent
212 | classroom | 405 | 27 |  | 759 | 17 | 17 | Univent
213 | classroom | 345 | 23 |  | 759 | 17 | 17 | Univent
215 | office | 385 | 25 |  | 675 | 15 | 15 | AHU-1
218 | classroom | 720 | 48 |  | 759 | 17 | 17 | Univent
220 | classroom | 360 | 24 |  | 759 | 17 | 17 | Univent
221 | classroom | 310 | 20 |  | 759 | 17 | 17 | Univent
225 | classroom | 413 | 27 |  | 759 | 17 | 17 | Univent
226 | classroom | 328 | 21 |  | 759 | 17 | 17 | Univent
228 | classroom | 345 | 23 |  | 759 | 17 | 17 | Univent
229 | classroom | 300 | 20 |  | 759 | 17 | 17 | Univent
230 | classroom | 345 | 23 |  | 1196 | 27 | 23 | Univent
236 | classroom | 83 | 5 |  | 494 | 11 | 5 | AHU-5
236A | STORAGE | 150 | 10 |  | 171 | 3 | 3 | AHU-5
236B | OFFICE | 0 | 0 |  | 171 | 3 | 0 | AHU-5
237B | STORAGE | 37 | 2 |  | 165 | 3 | 2 | AHU-5
237C | OFFICE | 63 | 4 |  | 165 | 3 | 3 | AHU-5
238 | classroom | 442 | 29 |  | 759 | 17 | 17 | Univent
239 | classroom | 284 | 18 |  | 759 | 17 | 17 | Univent
302 | classroom | 430 | 28 |  | 1081 | 24 | 24 | Univent
306 | classroom | 289 | 19 |  | 526 | 11 | 11 | Univent
307 | classroom | 299 | 19 |  | 621 | 14 | 14 | Univent
308 | classroom | 285 | 19 |  | 504 | 11 | 11 | Univent
310 | classroom | 320 | 21 |  | 759 | 17 | 17 | Univent
311 | classroom | 365 | 24 |  | 759 | 17 | 17 | Univent
312 | classroom | 325 | 21 |  | 759 | 17 | 17 | Univent
313 | office | 453 | 30 |  | 675 | 15 | 15 | AHU-1
316 | classroom | 345 | 23 |  | 759 | 17 | 17 | Univent
317 | classroom | 380 | 25 |  | 759 | 17 | 17 | Univent
319 | classroom | 307 | 20 |  | 989 | 22 | 20 | Unit Ventilator
319A | storage | 233 | 15 |  | 367 | 8 | 8 | Unit Ventilator
323 | classroom | 336 | 22 |  | 759 | 17 | 17 | Univent
324 | classroom | 384 | 25 |  | 759 | 17 | 17 | Univent
326 | classroom | 423 | 28 |  | 759 | 17 | 17 | Univent
327 | classroom | 453 | 30 |  | 759 | 17 | 17 | Univent
328 | classroom | 425 | 28 |  | 759 | 17 | 17 | Univent
335 | STUDIO | 389 | 25 |  | 798 | 18 | 18 | AHU-8
336 | classroom | 366 | 24 |  | 759 | 17 | 17 | Univent
337 | classroom | 375 | 25 |  | 759 | 17 | 17 | Univent
- | BOYS LOCKER ROOM | 80 | 5 |  | 143 | 3 | 3 | AHU-5
- | FRONT IMC LIBRARY | 118 | 7 |  | 171 | 3 | 3 | AHU-5
- | GIRLS LOCKER ROOM | 84 | 5 |  | 143 | 3 | 3 | AHU-5
- | GYM OFFICE | 41 | 2 |  | 225 | 5 | 2 | AHU-5
- | LIBRARY | 892 | 59 |  | 3276 | 74 | 59 | AHU-8
- | Mail Room | 159 | 10 |  | 200 | 4 | 4 | AHU-5
- | Main Office | 618 | 41 |  | 924 | 21 | 21 | AHU-5
- | Principal Office | 208 | 13 |  | 324 | 7 | 7 | AHU-5
- | Staff Locker Room |  | 0 |  | 70 | 1 | 0 | AHU-1
- | Storage Office | 38 | 2 |  | 100 | 2 | 2 | AHU-5
- | Cafeteria | 4650 | 310 |  | 6020 | 136 | 136 | AHU-2
- | Gym | 3322 | 221 |  | 5904 | 134 | 134 | ahu-6
- | Auditorium | 3405 | 227 |  | 2983 | 67 | 67 | AHU-7

## Decatur
Sheet Last Modified: | 2021-04-27
School: | Stephen Decatur Elementary School
Stephen Decatur Elementary School Annex
Stephen Decatur Elementary School White Building
Vendor: | EMCOR | Devine Brothers | Devine Retest | Emcor Retest 2-15
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Decatur Main Building
K-1 | classroom | 283 | 18 |  | 1450 | 32 | 18 | Unit Ventilator
K-2 | classroom | 375 | 25 |  | 1450 | 32 | 25 | Unit Ventilator
100 | classroom | 329 | 21 |  | 897 | 20 | 20 | Unit Ventilator
101 | classroom | 271 | 18 |  | 805 | 18 | 18 | Unit Ventilator
102 | classroom | 228 | 15 |  | 897 | 20 | 15 | Unit Ventilator
103 | classroom | 253 | 16 |  | 805 | 18 | 16 | Unit Ventilator
104 | classroom | 240 | 16 |  | 897 | 20 | 16 | Unit Ventilator
105 | classroom | 321 | 21 |  | 805 | 18 | 18 | Unit Ventilator
106 | Nurse's Office |  | 0 | Yes | 357 | 8 | 8 | N/A
107 | classroom | 326 | 21 |  | 805 | 18 | 18 | Unit Ventilator
108 | classroom | 322 | 21 |  | 897 | 20 | 20 | Unit Ventilator
109 | classroom | 326 | 21 |  | 851 | 19 | 19 | Unit Ventilator
110 | classroom | 301 | 20 |  | 702 | 15 | 15 | Unit Ventilator
200 | Classroom | 352 | 23 |  | 805 | 18 | 18 | Unit Ventilator
201 | Classroom |  | 0 | Yes | 805 | 18 | 18
202 | Classroom |  | 0 | Yes | 805 | 18 | 18
203 | Classroom | 234 | 15 |  | 854 | 19 | 15 | Unit Ventilator
204 | Classroom |  | 0 | Yes | 805 | 18 | 18
205 | Classroom |  | 0 | Yes | 805 | 18 | 18
206 | Classroom |  | 0 | Yes | 805 | 18 | 18
208 | Classroom | 301 | 20 |  | 805 | 18 | 18 | Unit Ventilator
210 | Classroom | 242 | 16 |  | 805 | 18 | 16 | Unit Ventilator
212 | Classroom |  | 0 | Yes | 805 | 18 | 18
214 | Classroom | 247 | 16 |  | 391 | 8 | 8 | Unit Ventilator
216/218 | Classroom | 599 | 39 |  | 1702 | 38 | 38 | Unit Ventilator
217 | Classroom | 283 | 18 |  | 1352 | 30 | 18 | Unit Ventilator
219 | Classroom | 274 | 18 |  | 798 | 18 | 18 | Unit Ventilator
220 | Classroom | 184 | 12 | Yes | 865 | 19 | 19 | Unit Ventilator
300 | Classroom |  | 0 | Yes | 910 | 20 | 20
301 | Classroom |  | 0 | Yes | 900 | 20 | 20
302 | Classroom |  | 0 | Yes | 900 | 20 | 20
303 | Classroom |  | 0 | Yes | 900 | 20 | 20
304 | Classroom |  | 0 | Yes | 900 | 20 | 20
305 | Classroom |  | 0 | Yes | 900 | 20 | 20
306 | Classroom |  | 0 | Yes | 900 | 20 | 20
308 | Classroom |  | 0 | Yes | 900 | 20 | 20
310 | Classroom |  | 0 | Yes | 910 | 20 | 20
312 | Classroom | 277 | 18 |  | 391 | 8 | 8 | Unit Ventilator
314 | Classroom | 241 | 16 |  | 397 | 9 | 9 | Unit Ventilator
316 | Classroom | 238 | 15 |  | 851 | 19 | 15 | Unit Ventilator
317 | Classroom |  | 0 | Yes | 910 | 20 | 20
318 | Classroom |  | 0 | Yes | 850 | 19 | 19
319 | Classroom |  | 0 | Yes | 910 | 20 | 20
320 | Classroom |  | 0 | Yes | 910 | 20 | 20
- | AP | N/A | 0 |  | 126 | 2 | 0 | N/A
- | Auditorium | 675 | 45 |  | 2800 | 63 | 45 | AHU
- | Basement | 0 | 0 |  | 456 | 10 | 0 | N/A
B-1 | - |  | 0 | Yes | 731 | 16 | 16 | Unit Ventilator
B-2 | Counselors | 356 | 23 |  | 875 | 19 | 19 | Unit Ventilator
- | Dean | N/A | 0 |  | 126 | 2 | 0 | N/A
- | ESOL | 275 | 18 |  | 750 | 17 | 17 | Unit Ventilator
- | GYM | 1543 | 102 |  | 4108 | 93 | 93 | AHU
- | IMC | 301 | 20 |  | 1404 | 31 | 20 | RTU
- | Main Office | 360 | 24 |  | 999 | 22 | 22 | Unit Ventilator
- | Cafeteria | 0 | 0 | Yes | 6161 | 140 | 140 | Unit Ventilator
Decatur Annex
A-1 | classroom | 335 | 22 |  | 875 | 19 | 19 | Unit Ventilator
A-2 | classroom | 294 | 19 |  | 899 | 20 | 19 | Unit Ventilator
A-3 | classroom | 329 | 21 |  | 874 | 19 | 19 | Unit Ventilator
A-4 | classroom | 285 | 19 |  | 852 | 19 | 19 | Unit Ventilator
A-5 | classroom | 326 | 21 |  | 861 | 19 | 19 | Unit Ventilator
A-6 | classroom | 322 | 21 |  | 789 | 17 | 17 | Unit Ventilator
A-7 | classroom | 317 | 21 |  | 899 | 20 | 20 | Unit Ventilator
A-8 | classroom | 332 | 22 |  | 832 | 18 | 18 | Unit Ventilator
A-9 | classroom | 288 | 19 |  | 879 | 19 | 19 | Unit Ventilator
A-10 | classroom | 281 | 18 |  | 888 | 20 | 18 | Unit Ventilator
Decatur White Building
1 | classroom | 315 | 21 |  | 875 | 19 | 19 | Unit Ventilator
2 | classroom | 241 | 16 |  | 888 | 20 | 16 | Unit Ventilator
3 | classroom | 340 | 22 |  | 878 | 19 | 19 | Unit Ventilator
4 | classroom | 284 | 18 |  | 845 | 19 | 18 | Unit Ventilator

## Dick
Sheet Last Modified: | 2021-04-29
School: | William Dick Elementary School
Vendor: | EMCOR | Exhaust Report | Retest Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 355 | 23 |  | 962.76 | 21 | 21 | Unit Ventilator
102 | Classroom | 319 | 21 |  | 963.22 | 21 | 21 | Unit Ventilator
103 | Nurses Office |  | 0 | Yes | 824.55 | 18 | 18
104 | Classroom | 481 | 32 |  | 1036.2 | 23 | 23 | Unit Ventilator
105 | Office | 0 | 0 | Yes | 4045.9 | 91 | 91 | Unit Ventilator
105-A | Principal's Office |  | 0 | Yes | 280 | 6 | 6
106 | Small room |  | 0 | Yes | 303 | 6 | 6
107 | Classroom | 328 | 21 |  | 1049.8 | 23 | 21 | Unit Ventilator
108 | Classroom | 167 | 11 |  | 1054.6 | 23 | 11 | Unit Ventilator
109 | Classroom | 237 | 15 | Yes | 1047.7 | 23 | 23 | Unit Ventilator
111 | Classroom | 176 | 11 | Yes | 1271.6 | 28 | 28 | Unit Ventilator
112 | Classroom | 345 | 23 |  | 1274.5 | 28 | 23 | Unit Ventilator
200 | Room |  | 0 | Yes | 133 | 3 | 3
201 | Classroom | 356 | 23 |  | 746.79 | 16 | 16 | Unit Ventilator
202 | Classroom | 286 | 19 |  | 1051.2 | 23 | 19 | Unit Ventilator
203 | Classroom | 158 | 10 | Yes | 1051.9 | 23 | 23 | Unit Ventilator
204 | Classroom | 142 | 9 | Yes | 1034.7 | 23 | 23 | Unit Ventilator
205 | Classroom | 191 | 12 | Yes | 1056.6 | 24 | 24 | Unit Ventilator
207 | Classroom | 199 | 13 | Yes | 1009.4 | 22 | 22 | Unit Ventilator
208 | Classroom | 207 | 13 | Yes | 1049.4 | 23 | 23 | Unit Ventilator
209 | Classroom | 317 | 21 |  | 1055.3 | 23 | 21 | Unit Ventilator
211 | Classroom | 286 | 19 |  | 1049.4 | 23 | 19 | Unit Ventilator
212 | Classroom | 344 | 22 |  | 1047.6 | 23 | 22 | Unit Ventilator
213 | Classroom | 235 | 15 | Yes | 1049 | 23 | 23 | Unit Ventilator
214 | Classroom | 119 | 7 | Yes | 1029.2 | 23 | 23 | Unit Ventilator
300 | Counselor's Office |  | 0 | Yes | 164 | 3 | 3
301 | Classroom | 136 | 9 | Yes | 741.44 | 16 | 16 | Unit Ventilator
302 | Classroom | 398 | 26 |  | 1052.6 | 23 | 23 | Unit Ventilator
303 | Library | 241 | 16 | Yes | 1032.2 | 23 | 23 | Unit Ventilator
304 | Classroom | 169 | 11 | Yes | 1049.2 | 23 | 23 | Unit Ventilator
305 | Classroom | 330 | 22 |  | 1213.2 | 27 | 22 | Unit Ventilator
307 | Classroom | 101 | 6 | Yes | 1056.5 | 24 | 24 | Unit Ventilator
308 | Classroom | 133 | 8 | Yes | 1028.4 | 23 | 23 | Unit Ventilator
309 | Classroom | 369 | 24 |  | 1047.7 | 23 | 23 | Unit Ventilator
311 | Classroom | 406 | 27 |  | 1050.3 | 23 | 23 | Unit Ventilator
312 | Classroom | 281 | 18 |  | 1046.3 | 23 | 18 | Unit Ventilator
313 | Classroom | 53 | 3 | Yes | 1045.6 | 23 | 23 | Unit Ventilator
314 | Classroom | 0 | 0 | Yes | 1046.7 | 23 | 23 | Unit Ventilator
- | Gymnasium | 248 | 16 |  | 739.29 | 16 | 16 | Unit Ventilator
- | Auditorium |  | 0 |  | 4435.7 | 100 | 0 | AHU
- | Building Engineer's Office |  | 0 | Yes | 482 | 10 | 10

## Disston
Sheet Last Modified: | 2021-04-03
School: | Hamilton Disston Elementary-Middle School
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Mechanical Rm. |  | 0 |  | 570 | 12 | 0 | House Fan
B1 | Cafeteria | 1021 | 68 |  | 1680 | 38 | 38 | House Fan
B2 | Food Service | 1059 | 70 |  | 816 | 18 | 18 | House Fan
B3 | Gym | 0 | 0 | Yes | 3840 | 87 | 87 | House Fan
- | Gym Office | 0 | 0 |  | 288 | 6 | 0 | House Fan
B4 | Classroom | 0 | 0 | Yes | 1008 | 22 | 22 | House Fan
B5 | Classroom | 1005 | 67 |  | 864 | 19 | 19 | House Fan
B6 | Classroom | 768 | 51 |  | 984 | 22 | 22 | House Fan
017B | Basement Girls Bathroom | 464 | 30 |  | 504 | 11 | 11 | House Fan
011B | Basement Boys Bathroom | 271 | 18 |  | 528 | 12 | 12 | House Fan
101 | Classroom | 545 | 36 |  | 816 | 18 | 18 | House Fan
102 | Classroom | 764 | 50 |  | 720 | 16 | 16 | House Fan
103 | Classroom | 821 | 54 |  | 864 | 19 | 19 | House Fan
104 | Classroom | 593 | 39 |  | 766 | 17 | 17 | House Fan
104A | Office | 0 | 0 | Yes | 168 | 3 | 3 | House Fan
- | Auditorium | 3956 | 263 |  | 2784 | 63 | 63 | House Fan
105 | Classroom | 635 | 42 |  | 766 | 17 | 17 | House Fan
106 | Classroom | 403 | 26 |  | 864 | 19 | 19 | House Fan
107 | Classroom | 574 | 38 |  | 720 | 16 | 16 | House Fan
108 | Classroom | 593 | 39 |  | 816 | 18 | 18 | House Fan
- | Nurses Office | 0 | 0 | Yes | 200 | 4 | 4 | House Fan
201 | Classroom | 447 | 29 |  | 816 | 18 | 18 | House Fan
202 | Classroom | 668 | 44 |  | 720 | 16 | 16 | House Fan
203 | Classroom | 601 | 40 |  | 864 | 19 | 19 | House Fan
203A | Climate Office | 0 | 0 | Yes | 280 | 6 | 6 | House Fan
204 | Classroom | 548 | 36 |  | 816 | 18 | 18 | House Fan
204A | AP Office | 0 | 0 |  | 180 | 4 | 0 | House Fan
205 | Classroom | 301 | 20 |  | 816 | 18 | 18 | House Fan
- | Counselor's Office | 0 | 0 | Yes | 260 | 5 | 5 | House Fan
206 | Classroom | 570 | 38 |  | 864 | 19 | 19 | House Fan
207 | Classroom | 421 | 28 |  | 720 | 16 | 16 | House Fan
208 | Classroom | 281 | 18 |  | 816 | 18 | 18 | House Fan
- | Helping Hands Office | 0 | 0 | Yes | 120 | 2 | 2 | House Fan
301A | Office | 0 | 0 |  | 280 | 6 | 0 | House Fan
301 | Classroom | 365 | 24 |  | 816 | 18 | 18 | House Fan
302 | Classroom | 563 | 37 |  | 720 | 16 | 16 | House Fan
303 | Classroom | 442 | 29 |  | 864 | 19 | 19 | House Fan
304 | Classroom | 657 | 43 |  | 816 | 18 | 18 | House Fan
305 | Classroom | 53 | 3 | Yes | 870 | 19 | 19 | House Fan
306 | Classroom | 186 | 12 |  | 864 | 19 | 12 | House Fan
307 | Classroom | 56 | 3 | Yes | 957 | 21 | 21 | House Fan
308 | Classroom | 489 | 32 |  | 864 | 19 | 19 | House Fan
309 | Classroom | 127 | 8 | Yes | 900 | 20 | 20 | House Fan
310 | Classroom | 96 | 6 | Yes | 816 | 18 | 18 | House Fan
311 | Classroom | 611 | 40 |  | 864 | 19 | 19 | House Fan
312 | Classroom | 424 | 28 |  | 720 | 16 | 16 | House Fan
313 | Classroom | 411 | 27 |  | 816 | 18 | 18 | House Fan
313A | Office | 0 | 0 |  | 816 | 18 | 0 | House Fan
- | Library | 747 | 49 |  | 2156 | 49 | 49 | RTU-1
- | Office | 155 | 10 |  | 312 | 7 | 7 | RTU-1
- | Office | 55 | 3 |  | 312 | 7 | 3 | RTU-1
- | Main Office | 0 | 0 | Yes | 308 | 7 | 7 | RTU-2
- | Principal Office | 0 | 0 |  | 160 | 3 | 0 | RTU-2
- | Faculty Lounge | 0 | 0 |  | 312 | 7 | 0 | RTU-2
- | Modular Classroom | 0 | 0 |  | 720 | 16 | 0 | AHU

## Dobbins
Sheet Last Modified: | 2021-04-19
School: | Murrell Dobbins Vocational High School
Vendor: | Capital | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
016 B-5 | Classroom | 1130 | 75 |  | 2511 | 57 | 57
016 B-6 | Classroom | 536 | 35 |  | 2511 | 57 | 35
016 B-7 | Classroom | 718 | 47 |  | 2424 | 55 | 47
016 B-8 | Classroom | 494 | 32 |  | 2543 | 57 | 32
120 | Classroom | 249 | 16 |  | 597 | 13 | 13
122-A | Classroom | 325 | 21 |  | 1226 | 27 | 21
122-B | Classroom | 391 | 26 |  | 1226 | 27 | 26
123-A | Classroom | 287 | 19 |  | 1445 | 32 | 19
123-B | Classroom | 0 | 0 |  | 1445 | 32 | 0
123C | Classroom | 0 | 0 |  | 136 | 3 | 0
123J | Classroom | 428 | 28 |  | 322 | 7 | 7
130 | Classroom | 284 | 18 |  | 1017 | 23 | 18
131-A | Classroom | 0 | 0 |  | 2226 | 50 | 0
131-B | Classroom | 458 | 30 |  | 2226 | 50 | 30
131-C | Classroom | 0 | 0 |  | 2226 | 50 | 0
131-D | Classroom | 232 | 15 |  | 2226 | 50 | 15
134 | Classroom | 0 | 0 |  | 596 | 13 | 0
201 | Library/IMC | 397 | 26 |  | 3115 | 70 | 26
220-A | Classroom | 760 | 50 |  | 435 | 9 | 9
220-B | Classroom | 452 | 30 |  | 210 | 4 | 4
220-C | Classroom | 398 | 26 |  | 210 | 4 | 4
220-D | Classroom | 411 | 27 |  | 308 | 7 | 7
222 | Classroom | 299 | 19 |  | 1228 | 27 | 19
223 | Classroom | 393 | 26 |  | 720 | 16 | 16
225 | Classroom | 394 | 26 |  | 735 | 16 | 16
227-A | Classroom | 505 | 33 |  | 871 | 19 | 19
227-B | Classroom | 335 | 22 |  | 871 | 19 | 19
231-A | Classroom | 0 | 0 |  | 1125 | 25 | 0
231-B | Classroom | 141 | 9 |  | 1125 | 25 | 9
233-A | Classroom | 371 | 24 |  | 2122 | 48 | 24
233-B | Classroom | 347 | 23 |  | 2122 | 48 | 23
233-C | Classroom | 319 | 21 |  | 2122 | 48 | 21
234 | Classroom | 0 | 0 |  | 771 | 17 | 0
236 | Classroom | 381 | 25 |  | 1030 | 23 | 23
236,234,233, 232, & 231 | Classrooms | 6741 | 449 |  | 792 | 18 | 18
- | 2nd E/Center Corr | 375 | 25 |  | 2310 | 52 | 25
- | 2nd East Corr | 312 | 20 |  | 2310 | 52 | 20
- | 2nd W/Center Corr | 292 | 19 |  | 2310 | 52 | 19
- | 2nd West Corr | 0 | 0 |  | 2310 | 52 | 0
300 | Classroom | 451 | 30 |  | 975 | 22 | 22
305,330,331, 332, & 332A | Classrooms | 7434 | 495 |  | 792 | 18 | 18
315-A | Classroom | 300 | 20 |  | 1008 | 22 | 20
315-B | Classroom | 390 | 26 |  | 1008 | 22 | 22
317 | Classroom | 346 | 23 |  | 832 | 18 | 18
321,323,322, 322A, &322B | Classrooms | 5053 | 336 |  | 792 | 18 | 18
322-A | Classroom | 0 | 0 |  | 3737 | 84 | 0
322-B | Classroom | 171 | 11 |  | 3737 | 84 | 11
322-C | Classroom | 0 | 0 |  | 3737 | 84 | 0
322-D | Classroom | 680 | 45 |  | 3737 | 84 | 45
322-E | Classroom | 756 | 50 |  | 3737 | 84 | 50
322B | Classroom | 89 | 5 |  | 187 | 4 | 4
323-A | Classroom | 682 | 45 |  | 1035 | 23 | 23
331-A | Classroom | 538 | 35 |  | 1852 | 42 | 35
331-B | Classroom | 221 | 14 |  | 1852 | 42 | 14
332-A | Classroom | 352 | 23 |  | 963 | 21 | 21
332-B | Classroom | 371 | 24 |  | 963 | 21 | 21
333-A | Classroom | 478 | 31 |  | 1862 | 42 | 31
333-B | Classroom | 0 | 0 |  | 1862 | 42 | 0
333-C | Classroom | 543 | 36 |  | 1862 | 42 | 36
335 | Classroom | 393 | 26 |  | 250 | 5 | 5
- | 3rd E/Center Corr | 296 | 19 |  | 2310 | 52 | 19
- | 3rd East Corr | 310 | 20 |  | 2310 | 52 | 20
- | 3rd W/Center Corr | 437 | 29 |  | 2310 | 52 | 29
- | 3rd West Corr | 0 | 0 |  | 2310 | 52 | 0
400-A | Classroom | 356 | 23 |  | 2045 | 46 | 23
400-B | Classroom | 333 | 22 |  | 2045 | 46 | 22
400, 402, 403, & 403A | Classroom | 21 | 1 |  | 2310 | 52 | 1
401-A | Classroom | 0 | 0 |  | 1080 | 24 | 0
401-B | Classroom | 168 | 11 |  | 1080 | 24 | 11
401A | Storage | 264 | 17 |  | 222 | 5 | 5
402-A | Classroom | 0 | 0 |  | 951 | 21 | 0
402-B | Classroom | 194 | 12 |  | 951 | 21 | 12
403-A | Classroom | 257 | 17 |  | 2279 | 51 | 17
403-B | Classroom | 81 | 5 |  | 2279 | 51 | 5
403-C | Classroom | 190 | 12 |  | 2279 | 51 | 12
403-D | Classroom | 226 | 15 |  | 2279 | 51 | 15
410-A | Classroom | 273 | 18 |  | 1058 | 24 | 18
410-B | Classroom | 273 | 18 |  | 1058 | 24 | 18
411-A | Classroom | 0 | 0 |  | 1067 | 24 | 0
411-B | Classroom | 0 | 0 |  | 1067 | 24 | 0
412 | Classroom | 422 | 28 |  | 1066 | 24 | 24
413 | Classroom | 0 | 0 |  | 952 | 21 | 0
414 | Classroom | 364 | 24 |  | 921 | 20 | 20
420-A | Classroom | 766 | 51 |  | 745 | 16 | 16
420-B | Classroom | 326 | 21 |  | 745 | 16 | 16
422-A | Classroom | 514 | 34 |  | 2438 | 55 | 34
422-B | Classroom | 417 | 27 |  | 2438 | 55 | 27
422-C | Classroom | 407 | 27 |  | 2438 | 55 | 27
423 & 420 | Classrooms | 0 | 0 |  | 576 | 13 | 0
423-A | Classroom | 0 | 0 |  | 1372 | 31 | 0
423-B | Classroom | 0 | 0 |  | 1372 | 31 | 0
430-A | Classroom | 300 | 20 |  | 1431 | 32 | 20
430-B | Classroom | 319 | 21 |  | 1431 | 32 | 21
430,431, & 432 | Classrooms | 8038 | 535 |  | 792 | 18 | 18
431-A | Classroom | 673 | 44 |  | 2491 | 56 | 44
431-B | Classroom | 221 | 14 |  | 2491 | 56 | 14
431-C | Classroom | 533 | 35 |  | 2491 | 56 | 35
431-D | Classroom | 347 | 23 |  | 2491 | 56 | 23
431-E | Classroom | 325 | 21 |  | 2491 | 56 | 21
- | 4th E/Center Corr | 0 | 0 |  | 2310 | 52 | 0
- | 4th East Corr | 0 | 0 |  | 2310 | 52 | 0
- | 4th W/ Center Corr | 199 | 13 |  | 2310 | 52 | 13
- | 4th West Corr | 267 | 17 |  | 2310 | 52 | 17
500 | Classroom | 299 | 19 |  | 1160 | 26 | 19
500-A | Classroom | 301 | 20 |  | 270 | 6 | 6
501 | Classroom | 388 | 25 |  | 956 | 21 | 21
502-A | Classroom | 206 | 13 |  | 956 | 21 | 13
502-B | Classroom | 258 | 17 |  | 956 | 21 | 17
503-A | Classroom | 208 | 13 |  | 956 | 21 | 13
503-B | Classroom | 144 | 9 |  | 956 | 21 | 9
504-A | Classroom | 224 | 14 |  | 957 | 21 | 14
504-B | Classroom | 108 | 7 |  | 957 | 21 | 7
505 | Classroom | 0 | 0 |  | 863 | 19 | 0
506-A | Classroom | 0 | 0 |  | 833 | 18 | 0
506-B | Classroom | 280 | 18 |  | 833 | 18 | 18
507-A | Classroom | 221 | 14 |  | 1032 | 23 | 14
507-B | Classroom | 467 | 31 |  | 1032 | 23 | 23
510-A | Classroom | 313 | 20 |  | 1085 | 24 | 20
510-B | Classroom | 323 | 21 |  | 1085 | 24 | 21
511 | Classroom | 293 | 19 |  | 954 | 21 | 19
512 | Classroom | 344 | 22 |  | 712 | 16 | 16
513 | Classroom | 294 | 19 |  | 712 | 16 | 16
514 | Classroom | 311 | 20 |  | 665 | 15 | 15
515 | Classroom | 358 | 23 |  | 818 | 18 | 18
516 | Classroom | 394 | 26 |  | 819 | 18 | 18
520-B | Classroom | 0 | 0 |  | 221 | 5 | 0
522 | Classroom | 0 | 0 |  | 316 | 7 | 0
523 | Classroom | 0 | 0 |  | 795 | 18 | 0
524 | Classroom | 0 | 0 |  | 800 | 18 | 0
525 | Classroom | 378 | 25 |  | 851 | 19 | 19
526-A | Classroom | 57 | 3 |  | 961 | 21 | 3
526-B | Classroom | 377 | 25 |  | 961 | 21 | 21
530 | Classroom | 293 | 19 |  | 821 | 18 | 18
531-A | Classroom | 576 | 38 |  | 724 | 16 | 16
531-B | Classroom | 81 | 5 |  | 724 | 16 | 5
532 | Classroom | 292 | 19 |  | 879 | 19 | 19
533-A | Classroom | 225 | 15 |  | 800 | 18 | 15
533-B | Classroom | 0 | 0 |  | 800 | 18 | 0
534-A | Classroom | 438 | 29 |  | 1036 | 23 | 23
534-B | Classroom | 0 | 0 |  | 1036 | 23 | 0
535 | Classroom | 0 | 0 |  | 1006 | 22 | 0
- | 5th E.Cent Corr | 201 | 13 |  | 2310 | 52 | 13
- | 5th East Corr. | 0 | 0 |  | 2310 | 52 | 0
- | 5th W.Cent Corr | 276 | 18 |  | 2310 | 52 | 18
601-A | Classroom | 138 | 9 |  | 1553 | 35 | 9
601-B | Classroom | 0 | 0 |  | 1553 | 35 | 0
601-C | Classroom | 0 | 0 |  | 1553 | 35 | 0
603-A | Classroom | 0 | 0 |  | 962 | 21 | 0
603-B | Classroom | 229 | 15 |  | 962 | 21 | 15
604 | Classroom | 0 | 0 |  | 400 | 9 | 0
610 | Classroom | 331 | 22 |  | 738 | 16 | 16
611 | Classroom | 460 | 30 |  | 712 | 16 | 16
612 | Classroom | 298 | 19 |  | 704 | 16 | 16
613 | Classroom | 257 | 17 |  | 711 | 16 | 16
614 | Classroom | 270 | 18 |  | 800 | 18 | 18
615 | Classroom | 382 | 25 |  | 814 | 18 | 18
622-A | Classroom | 0 | 0 |  | 801 | 18 | 0
622-B | Classroom | 242 | 16 |  | 801 | 18 | 16
623 | Classroom | 682 | 45 |  | 679 | 15 | 15
624 | Classroom | 267 | 17 |  | 820 | 18 | 17
625 | Classroom | 174 | 11 |  | 680 | 15 | 11
627 | Classroom | 815 | 54 |  | 794 | 18 | 18
- | 6th Center Corr. | 0 | 0 |  | 792 | 18 | 0
- | 6th East Corr. | 466 | 31 |  | 792 | 18 | 18
- | Admin | 4788 | 319 |  | 786 | 17 | 17
- | Auditorium | 0 | 0 | Yes | 10676 | 242 | 242
- | Boy's Gym | 0 | 0 |  | 5940 | 135 | 0
- | Girl's Gym | 0 | 0 |  | 5696 | 129 | 0
- | Lunch Rm | 0 | 0 |  | 4563 | 103 | 0
- | Lunch Rm | 0 | 0 |  | 4563 | 103 | 0

## Dobson
Sheet Last Modified: | 2021-04-27
School: | James Dobson Middle School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom |  | 0 | Yes | 108 | 2 | 2 | House Fan
101 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan
103 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
104 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
106 | Office |  | 0 | Yes | 638 | 14 | 14 | House Fan
107 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
108 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
109 | Classroom |  | 0 | Yes | 120 | 2 | 2 | House Fan
201 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
203 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
204 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
205 | Office |  | 0 | Yes | 342 | 7 | 7 | House Fan
206 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
207 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
208 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
209 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
210 | Office |  | 0 | Yes | 660 | 15 | 15 | House Fan
303/304 | Classroom |  | 0 | Yes | 1320 | 30 | 30 | House Fan
306/307 | Classroom |  | 0 | Yes | 1320 | 30 | 30 | House Fan
308 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
309 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
313 | Classroom |  | 0 | Yes | 858 | 19 | 19 | House Fan
- | Councelors office |  | 0 | Yes | 243 | 5 | 5
- | Main Office |  | 0 | Yes | 510 | 11 | 11 | House Fan
- | Principals office |  | 0 | Yes | 236 | 5 | 5 | House Fan
- | Gym |  | 0 | Yes | 3080 | 70 | 70
- | Cafeteria large |  | 0 |  | 944 | 21 | 0
- | Auditorium |  | 0 |  | 3124 | 71 | 0
- | Library |  | 0 | Yes | 1320 | 30 | 30
- | Nurses office |  | 0 | Yes | 264 | 6 | 6
| Cafeteria small |  | 0 |  | 919 | 20

## Duckrey
Sheet Last Modified: | 2021-04-21
School: | Tanner Duckrey Elementary School
Exhaust Report
Vendor: | Chadwick | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B19 | Art Room | 358 | 23 |  | 1032.1 | 23 | 23 | AHU
B21 | Classroom | 0 | 0 | Yes | 1029.2 | 23 | 23 | Unit Ventilator
111 | Classroom | 718 | 47 |  | 1115.1 | 25 | 25 | Unit Ventilator
114 | Classroom | 284 | 18 |  | 940.88 | 21 | 18 | Unit Ventilator
117 | Classroom | 608 | 40 |  | 940.23 | 21 | 21 | Unit Ventilator
118 | Classroom | 271 | 18 |  | 690.76 | 15 | 15 | Unit Ventilator
119 | - | 276 | 18 | Yes | 1237.3 | 28 | 28 | Unit Ventilator
120 | Classroom | 638 | 42 |  | 1024.1 | 23 | 23 | Unit Ventilator
121A | Classroom | 367 | 24 |  | 715.35 | 16 | 16 | Unit Ventilator
121B | Classroom | 315 | 21 |  | 794.84 | 18 | 18 | Unit Ventilator
122 | Classroom | 413 | 27 |  | 1027 | 23 | 23 | Unit Ventilator
124 | Classroom | 686 | 45 |  | 921.12 | 20 | 20 | Unit Ventilator
126 | Classroom | 310 | 20 |  | 926.88 | 21 | 20 | Unit Ventilator
128 | Classroom | 409 | 27 |  | 1012.4 | 23 | 23 | Unit Ventilator
130 | Classroom | 429 | 28 |  | 1101.2 | 25 | 25 | Unit Ventilator
200 | - | 639 | 42 |  | 1035.8 | 23 | 23 | Unit Ventilator
201 | - | 803 | 53 |  | 1049.9 | 23 | 23 | Unit Ventilator
204 | - | 564 | 37 |  | 951.77 | 21 | 21 | Unit Ventilator
207 | - | 0 | 0 | Yes | 951.45 | 21 | 21 | Unit Ventilator
208 | - | 786 | 52 |  | 917.18 | 20 | 20 | Unit Ventilator
209 | - | 648 | 43 |  | 950.51 | 21 | 21 | Unit Ventilator
210 | - | 638 | 42 |  | 953.12 | 21 | 21 | Unit Ventilator
211 | - | 617 | 41 |  | 918.99 | 20 | 20 | Unit Ventilator
212 | - |  | 0 | Yes | 1023.3 | 23 | 23
213 | - | 830 | 55 |  | 1088 | 24 | 24 | Unit Ventilator
214 | - | 819 | 54 |  | 1036.5 | 23 | 23 | Unit Ventilator
215 | - | 475 | 31 |  | 1034.6 | 23 | 23 | Unit Ventilator
216 | - | 838 | 55 |  | 1039.3 | 23 | 23 | Unit Ventilator
216A | - | 384 | 25 |  | 925.97 | 21 | 21 | Unit Ventilator
217 | - | 546 | 36 |  | 922.32 | 20 | 20 | Unit Ventilator
218 | - | 307 | 20 |  | 922.02 | 20 | 20 | Unit Ventilator
219 | - | 348 | 23 |  | 925.05 | 21 | 21 | Unit Ventilator
220 | - | 459 | 30 |  | 411.32 | 9 | 9 | Unit Ventilator
220A | - | 290 | 19 |  | 330.33 | 7 | 7 | Unit Ventilator
221 | - | 556 | 37 |  | 872.69 | 19 | 19 | Unit Ventilator
221A | - | 432 | 28 |  | 193.51 | 4 | 4 | Unit Ventilator
222 | - | 334 | 22 |  | 875.27 | 19 | 19 | Unit Ventilator
223 | - | 538 | 35 |  | 872.03 | 19 | 19 | Unit Ventilator
- | Auditorium/Cafe | 264 | 17 | Yes | 5375.5 | 122 | 122 | AHU
- | Faculty Lounge | 1156 | 77 |  | 512.97 | 11 | 11 | Unit Ventilator
- | Kitchen | 203 | 13 |  | 2070 | 47 | 13 | AHU
- | Library | 336 | 22 |  | 1914 | 43 | 22 | AHU
- | Main Office | 1063 | 70 |  | 903 | 20 | 20 | Unit Ventilator
- | Nurse | 334 | 22 |  | 387 | 8 | 8 | Unit Ventilator
- | Science Room | 1464 | 97 |  | 798.8 | 18 | 18 | Unit Ventilator
- | Gym | 215 | 14 |  | 4808 | 109 | 14 | AHU

## Dunbar
Sheet Last Modified: | 2021-04-06
School: | Paul L. Dunbar High School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
102 | Clasroom | 0 | 0 | Yes | 730.15 | 16 | 16 | House Fan
103 | office | 0 | 0 | Yes | 682.42 | 15 | 15 | House Fan
103 | bathroom | 0 | 0 |  | 48.66 | 1 | 0 | House Fan
104 | Lunchroom | 0 | 0 | Yes | 1412.93 | 32 | 32 | House Fan
105 | Classroom | 0 | 0 | Yes | 730.15 | 16 | 16 | House Fan
105 | Bathroom | 0 | 0 |  | 54 | 1 | 0 | House Fan
107 | Classroom | 0 | 0 | Yes | 913.71 | 20 | 20 | House Fan
107 | Bathroom | 0 | 0 |  | 41.48 | 0 | 0 | House Fan
108 | Classroom | 0 | 0 | Yes | 682.42 | 15 | 15 | House Fan
108 | Bathroom | 0 | 0 |  | 44.96 | 1 | 0 | House Fan
109 | Climate rm | 0 | 0 | Yes | 251.16 | 5 | 5 | House Fan
109 | Bathroom | 0 | 0 |  | 58.2 | 1 | 0 | House Fan
201 | Classroom | 0 | 0 | Yes | 682.42 | 15 | 15 | House Fan
202 | Classroom | 0 | 0 | Yes | 698.45 | 15 | 15 | House Fan
203 | Classroom | 0 | 0 | Yes | 682.42 | 15 | 15 | House Fan
204 | Classroom | 0 | 0 | Yes | 666.39 | 15 | 15 | House Fan
205 | Classroom | 0 | 0 | Yes | 682.42 | 15 | 15 | House Fan
206 | Classroom | 0 | 0 | Yes | 715.92 | 16 | 16 | House Fan
207 | Art room | 0 | 0 | Yes | 837.96 | 19 | 19 | House Fan
208 | Classroom | 0 | 0 | Yes | 679.44 | 15 | 15 | House Fan
209 | scc room | 0 | 0 | Yes | 457.08 | 10 | 10 | House Fan
300 | computer lab | 0 | 0 | Yes | 687.7 | 15 | 15 | House Fan
301 | Classroom | 0 | 0 | Yes | 687.7 | 15 | 15 | House Fan
302 | Classroom | 0 | 0 | Yes | 703.8 | 15 | 15 | House Fan
303 | Classroom | 0 | 0 | Yes | 669.53 | 15 | 15 | House Fan
304 | Classroom | 0 | 0 | Yes | 643.4 | 14 | 14 | House Fan
305 | Classroom | 0 | 0 | Yes | 690.69 | 15 | 15 | House Fan
306 | Classroom | 0 | 0 | Yes | 724.5 | 16 | 16 | House Fan
307 | Classroom | 0 | 0 | Yes | 966 | 21 | 21 | House Fan
308 |  | 0 |  |  | 687.7 |  | 0 | House Fan
309 |  | 0 |  |  | 360.36 |  | 0 | House Fan
310 |  | 0 |  |  | 171.5 |  | 0 | House Fan
- | Auditorium | 0 | 0 |  | 3201.6 | 72 | 0 | House Fan
- | Boys bathroom near rm 307 | 0 | 0 |  | 296.82 | 6 | 0 | N/A
- | Boys bathroom near Nurse's Office | 0 | 0 |  | 143.81 | 3 | 0 | N/A
- | Basement Boys Bathroom | 0 | 0 |  | 598.91 | 13 | 0 | N/A
- | Basement Boys Bathroom | 0 | 0 |  | 317.46 | 7 | 0 | N/A
- | Girls bathroom near rm 301 | 0 | 0 |  | 414.8 | 9 | 0 | N/A
- | Basement Girls Bathroom | 0 | 0 |  | 386.75 | 8 | 0 | N/A
- | Girls bathroom near rm 201 | 0 | 0 |  | 440.92 | 10 | 0 | N/A
- | Gym | 0 | 0 |  | 2722.5 | 61 | 0 | House Fan
- | IMC | 0 | 0 | Yes | 1168 | 26 | 26 | House Fan
- | Main Office | 0 | 0 | Yes | 359.53 | 8 | 8 | House Fan
- | Nurse Office | 0 | 0 | Yes | 174.6 | 3 | 3 | House Fan
- | Principal Office | 0 | 0 | Yes | 230.79 | 5 | 5 | House Fan
- | Asst Principal Office |  | 0 | Yes | 879.11 | 19 | 19 | House Fan
- | Counselor Office |  | 0 | Yes | 458.49 | 10 | 10 | House Fan
- | Teachers Lounge | 0 | 0 |  | 605.28 | 13 | 0 | House Fan

## Edison
Sheet Last Modified: | 2021-04-20
School: | Thomas Edison High School
Vendor: | Devine Brothers | Devine Retest
Devine 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Office | 85 | 5 |  | 568 | 12 | 5 | AHU
102 | Nurse | 212 | 14 |  | 498 | 11 | 11 | AHU
103A | Mail room | 261 | 17 |  | 414 | 9 | 9 | AHU
104 | Office | 66 | 4 |  | 140 | 3 | 3 | AHU
105 | Office | 171 | 11 |  | 284 | 6 | 6 | AHU
105C | Conference | 79 | 5 |  | 241.69 | 5 | 5 | AHU
106 | Office | 94 | 6 |  | 119 | 2 | 2 | AHU
107 | Office | 68 | 4 |  | 112 | 2 | 2 | AHU
108 | Office | 61 | 4 |  | 86 | 1 | 1 | AHU
109 | Office | 56 | 3 |  | 74 | 1 | 1 | AHU
110 | Office | 71 | 4 |  | 86 | 1 | 1 | AHU
111 | Office | 68 | 4 |  | 86 | 1 | 1 | AHU
112 | Office | 80 | 5 |  | 86 | 1 | 1 | AHU
113 | Office | 63 | 4 |  | 86 | 1 | 1 | AHU
114 | Office | 115 | 7 |  | 86 | 1 | 1 | AHU
115 | Office | 124 | 8 |  | 86 | 1 | 1 | AHU
116 | Office | 160 | 10 |  | 242 | 5 | 5 | AHU
117 | Office | 92 | 6 |  | 20 | 0 | 0 | AHU
118 | Office | 55 | 3 |  | 83 | 1 | 1 | AHU
120 | Office | 70 | 4 |  | 90 | 2 | 2 | AHU
121 | Office | 56 | 3 |  | 90 | 2 | 2 | AHU
122 | Office | 69 | 4 |  | 90 | 2 | 2 | AHU
123 | Office | 59 | 3 |  | 90 | 2 | 2 | AHU
124 | Office | 57 | 3 |  | 90 | 2 | 2 | AHU
125 | Office | 68 | 4 |  | 90 | 2 | 2 | AHU
127B | Office | 136 | 9 |  | 173.685 | 3 | 3 | AHU
128 | Conference | 658 | 43 |  | 676 | 15 | 15 | AHU
129 | Office | 150 | 10 |  | 281 | 6 | 6 | AHU
130 | Office | 262 | 17 |  | 345 | 7 | 7 | AHU
131 | Break Room | 84 | 5 |  | 131 | 2 | 2 | AHU
132 | Classroom | 292 | 19 |  | 713 | 16 | 16 | AHU
133 | Classroom | 273 | 18 |  | 566 | 12 | 12 | AHU
134 | Classroom | 575 | 38 |  | 2286 | 51 | 38 | AHU
135 | Classroom | 460 | 30 |  | 1604 | 36 | 30 | AHU
135A | Kitchen | 61 | 4 |  | 37 | 0 | 0 | AHU
135B | Office | 78 | 5 |  | 137 | 3 | 3 | AHU
136 | Classroom | 310 | 20 |  | 1144 | 26 | 20 | AHU
136B | Classroom | 483 | 32 |  | 1142.49 | 25 | 25 | AHU
137 | Classroom | 297 | 19 |  | 2086 | 47 | 19 | AHU
137A | Office | 77 | 5 |  | 228 | 5 | 5 | AHU
138 | Womens Locker Room | 1166 | 77 |  | 4342 | 98 | 77 | AHU
138A | Office | 50 | 3 |  | 77.7 | 1 | 1 | AHU
138B | Office | 124 | 8 |  | 314 | 7 | 7 | AHU
139 | Mens Locker Room | 1278 | 85 |  | 3031 | 68 | 68 | AHU
139A | Office | 122 | 8 |  | 77.274 | 1 | 1 | AHU
139B | Storage | 66 | 4 |  | 177.97 | 4 | 4 | AHU
141 | Physical Fitness | 603 | 40 |  | 1325.3 | 30 | 30 | AHU
144A | Bathroom | 52 | 3 |  | 332.5 | 7 | 3 | AHU
144B | Bathroom | 36 | 2 |  | 210.9 | 4 | 2 | AHU
145 | Plumbing Shop | 6184 | 412 |  | 1635.35 | 37 | 37 | AHU
145 | Classroom | 358 | 23 |  | 2286 | 51 | 23 | AHU
145B | Classroom | 161 | 10 |  | 497.6 | 11 | 10 | AHU
146 | Office | 297 | 19 |  | 1280 | 29 | 19 | AHU
146 | Office | 332 | 22 |  | 276 | 6 | 6 | AHU
147 | Storage | 87 | 5 |  | 475.9 | 10 | 5 | AHU
147 | Classroom | 553 | 36 |  | 1497 | 34 | 34 | AHU
148 | Classroom |  | 0 | Yes | 3146 | 71 | 71
149 | Camera Room | 88 | 5 |  | 208.19 | 4 | 4 | AHU
150 | Classroom | 375 | 25 |  | 814 | 18 | 18 | AHU
150A | Office | 0 | 0 |  | 165 | 3 | 0 | AHU
150B | Studio | 114 | 7 |  | 1182 | 26 | 7 | AHU
151A | Classroom | 534 | 35 |  | 1233.16 | 28 | 28 | AHU
151B | Classroom | 912 | 60 |  | 1441.36 | 32 | 32 | AHU
152 | Classroom | 655 | 43 |  | 794 | 18 | 18 | AHU
152A | Classroom | 994 | 66 |  | 244 | 5 | 5 | AHU
152B | Classroom | 901 | 60 |  | 1073.49 | 24 | 24 | AHU
153A | Classroom | 321 | 21 |  | 533 | 12 | 12 | AHU
153B | Classroom | 302 | 20 |  | 107 | 2 | 2 | AHU
154A | Office | 278 | 18 |  | 175 | 3 | 3 | AHU
154E | Classroom | 0 | 0 |  | 516 | 11 | 0 | AHU
154H | Classroom | 304 | 20 |  | 407 | 9 | 9 | AHU
154D 154A | Theory | 240 | 16 |  | 514 | 11 | 11 | AHU
156 | Classroom | 293 | 19 |  | 514 | 11 | 11 | AHU
157 | Classroom | 961 | 64 |  | 1255 | 28 | 28 | AHU
158 | Classroom | 592 | 39 |  | 1234 | 28 | 28 | AHU
160 | Classroom | 727 | 48 |  | 1267 | 28 | 28 | AHU
160A | Office | 78 | 5 |  | 119 | 2 | 2 | AHU
161 | Classroom | 551 | 36 |  | 1440 | 32 | 32 | AHU
161A | Office | 88 | 5 |  | 120 | 2 | 2 | AHU
161H | Classroom | 52 | 3 |  | 36 | 0 | 0 | AHU
161I | Practice room | 9 | 0 |  | 36 | 0 | 0 | AHU
161J | Classroom | 73 | 4 |  | 90 | 2 | 2 | AHU
164 | Classroom | 1398 | 93 |  | 825 | 18 | 18 | AHU
164B | Classroom | 402 | 26 |  | 159 | 3 | 3 | AHU
171 | Classroom | 0 | 0 |  | 1392 | 31 | 0 | AHU
201 | Classroom | 333 | 22 |  | 679 | 15 | 15 | AHU
202 | Classroom | 334 | 22 |  | 677 | 15 | 15 | AHU
203 | Classroom | 325 | 21 |  | 680 | 15 | 15 | AHU
204 | Classroom | 436 | 29 |  | 770 | 17 | 17 | AHU
205 | Classroom | 601 | 40 |  | 1444 | 32 | 32 | AHU
205B | Storage | 153 | 10 |  | 375 | 8 | 8 | AHU
207 | Classroom | 845 | 56 |  | 2973 | 67 | 56 | AHU
209 | Classroom | 472 | 31 |  | 1646 | 37 | 31 | AHU
209B | Storage | 112 | 7 |  | 279 | 6 | 6 | AHU
210 | Classroom | 466 | 31 |  | 1552 | 35 | 31 | AHU
210B | Storage | 190 | 12 |  | 331 | 7 | 7 | AHU
212 | Office | 134 | 8 |  | 174 | 3 | 3 | AHU
213A | Classroom | 384 | 25 |  | 721 | 16 | 16 | AHU
213B | Classroom | 312 | 20 |  | 872 | 19 | 19 | AHU
214 | Classroom | 282 | 18 |  | 703 | 15 | 15 | AHU
215 | Classroom | 286 | 19 |  | 828 | 18 | 18 | AHU
216 | Office | 164 | 10 |  | 397 | 9 | 9 | AHU
217 | Classroom | 356 | 23 |  | 601 | 13 | 13 | AHU
218 | Classroom | 352 | 23 |  | 639 | 14 | 14 | AHU
219 | Office | 129 | 8 |  | 265 | 6 | 6 | AHU
220 | Classroom | 444 | 29 |  | 715 | 16 | 16 | AHU
220 | Classroom | 456 | 30 |  | 715 | 16 | 16 | AHU
221 | Classroom | 321 | 21 |  | 720 | 16 | 16 | AHU
222 | Classroom | 328 | 21 |  | 680 | 15 | 15 | AHU
223 | Classroom | 299 | 19 |  | 781 | 17 | 17 | AHU
224 | Classroom | 292 | 19 |  | 790 | 17 | 17 | AHU
225 | Classroom | 284 | 18 |  | 749 | 17 | 17 | AHU
226 | Classroom | 293 | 19 |  | 721 | 16 | 16 | AHU
229 | Library | 1039 | 69 |  | 6194 | 140 | 69 | AHU
229A | Office | 79 | 5 |  | 117 | 2 | 2 | AHU
229B | Office | 148 | 9 |  | 229 | 5 | 5 | AHU
229C | Computer Lab | 100 | 6 |  | 270 | 6 | 6 | AHU
230 | Office | 79 | 5 |  | 218 | 4 | 4 | AHU
231 | Classroom | 308 | 20 |  | 613 | 13 | 13 | AHU
232 | Office | 144 | 9 |  | 931 | 21 | 9 | AHU
233 | Classroom | 325 | 21 |  | 613 | 13 | 13 | AHU
234 | Classroom | 334 | 22 |  | 700 | 15 | 15 | AHU
235 | Classroom | 457 | 30 |  | 592 | 13 | 13 | AHU
236 | Classroom | 431 | 28 |  | 720 | 16 | 16 | AHU
237 | Classroom | 220 | 14 |  | 931 | 21 | 14 | AHU
238 | Classroom | 112 | 7 |  | 606 | 13 | 7 | AHU
239 | Classroom | 494 | 32 |  | 627 | 14 | 14 | AHU
240 | Classroom | 957 | 63 |  | 1407 | 31 | 31 | AHU
241 | Classroom | 318 | 21 |  | 714 | 16 | 16 | AHU
241A | Classroom | 156 | 10 |  | 700 | 15 | 10 | AHU
242 | Classroom | 1072 | 71 |  | 1512 | 34 | 34 | AHU
243 | Classroom | 605 | 40 |  | 2253 | 51 | 40 | AHU
245 | Classroom | 403 | 26 |  | 1908 | 43 | 26 | AHU
245A | Office | 107 | 7 |  | 258 | 5 | 5 | AHU
246 | Classroom | 380 | 25 |  | 2009 | 45 | 25 | AHU
246B | Classroom | 308 | 20 |  | 510 | 11 | 11 | AHU
247 | Classroom | 676 | 45 |  | 1992 | 45 | 45 | AHU
247A | Classroom | 383 | 25 |  | 495 | 11 | 11 | AHU
249 | Classroom | 307 | 20 |  | 888 | 20 | 20 | AHU
250 | Classroom | 121 | 8 |  | 142 | 3 | 3 | AHU
251 | Classroom | 223 | 14 |  | 503.97 | 11 | 11 | AHU
253 | Classroom | 0 | 0 |  | 939 | 21 | 0 | AHU
301 | Science Lab | 428 | 28 |  | 940 | 21 | 21 | AHU
302 | science prep | 0 | 0 |  | 197 | 4 | 0 | AHU
304 | Classroom | 448 | 29 |  | 1086 | 24 | 24 | AHU
305 | Classroom | 428 | 28 |  | 469 | 10 | 10 | AHU
307 | Lab | 150 | 10 |  | 370 | 8 | 8 | AHU
307B | Office | 205 | 13 |  | 161 | 3 | 3 | AHU
307C | Office | 152 | 10 |  | 92 | 2 | 2 | AHU
308 | Science Lab | 360 | 24 |  | 1015 | 23 | 23 | AHU
309 | Science Prep | 316 | 21 |  | 260 | 5 | 5 | AHU
310 | Classroom | 331 | 22 |  | 990 | 22 | 22 | AHU
311 | Classroom | 417 | 27 |  | 997 | 22 | 22 | AHU
313 | Classroom | 389 | 25 |  | 716 | 16 | 16 | AHU
314 | Classroom | 296 | 19 |  | 793 | 18 | 18 | AHU
315 | Classroom | 410 | 27 |  | 804 | 18 | 18 | AHU
316 | Classroom | 326 | 21 |  | 750 | 17 | 17 | AHU
317A | Office | 58 | 3 |  | 213 | 4 | 3 | AHU
317B | Office | 42 | 2 |  | 220 | 5 | 2 | AHU
318 | Classroom | 378 | 25 |  | 678 | 15 | 15 | AHU
319 | Classroom | 329 | 21 |  | 678 | 15 | 15 | AHU
320 | Classroom | 325 | 21 |  | 678 | 15 | 15 | AHU
321 | Classroom | 367 | 24 |  | 678 | 15 | 15 | AHU
322 | Faculty Lounge | 34 | 2 |  | 196 | 4 | 2 | AHU
324 | Classroom | 282 | 18 |  | 611 | 13 | 13 | AHU
325 | Classroom | 326 | 21 |  | 703 | 15 | 15 | AHU
326 | Classroom | 280 | 18 |  | 681 | 15 | 15 | AHU
327 | Classroom | 310 | 20 |  | 702 | 15 | 15 | AHU
328 | Office | 135 | 9 |  | 334 | 7 | 7 | AHU
328A and B | Office | 229 | 15 |  | 391 | 8 | 8 | AHU
329 | Classroom | 310 | 20 |  | 573 | 13 | 13 | AHU
330 | Classroom | 330 | 22 |  | 573 | 13 | 13 | AHU
331 | Classroom | 425 | 28 |  | 708 | 16 | 16 | AHU
333 | Classroom | 304 | 20 |  | 697 | 15 | 15 | AHU
334 | Classroom | 296 | 19 |  | 631 | 14 | 14 | AHU
335 | Classroom | 280 | 18 |  | 614 | 13 | 13 | AHU
336 | Classroom | 282 | 18 |  | 632 | 14 | 14 | AHU
338 | Classroom | 283 | 18 |  | 678 | 15 | 15 | AHU
339 | Office | 47 | 3 |  | 322 | 7 | 3 | AHU
340 | Classroom | 281 | 18 |  | 931 | 21 | 18 | AHU
341A | Classroom | 300 | 20 |  | 834 | 18 | 18 | AHU
341B | Classroom | 122 | 8 |  | 262 | 5 | 5 | AHU
342 | Classroom | 332 | 22 |  | 587 | 13 | 13 | AHU
344 | Classroom | 311 | 20 |  | 820 | 18 | 18 | AHU
345 | Classroom | 290 | 19 |  | 1154 | 26 | 19 | AHU
- | Main office Rear reception desk | 79 | 5 |  | 429 | 9 | 5 | AHU
- | Main office | 221 | 14 |  | 1109 | 25 | 14 | AHU
- | Student Store | 236 | 15 |  | 339.3 | 7 | 7 | AHU
- | Teaching Kitchen | 2167 | 144 |  | 2843 | 64 | 64 | AHU
- | Cafeteria | 0 | 0 |  | 8970 | 203 | 0 | AHU
- | Teaching Kitchen | 2480 | 165 |  | 1316 | 29 | 29 | AHU
- | Kitchen | 1030 | 68 |  | 1361 | 30 | 30 | AHU
- | Kitchen Hood | 3846 | 256 |  | N/A | 0 | 0 | AHU
- | Auditorium | 6454 | 430 |  | 5600 | 127 | 127 | AHU
- | 1st Floor NE | 176 | 11 |  | 20126 | 457 | 11 | AHU
- | Heavy Equipment | 2723 | 181 |  | 3189 | 72 | 72 | AHU
- | Autobody | 4337 | 289 |  | 444 | 10 | 10 | AHU
- | Welding | 1296 | 86 |  | 520 | 11 | 11 | AHU
- | Sheet Metal | 3436 | 229 |  | 514 | 11 | 11 | AHU
- | Warehouse Classroom | 8094 | 539 |  | 533 | 12 | 12 | AHU
- | Gym | 7088 | 472 |  | 15450 | 351 | 351 | AHU
- | Factory Lab | 3833 | 255 |  | 416.6 | 9 | 9 | AHU
- | 1st Floor | 210 | 14 |  | 2760 | 62 | 14 | AHU
- | Vending Machine Repair | 317 | 21 |  | 3167 | 71 | 21 | AHU
- | Boiler Room | 3303 | 220 |  | 4914 | 111 | 111 | AHU
- | Maint. Break room | 153 | 10 |  | 461 | 10 | 10 | AHU
- | Eng. Office | 128 | 8 |  | 187 | 4 | 4 | AHU
- | Weight Room | 990 | 66 |  | 939 | 21 | 21 | AHU
- | Offices | 3928 | 261 |  | 90 | 2 | 2 | AHU

## Edmonds, FS
Sheet Last Modified: | 2021-04-21
School: | Franklin S. Edmonds Elementary School
Vendor: | Devine | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B1 | Classroom | 0 | 0 | Yes | 400 | 9 | 9 | Unit Ventilator
B2 | Kitchen | 75 | 5 |  | 572 | 13 | 5 | Unit Ventilator
B3 | Kitchen | 165 | 11 |  | 480 | 10 | 10 | Unit Ventilator
H2 | Office |  | 0 | Yes | 178 | 4 | 4
101 | Classroom | 165 | 11 | Yes | 1128 | 25 | 25 | Unit Ventilator
102 | Classroom | 441 | 29 |  | 1056 | 24 | 24 | Unit Ventilator
103 | Classroom | 397 | 26 |  | 864 | 19 | 19 | Unit Ventilator
104 | Classroom | 455 | 30 |  | 1056 | 24 | 24 | Unit Ventilator
105 | Classroom | 412 | 27 |  | 1128 | 25 | 25 | Unit Ventilator
106 | Classroom | 460 | 30 |  | 1056 | 24 | 24 | Unit Ventilator
107 | Classroom | 256 | 17 |  | 720 | 16 | 16 | Unit Ventilator
108 | Classroom | 567 | 37 |  | 1056 | 24 | 24 | Unit Ventilator
109 | Classroom | 527 | 35 |  | 1056 | 24 | 24 | Unit Ventilator
110 | Classroom | 431 | 28 |  | 1056 | 24 | 24 | Unit Ventilator
111 | Classroom | 634 | 42 |  | 1008 | 22 | 22 | Unit Ventilator
112A | Office |  | 0 | Yes | 364 | 8 | 8 | Not supplied
112B | Office |  | 0 | Yes | 210 | 4 | 4
113 | Classroom | 662 | 44 |  | 1008 | 22 | 22 | Unit Ventilator
114 | Office |  | 0 | Yes | 364 | 8 | 8 | Unit Ventilator
115 | Classroom | 551 | 36 |  | 1008 | 22 | 22 | Unit Ventilator
115A | Office |  | 0 | Yes | 252 | 5 | 5
116 | Classroom | 169 | 11 | Yes | 736 | 16 | 16 | Unit Ventilator
117 | Classroom | 299 | 19 |  | 912 | 20 | 19 | Unit Ventilator
118 | Classroom | 281 | 18 |  | 912 | 20 | 18 | Unit Ventilator
118A | Office |  | 0 |  | 175 | 3 | 0
119 | Classroom | 282 | 18 |  | 912 | 20 | 18 | Unit Ventilator
120 | Classroom | 0 | 0 | Yes | 912 | 20 | 20 | Unit Ventilator
121 | Classroom | 0 | 0 | Yes | 912 | 20 | 20 | Unit Ventilator
122 | Classroom | 340 | 22 |  | 912 | 20 | 20 | Unit Ventilator
201 | Classroom | 503 | 33 |  | 1056 | 24 | 24 | Unit Ventilator
202 | Classroom | 418 | 27 |  | 1056 | 24 | 24 | Unit Ventilator
203 | Classroom | 415 | 27 |  | 1056 | 24 | 24 | Unit Ventilator
204 | Classroom | 395 | 26 |  | 1056 | 24 | 24 | Unit Ventilator
205 | Classroom | 491 | 32 |  | 1056 | 24 | 24 | Unit Ventilator
206 | Classroom | 414 | 27 |  | 1056 | 24 | 24 | Unit Ventilator
207 | Classroom | 485 | 32 |  | 1056 | 24 | 24 | Unit Ventilator
208 | Classroom | 348 | 23 |  | 1056 | 24 | 23 | Unit Ventilator
209 | Classroom | 431 | 28 |  | 1056 | 24 | 24 | Unit Ventilator
210 | Classroom | 304 | 20 |  | 1056 | 24 | 20 | Unit Ventilator
211 | Classroom | 322 | 21 |  | 1056 | 24 | 21 | Unit Ventilator
212 | Classroom | 31 | 2 | Yes | 1056 | 24 | 24 | Unit Ventilator
213 | Classroom | 186 | 12 |  | 1008 | 22 | 12 | Unit Ventilator
215 | Classroom | 509 | 33 |  | 1008 | 22 | 22 | Unit Ventilator
216 | Library | 969 | 64 |  | 1008 | 22 | 22 | Unit Ventilator
217 | Classroom | 503 | 33 |  | 1008 | 22 | 22 | Unit Ventilator
217-A | VP office |  | 0 | Yes | 252 | 5 | 5 | Convector
218 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator
219 | Classroom | 44 | 2 |  | 1008 | 22 | 2 | Unit Ventilator
- | Auditorium | 1860 | 124 |  | 1849 | 42 | 42 | AHU
- | Gym | 1195 | 79 |  | 2795 | 63 | 63 | AHU
- | Lunch | 0 | 0 |  | 780 | 17 | 0 | Unit Ventilator
- | Cafeteria | 411 | 27 | Yes | 1560 | 35 | 35 | Unit Ventilator
- | Kitchen | 0 | 0 | Yes | 400 | 9 | 9 | Unit Ventilator
| Women Helper |  | 0 | Yes | 262 | 5 | 5
- | Nurse | 0 | 0 | Yes | 280 | 6 | 6 | N/A
- | Prin. Office | 0 | 0 | Yes | 322 | 7 | 7 | Convector
- | Main Office | 0 | 0 | Yes | 650 | 14 | 14 | Convector

## Elkin
Sheet Last Modified: | 2021-04-26
School: | Lewis Elkin Elementary School
Vendor: | Devine Part 1 | Devine Part 2 | Devine Part 3
School: | Elkin Little School House
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
101 | Classroom | 391 | 26 |  | 420 | 9 | 9 | Unit Ventilator
102 | Classroom | 0 | 0 | Yes | 1136 | 25 | 25 | Unit Ventilator | Bad Motor
103 | Classroom | 299 | 19 | Yes | 1303 | 29 | 29 | Unit Ventilator
104 | Classroom | 293 | 19 |  | 1201 | 27 | 19 | Unit Ventilator
105 | Classroom | 301 | 20 | Yes | 1269 | 28 | 28 | Unit Ventilator
106 | Classroom | 300 | 20 |  | 418 | 9 | 9 | Unit Ventilator
107 | Classroom | 411 | 27 |  | 897 | 20 | 20 | Unit Ventilator
108 | Classroom | 386 | 25 |  | 897 | 20 | 20 | Unit Ventilator
109 | Classroom | 389 | 25 |  | 897 | 20 | 20 | Unit Ventilator
110 | Classroom | 376 | 25 |  | 821 | 18 | 18 | Unit Ventilator
111 | Classroom | 313 | 20 |  | 938 | 21 | 20 | Unit Ventilator
112 | Classroom | 363 | 24 |  | 898 | 20 | 20 | Unit Ventilator
113 | Classroom | 318 | 21 |  | 898 | 20 | 20 | Unit Ventilator
114 | Classroom | 349 | 23 |  | 898 | 20 | 20 | Unit Ventilator
115 | Classroom | 345 | 23 |  | 1024 | 23 | 23 | Unit Ventilator
116 | Lounge | 133 | 8 |  | 309 | 7 | 7 | Unit Ventilator
117 | Classroom | 129 | 8 |  | 215 | 4 | 4 | Unit Ventilator
117 | Office | 96 | 6 |  | 317 | 7 | 6 | Unit Ventilator
117A | Classroom Vestibule | 171 | 11 |  | 102 | 2 | 2 | Unit Ventilator
118 | Office | 109 | 7 |  | 122 | 2 | 2 | Unit Ventilator
119 | Office | 105 | 7 |  | 117 | 2 | 2 | Unit Ventilator
120 | Security Office | 214 | 14 |  | 259 | 5 | 5 | Unit Ventilator
121 | Office |  | 0 | Yes | 400 | 9 | 9
201 | Classroom | 496 | 33 |  | 772 | 17 | 17 | Unit Ventilator
202 | Classroom | 325 | 21 |  | 933 | 21 | 21 | Unit Ventilator
203 | Classroom | 385 | 25 |  | 838 | 19 | 19 | Unit Ventilator
204 | Classroom | 360 | 24 |  | 756 | 17 | 17 | Unit Ventilator
204A | Office | 178 | 11 |  | 201 | 4 | 4 | Unit Ventilator
205 | Classroom | 334 | 22 |  | 815 | 18 | 18 | Unit Ventilator
206 | Classroom | 402 | 26 |  | 815 | 18 | 18 | Unit Ventilator
207 | Classroom | 357 | 23 |  | 815 | 18 | 18 | Unit Ventilator
207A | Office | 74 | 4 |  | 201 | 4 | 4 | Unit Ventilator
208 | Classroom | 388 | 25 |  | 762 | 17 | 17 | Unit Ventilator
209 | Classroom | 365 | 24 |  | 811 | 18 | 18 | Unit Ventilator
210 | Classroom | 285 | 19 |  | 814 | 18 | 18 | Unit Ventilator
211 | Classroom | 430 | 28 |  | 746 | 16 | 16 | Unit Ventilator
211A | Office | 161 | 10 |  | 201 | 4 | 4 | Unit Ventilator
212 | Classroom | 312 | 20 |  | 810 | 18 | 18 | Unit Ventilator
213 | Classroom | 358 | 23 |  | 815 | 18 | 18 | Unit Ventilator
214 | Classroom | 376 | 25 |  | 786 | 17 | 17 | Unit Ventilator
215 | Classroom | 0 | 0 | Yes | 863 | 19 | 19 | Unit Ventilator | Not operating. Facility manager is aware
215A | Classroom | 131 | 8 |  | 201 | 4 | 4 | Unit Ventilator
216 | Classroom | 395 | 26 |  | 855 | 19 | 19 | Unit Ventilator
217 | Classroom | 493 | 32 |  | 1259 | 28 | 28 | Unit Ventilator | 2 Units.
218 | Classroom | 437 | 29 |  | 788 | 17 | 17 | Unit Ventilator
219 | Classroom | 76 | 5 |  | 117 | 2 | 2 | Unit Ventilator
220 | Library | 1770 | 118 |  | 2982 | 67 | 67 | Unit Ventilator | 4 Units. 1 unit is a wall unit. 1 unit is a window unit. 1 unit serves 220, but, is in 220B. 1 unit serves 220, but, is in 220C. This unit needs repair and has 0 CFM of OA.
220A | Office | 214 | 14 |  | 373 | 8 | 8 | Unit Ventilator
220B | Office | 0 | 0 |  | 421 | 9 | 0 | N/A | No ouside air to room.
220C | Office | 0 | 0 |  | 398 | 9 | 0 | N/A | No ouside air to room.
221 | Room | 0 | 0 |  | 141 | 3 | 0 | Unit Ventilator | Unit not operating
B01 | Classroom | 360 | 24 |  | 1859 | 42 | 24 | Unit Ventilator | No return air cover/grille
B02 | Classroom | 364 | 24 |  | 928 | 21 | 21 | Unit Ventilator
B03 | Classroom | 183 | 12 |  | 525 | 11 | 11 | Unit Ventilator
B04 | Classroom | 300 | 20 |  | 613 | 13 | 13 | Unit Ventilator | 2 Units. UV-2 is a window unit. UV-3 is a wall unit.
- | Assistant Principal's Office | 40 | 2 |  | 98 | 2 | 2 | Unit Ventilator
- | Auditorium | 0 | 0 |  | 7138 | 162 | 0 | Unit Ventilator | 4 units. UV-1, UV-2, UV-3, and UV-4 are not operating. One fell down. Facility manager is aware. Might be control issue
- | Main Office Conference Room | 0 | 0 |  | 181 | 4 | 0 | Unit Ventilator | Measured 0 CFM at all diffusers. No access to unit since Building Engineer does not have key to Server Room.
- | Copy room | 34 | 2 |  | 179 | 4 | 2 | Unit Ventilator | Measured 0 CFM at all diffusers. No access to unit since Building Engineer does not have key to Server Room.
- | Parent Resources Office | 0 | 0 |  | 84 | 1 | 0 | Unit Ventilator | Measured 0 CFM at all diffusers. No access to unit since Building Engineer does not have key to Server Room.
- | Education Office | 57 | 3 |  | 207 | 4 | 3 | Unit Ventilator
- | Gymnasium | 3457 | 230 |  | 4778 | 108 | 108 | Unit Ventilator | 2 Units.
- | Ms. Potts' Office | 46 | 3 |  | 133 | 3 | 3 | Unit Ventilator
- | Health Office/Nurses Area/Nurse's Suite | 480 | 32 |  | 637 | 14 | 14 | Unit Ventilator
- | Cafeteria/Lunchroom | 1731 | 115 |  | 2558 | 58 | 58 | Unit Ventilator | 6 Units. Univent 6 has a bad motor and 0 CFM of OA.
- | Principal's Office | 34 | 2 |  | 167 | 3 | 2 | Unit Ventilator
- | Main Office | 235 | 15 | Yes | 674 | 15 | 15 | Unit Ventilator
- | Teacher's Lounge | 0 | 0 |  | 623 | 14 | 0 | Unit Ventilator | Not operating. Facility manager is aware. Might be control issue
- | Library (Wall mount unit, south area) | 33 | 2 |  | 2775 | 63 | 2 | Unit Ventilator | data is for Wall mount unit, south area. Unit against window not operating
LSH Building
1 | Classroom | 829 | 55 |  | 1018 | 23 | 23 | AHU
2 | Classroom | 619 | 41 |  | 1018 | 23 | 23 | AHU
3 | Classroom | 651 | 43 |  | 1018 | 23 | 23 | AHU
4 | Classroom | 486 | 32 |  | 1018 | 23 | 23 | AHU
5 | Classroom | 410 | 27 |  | 1018 | 23 | 23 | AHU
6 | Classroom | 586 | 39 |  | 1018 | 23 | 23 | AHU
7 | Classroom | 379 | 25 |  | 1018 | 23 | 23 | AHU
8 | Classroom | 519 | 34 |  | 1018 | 23 | 23 | AHU
- | Main Office | 0 | 0 |  | 295 | 6 | 0 | AHU | Need to confirm with Jason that this reading is for the main office. Previous note for this line: Broken belt none onsite
- | Multi Purpose Room | 1105 | 73 |  | 1995 | 45 | 45 | AHU
- | Teacher's Lounge | 0 | 0 |  | 220 | 5 | 0 | AHU | Motor Issue

## Ellwood
Sheet Last Modified: | 2021-03-12
School: | Ellwood Elementary School
Vendor: | EMCOR | Exhaust | Retest
Devine 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | 100 | 13 | 0 | Yes | 1465 | 33 | 33 | Unit Ventilator
100 A | Counselor Office |  | 0 | Yes | 297 | 6 | 6
100 B-C | Nurse |  | 0 | Yes | 342 | 7 | 7
100 E | Main Office |  | 0 | Yes | 416 | 9 | 9
102 | 102 | 414 | 27 |  | 574 | 13 | 13 | Unit Ventilator
102 C | Principal |  | 0 | Yes | 400 | 9 | 9
103 | 103 | 328 | 21 |  | 582 | 13 | 13 | Unit Ventilator
104 | 104 | 392 | 26 |  | 701 | 15 | 15 | Unit Ventilator
105 | 105 | 457 | 30 |  | 1158 | 26 | 26 | Unit Ventilator
107 | 107 | 420 | 28 |  | 905 | 20 | 20 | Unit Ventilator
108 | 108 | 443 | 29 |  | 906 | 20 | 20 | Unit Ventilator
109 | 109 | 468 | 31 |  | 904 | 20 | 20 | Unit Ventilator
110 | 110 | 372 | 24 |  | 916 | 20 | 20 | Unit Ventilator
111 | 111 | 260 | 17 |  | 448 | 10 | 10 | Unit Ventilator
201 | 201 | 520 | 34 |  | 940 | 21 | 21 | Unit Ventilator
202 | 202 | 195 | 13 |  | 912 | 20 | 13 | Unit Ventilator
203 | 203 | 640 | 42 |  | 903 | 20 | 20 | Unit Ventilator
204 | 204 | 430 | 28 |  | 914 | 20 | 20 | Unit Ventilator
206 | 206 | 409 | 27 |  | 860 | 19 | 19 | Unit Ventilator
207 | 207 | 423 | 28 |  | 912 | 20 | 20 | Unit Ventilator
208 | 208 | 417 | 27 |  | 904 | 20 | 20 | Unit Ventilator
210 | 210 | 154 | 10 |  | 903 | 20 | 10 | Unit Ventilator
211 | 211 | 511 | 34 |  | 912 | 20 | 20 | Unit Ventilator
212 | 212 | 534 | 35 |  | 975 | 22 | 22 | Unit Ventilator
- | Auditorium | 0 | 0 |  | 2900 | 65 | 0 | AHU
- | Gym | 2115 | 141 |  | 3922 | 89 | 89 | AHU
- | Library | 0 | 0 | Yes | 2809 | 63 | 63 | AHU
- | Floor 1 East Corridor | 0 | 0 |  |  | 0 | 0 | Unit Ventilator
- | Floor 1 East Corridor | 0 | 0 |  |  | 0 | 0 | Unit Ventilator

## Elverson
Sheet Last Modified: | 2021-03-17
School: | Philadelphia Military Academy At Elverson
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
103 | Conference room | 788 | 52 |  | 690 | 15 | 15
104 | IMC | 973 | 64 |  | 690 | 15 | 15
105 | Conference room | 354 | 23 |  | 690 | 15 | 15
106 | Weight room | 871 | 58 |  | 943 | 21 | 21
107 | Classroom | 1423 | 94 |  | 690 | 15 | 15
108 | Classroom | 787 | 52 |  | 690 | 15 | 15
111 | Classroom | 625 | 41 |  | 736 | 16 | 16
112 | Classroom | 112 | 7 |  | 736 | 16 | 7
113 | Classroom | 728 | 48 |  | 736 | 16 | 16
114 | Classroom | 525 | 35 |  | 1180 | 26 | 26
201 | Classroom | 1325 | 88 |  | 690 | 15 | 15
202 | Classroom | 180 | 12 |  | 690 | 15 | 12
203 | Classroom | 428 | 28 |  | 690 | 15 | 15
204 | Classroom | 487 | 32 |  | 690 | 15 | 15
205 | Classroom | 73 | 4 |  | 805 | 18 | 4
206 | Classroom | 796 | 53 |  | 943 | 21 | 21
207 | Classroom | 63 | 4 |  | 690 | 15 | 4
208 | Classroom | 445 | 29 |  | 690 | 15 | 15
211 | Classroom | 0 | 0 |  | 736 | 16 | 0
212 | Classroom | 0 | 0 |  | 736 | 16 | 0
213 | Classroom | 670 | 44 |  | 736 | 16 | 16
214 | Classroom | 0 | 0 |  | 736 | 16 | 0
215 | Classroom | 745 | 49 |  | 736 | 16 | 16
301 | Classroom | 142 | 9 |  | 690 | 15 | 9
302 | Classroom | 447 | 29 |  | 690 | 15 | 15
303 | Classroom | 117 | 7 |  | 690 | 15 | 7
304 | Classroom | 147 | 9 |  | 690 | 15 | 9
305 | Classroom | 120 | 8 |  | 805 | 18 | 8
306 | Classroom | 796 | 53 |  | 1048 | 23 | 23
307 | Classroom | 370 | 24 |  | 690 | 15 | 15
308 | Classroom | 477 | 31 |  | 690 | 15 | 15
309 | Classroom | 115 | 7 |  | 690 | 15 | 7
311 | Classroom | 572 | 38 |  | 736 | 16 | 16
312 | Classroom | 0 | 0 |  | 736 | 16 | 0
313 | Classroom | 697 | 46 |  | 736 | 16 | 16
314 | Classroom | 0 | 0 |  | 736 | 16 | 0
315 | Classroom | 0 | 0 |  | 736 | 16 | 0
- | Cafeteria / Kitchen | 970 | 64 |  | 2595 | 58 | 58
- | Hallway | 462 | 30 |  | 1400 | 31 | 30
- | Hallway | 0 | 0 |  | 1400 | 31 | 0
- | Hallway | 432 | 28 |  | 1400 | 31 | 28
- | main office | 1050 | 70 |  | 744 | 16 | 16
- | Office / storage | 735 | 49 |  | 720 | 16 | 16

## Emlen
Sheet Last Modified: | 2021-04-21
School: | Eleanor Emlen Elementary School |  |  | House fan Abated
Vendor: | Devine Brothers |  | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B001 | Classroom | 736 | 49 |  | 736 | 16 | 16 | Unit Ventilator
B002 | Classroom | 0 | 0 | Yes | 1848 | 42 | 42 | Unit Ventilator
B003 | Classroom | 994 | 66 |  | 1032 | 23 | 23 | Unit Ventilator
B004A | Classroom | 701 | 46 |  | 768 | 17 | 17 | Unit Ventilator
B004B | Classroom | 360 | 24 |  | 816 | 18 | 18 | Unit Ventilator
B005 | Classroom | 419 | 27 |  | 546 | 12 | 12 | Unit Ventilator
101 | Classroom | 857 | 57 |  | 768 | 17 | 17 | House Fan
102 | Classroom | 267 | 17 |  | 690 | 15 | 15 | House Fan
103 | Classroom | 517 | 34 |  | 690 | 15 | 15 | House Fan
104 | Office | 193 | 12 |  | 88 | 2 | 2 | House Fan
104D | Waiting Room | 255 | 17 |  | 90 | 2 | 2 | House Fan
104D | Office | 199 | 13 |  | 396 | 9 | 9 | House Fan
104D | Storage | 136 | 9 |  | 207 | 4 | 4 | House Fan
104D | Nurse | 173 | 11 |  | 144 | 3 | 3 | House Fan
105 | Waiting Room | 174 | 11 |  | 248 | 5 | 5 | House Fan
105A | Office | 93 | 6 |  | 182 | 4 | 4 | House Fan
105B | Office | 85 | 5 |  | 126 | 2 | 2 | House Fan
105C | Office | 103 | 6 |  | 126 | 2 | 2 | House Fan
106 | Classroom | 378 | 25 |  | 690 | 15 | 15 | House Fan
107 | Classroom | 289 | 19 |  | 792 | 18 | 18 | House Fan
108 | Classroom | 643 | 42 |  | 690 | 15 | 15 | House Fan
109 | Classroom | 782 | 52 |  | 1050 | 23 | 23 | House Fan
110 | Classroom | 485 | 32 |  | 621 | 14 | 14 | House Fan
200 | Classroom | 0 | 0 | Yes | 528 | 12 | 12 | House Fan
201 | Classroom | 531 | 35 |  | 800 | 18 | 18 | House Fan
202 | Classroom | 312 | 20 |  | 690 | 15 | 15 | House Fan
203 | Classroom | 273 | 18 |  | 690 | 15 | 15 | House Fan
204 | Classroom | 97 | 6 | Yes | 690 | 15 | 15 | House Fan
205 | Classroom | 443 | 29 |  | 690 | 15 | 15 | House Fan
206 | Classroom | 267 | 17 |  | 900 | 20 | 17 | House Fan
207 | Classroom | 372 | 24 |  | 690 | 15 | 15 | House Fan
208 | Classroom | 437 | 29 |  | 805 | 18 | 18 | House Fan
209 | Classroom | 504 | 33 |  | 690 | 15 | 15 | House Fan
210 | Classroom | 361 | 24 |  | 690 | 15 | 15 | House Fan
211 | Classroom | 416 | 27 |  | 690 | 15 | 15 | House Fan
213 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan
214 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | House Fan
215 | Classroom | 0 | 0 | Yes | 744 | 16 | 16 | House Fan
216 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan
217 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | House Fan
218 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan
301 | Classroom |  | 0 | Yes | 1190 | 27
302 | Classroom | 695 | 46 |  | 660 | 15 | 15 | House Fan
303 | Classroom | 99 | 6 | Yes | 660 | 15 | 15 | House Fan
304 | Classroom | 719 | 47 |  | 660 | 15 | 15 | House Fan
305 | Classroom | 427 | 28 |  | 616 | 14 | 14 | House Fan
306 | Classroom | 259 | 17 |  | 638 | 14 | 14 | House Fan
307 | Classroom | 336 | 22 |  | 690 | 15 | 15 | House Fan
308 | Classroom | 372 | 24 |  | 660 | 15 | 15 | House Fan
308A | Classroom |  | 0 | Yes | 220 | 5
309 | Classroom | 105 | 7 | Yes | 690 | 15 | 15 | House Fan
310 | Classroom | 346 | 23 |  | 540 | 12 | 12 | House Fan
311 | Classroom | 178 | 11 |  | 690 | 15 | 11 | House Fan
Portable Building | Cafeteria 1 |  | 0 |  | 1840 | 41
Portable Building | Cafeteria 2 |  | 0 |  | 989 | 22
- | Auditorium | 0 | 0 | Yes | 5336 | 121 | 121 | House Fan
- | Basement Office/Classroom | 617 | 41 |  | 1088 | 24 | 24 | House Fan
- | Gym | 3331 | 222 |  | 5005 | 113 | 113 | AHU
- | Prinicipal Office |  | 0 |  | 108 | 2 | 0
- | Main Office |  | 0 |  | 234 | 5 | 0

## Farrell
Sheet Last Modified: | 2021-04-27
School: | Louis H. Farrell Elementary School
Vendor: | EMCOR | Retest
| Devine 2nd Retest | Devine 3rd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
A-2 | LS | 269 | 17 |  | 891 | 20 | 17 | Unit Ventilator
A-3 | LS | 319 | 21 |  | 891 | 20 | 20 | Unit Ventilator
A-4 | LS | 259 | 17 |  | 540 | 12 | 12 | Unit Ventilator
A-6 | LS | 274 | 18 |  | 891 | 20 | 18 | Unit Ventilator
A-10 | A-10 | 290 | 19 |  | 1130 | 25 | 19 | RTU
A-11 | A-11 | 276 | 18 |  | 800 | 18 | 18 | RTU
A-12 | A-12 | 296 | 19 |  | 800 | 18 | 18 | RTU
A-13 | A-13 | 306 | 20 |  | 800 | 18 | 18 | RTU
A-14 | A-14 | 293 | 19 |  | 800 | 18 | 18 | RTU
A-15 | A-15 | 331 | 22 |  | 800 | 18 | 18 | RTU
A-16 | A-16 | 303 | 20 |  | 800 | 18 | 18 | RTU
A-21 | A-21 | 314 | 20 |  | 800 | 18 | 18 | RTU
A-22 | A-22 | 285 | 19 |  | 800 | 18 | 18 | RTU
A-23 | A-23 | 293 | 19 |  | 800 | 18 | 18 | RTU
A-24 | A-24 | 293 | 19 |  | 800 | 18 | 18 | RTU
A-25 | A-25 | 333 | 22 |  | 800 | 18 | 18 | RTU
A-26 | A-26 | 316 | 21 |  | 800 | 18 | 18 | RTU
100 | LS | 328 | 21 |  | 1813 | 41 | 21 | Unit Ventilator
101 | LS | 326 | 21 |  | 1813 | 41 | 21 | Unit Ventilator
103 | LS | 406 | 27 |  | 925 | 21 | 21 | Unit Ventilator
105 | AS | 318 | 21 |  | 672 | 15 | 15 | Unit Ventilator
108 |  |  |  | Yes | 350 |  |  | N/A
111 | AS | 241 | 16 |  | 950 | 21 | 16 | Unit Ventilator
112 | ? | 282 | 18 |  | 950 | 21 | 18 | Unit Ventilator
113 | ? | 222 | 14 |  | 950 | 21 | 14 | Unit Ventilator
200 | LIT/SS | 318 | 21 |  | 950 | 21 | 21 | Unit Ventilator
201 | M/SC | 278 | 18 |  | 950 | 21 | 18 | Unit Ventilator
202 | LS | 297 | 19 |  | 950 | 21 | 19 | Unit Ventilator
203 | RELA/LS/EL PI | 297 | 19 |  | 950 | 21 | 19 | Unit Ventilator
204 | Classroom |  | 0 | Yes | 288 | 6 | 6 | Unit Ventilator
205 | M/SC/SS | 345 | 23 |  | 950 | 21 | 21 | Unit Ventilator
206 | RELA | 327 | 21 |  | 950 | 21 | 21 | Unit Ventilator
207 | ESOL | 372 | 24 |  | 950 | 21 | 21 | Unit Ventilator
208 | MATH | 308 | 20 |  | 950 | 21 | 20 | Unit Ventilator
209 | M/SC/SS | 294 | 19 |  | 950 | 21 | 19 | Unit Ventilator
209A |  |  |  | Yes | 310 |  |  | N/A
210 | RELA/SS | 203 | 13 |  | 950 | 21 | 13 | Unit Ventilator
211 | MATH/SC | 245 | 16 |  | 950 | 21 | 16 | Unit Ventilator
212 | RELA | 293 | 19 |  | 950 | 21 | 19 | Unit Ventilator
213 | SC/SS | 283 | 18 |  | 950 | 21 | 18 | Unit Ventilator
300 | RELA / SS | 265 | 17 |  | 950 | 21 | 17 | Unit Ventilator
301 | CSC | 277 | 18 |  | 950 | 21 | 18 | Unit Ventilator
302 | MATH | 254 | 16 |  | 950 | 21 | 16 | Unit Ventilator
303 | SC/SS | 224 | 14 |  | 950 | 21 | 14 | Unit Ventilator
304 | Room |  | 0 | Yes | 192 | 4 | 4
305 | SC/MATH | 287 | 19 |  | 950 | 21 | 19 | Unit Ventilator
306 | MATH | 300 | 20 |  | 950 | 21 | 20 | Unit Ventilator
307 | SS/RELA | 226 | 15 |  | 950 | 21 | 15 | Unit Ventilator
308 | RELA/EL B | 277 | 18 |  | 950 | 21 | 18 | Unit Ventilator
309 | SC/SS | 277 | 18 |  | 1175 | 26 | 18 | Unit Ventilator
310 | MATH | 346 | 23 |  | 950 | 21 | 21 | Unit Ventilator
311 | RELA EL PI | 232 | 15 |  | 950 | 21 | 15 | Unit Ventilator
312 | SS/RELA ALG | 203 | 13 |  | 950 | 21 | 13 | Unit Ventilator
313 | SC/MATH | 223 | 14 |  | 950 | 21 | 14 | Unit Ventilator
- | Lunchroom | 815 | 54 |  | 2604 | 59 | 54 | Unit Ventilator
Gymnasium | Gymnasium |  | 0 | Yes | 3940 | 89 | 89
Gymnasium | Office |  | 0 | Yes | 247 | 5 | 5
- | Auditorium | 72 | 4 |  | 3808 | 86 | 4 | Unit Ventilator
- | Main Office |  | 0 | Yes | 279 | 6 | 6 | N/A
- | Principal Office |  | 0 |  | 288 | 6 | 0 | N/A
Vice Principal | Office |  | 0 | Yes | 96 | 2 | 2
- | Counselor Office |  | 0 | Yes | 288 | 6 | 6 | N/A
Building Engineer | Office |  | 0 | Yes | 275 | 6 | 6
- | IMC |  | 0 | Yes | 1485 | 33 | 33 | N/A
- | Nurse |  | 0 | Yes | 234 | 5 | 5 | N/A

## Fell
Sheet Last Modified: | 2021-03-23
School: | D. Newlin Fell Elementary-Middle School |  |  | House fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
2 | Music Room | 519 | 34 |  | 418 | 9 | 9 | House Fan
100 | Classroom | 677 | 45 |  | 704 | 16 | 16 | House Fan
101 | Classroom | 791 | 52 |  | 308 | 7 | 7 | House Fan
102 | Classroom | 653 | 43 |  | 704 | 16 | 16 | House Fan
103 | Classroom | 588 | 39 |  | 660 | 15 | 15 | House Fan
104 | Classroom | 604 | 40 |  | 660 | 15 | 15 | House Fan
105 | Classroom | 960 | 64 |  | 660 | 15 | 15 | House Fan
106 | Classroom | 560 | 37 |  | 660 | 15 | 15 | House Fan
107 | Classroom | 760 | 50 |  | 682 | 15 | 15 | House Fan
108 | Classroom | 550 | 36 |  | 638 | 14 | 14 | House Fan
109 | Classroom | 491 | 32 |  | 687 | 15 | 15 | House Fan
200 | Classroom | 362 | 24 |  | 682 | 15 | 15 | House Fan
201 | Classroom | 750 | 50 |  | 638 | 14 | 14 | House Fan
202 | Classroom | 840 | 56 |  | 682 | 15 | 15 | House Fan
203 | Classroom | 411 | 27 |  | 660 | 15 | 15 | House Fan
204 | Classroom | 952 | 63 |  | 660 | 15 | 15 | House Fan
205 | Library | 670 | 44 |  | 638 | 14 | 14 | House Fan
206 | Library | 668 | 44 |  | 638 | 14 | 14 | House Fan
207 | Classroom | 512 | 34 |  | 682 | 15 | 15 | House Fan
208 | Classroom | 765 | 51 |  | 638 | 14 | 14 | House Fan
209 | Classroom | 478 | 31 |  | 682 | 15 | 15 | House Fan
300 | Classroom | 500 | 33 |  | 704 | 16 | 16 | House Fan
301 | Classroom | 406 | 27 |  | 638 | 14 | 14 | House Fan
302 | Classroom | 110 | 7 |  | 682 | 15 | 7 | House Fan
303 | Classroom | 426 | 28 |  | 660 | 15 | 15 | House Fan
304 | Classroom | 630 | 42 |  | 660 | 15 | 15 | House Fan
305 | Classroom | 888 | 59 |  | 660 | 15 | 15 | House Fan
306 | Classroom | 791 | 52 |  | 660 | 15 | 15 | House Fan
307 | Classroom | 407 | 27 |  | 682 | 15 | 15 | House Fan
308 | Classroom | 641 | 42 |  | 638 | 14 | 14 | House Fan
309 | Classroom | 645 | 43 |  | 704 | 16 | 16 | House Fan
309A | Classroom |  | 0 | Yes | 275 | 6 | 6 | N/A
310 | Classroom | 310 | 20 |  | 275 | 6 | 6 | House Fan
- | Auditrium | 3031 | 202 |  | 3055 | 69 | 69 | House Fan
- | Boys Bathroom | 300 | 20 |  | 114 | 2 | 2 | N/A
- | Cafeteria | 375 | 25 |  | 990 | 22 | 22 | House Fan
- | Girls Bathroom | 421 | 28 |  | 96 | 2 | 2 | N/A
- | Gym | 0 | 0 | Yes | 3219 | 73 | 73 | N/A
- | Main Office | 0 | 0 | Yes | 330 | 7 | 7 | House Fan
- | Principal Office |  | 0 | Yes | 288 | 6 | 6 | N/A
- | Nurse Office | 0 | 0 | Yes | 220 | 5 | 5 | House Fan
- | PTA Room | 900 | 60 |  | 1540 | 35 | 35 | House Fan
- | Speech Room | 438 | 29 |  | 506 | 11 | 11 | House Fan
- | Teachers Lounge | 0 | 0 |  | 330 | 7 | 0 | House Fan

## Fels
Sheet Last Modified: | 2021-04-30
School: | Samuel Fels High School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
A100 | Classroom | 69 | 4 |  | 290 | 6 | 4
A103 | Classroom | 125 | 8 |  | 870 | 19 | 8
A105 | Classroom | 148 | 9 |  | 870 | 19 | 9
A106 | Classroom | 147 | 9 |  | 870 | 19 | 9
A107 | Classroom | 135 | 9 |  | 870 | 19 | 9
A108 | Classroom | 39 | 2 |  | 870 | 19 | 2
A109 | Classroom | 162 | 10 |  | 870 | 19 | 10
A110 | Classroom | 162 | 10 |  | 870 | 19 | 10
A111 | Classroom | 167 | 11 |  | 870 | 19 | 11
A113 | Classroom | 161 | 10 |  | 870 | 19 | 10
A114 | Classroom | 0 | 0 |  | 930 | 21 | 0
A120 | Office | 125 | 8 |  | 144 | 3 | 3
A123 | Classroom | 298 | 19 |  | 900 | 20 | 19
A124 | Classroom | 345 | 23 |  | 900 | 20 | 20
A125 | Classroom | 376 | 25 |  | 900 | 20 | 20
A126 | Classroom | 266 | 17 |  | 900 | 20 | 17
A130 | Classroom | 697 | 46 |  | 900 | 20 | 20
A131 | Classroom | 155 | 10 |  | 900 | 20 | 10
A132 | Classroom | 291 | 19 |  | 960 | 21 | 19
A135 | Classroom | 645 | 43 |  | 960 | 21 | 21
A136 | Classroom | 162 | 10 |  | 960 | 21 | 10
A137 | Classroom | 229 | 15 |  | 1320 | 30 | 15
A138 | Classroom | 963 | 64 |  | 1376 | 31 | 31
A139 | Classroom | 161 | 10 |  | 1376 | 31 | 10
A140 | Classroom | 1027 | 68 |  | 1376 | 31 | 31
A142 | Classroom | 1338 | 89 |  | 1271 | 28 | 28
A143 | Classroom | 964 | 64 |  | 1505 | 34 | 34
A144 | Classroom | 937 | 62 |  | 1394 | 31 | 31
A148 | Hallway | 193 | 12 |  |  | 0 | 0
A150 | Hallway | 255 | 17 |  |  | 0 | 0
A152 | Hallway | 180 | 12 |  |  | 0 | 0
A200 | Classroom | 451 | 30 |  | 290 | 6 | 6
A203 | Classroom | 252 | 16 |  | 870 | 19 | 16
A205 | Classroom | 332 | 22 |  | 870 | 19 | 19
A206 | Classroom | 911 | 60 |  | 870 | 19 | 19
A207 | Classroom | 536 | 35 |  | 870 | 19 | 19
A208 | Classroom | 1475 | 98 |  | 870 | 19 | 19
A209 | Classroom | 620 | 41 |  | 870 | 19 | 19
A210 | Classroom | 1060 | 70 |  | 870 | 19 | 19
A211 | Classroom | 1246 | 83 |  | 870 | 19 | 19
A212 | Classroom | 1262 | 84 |  | 1271 | 28 | 28
A213 | Classroom | 879 | 58 |  | 961 | 21 | 21
A214 | Classroom | 667 | 44 |  | 961 | 21 | 21
A220 | Office | 7 | 0 |  | 144 | 3 | 0
A223 | Classroom | 486 | 32 |  | 1860 | 42 | 32
A225 | Classroom | 90 | 6 |  | 160 | 3 | 3
A226 | Classroom | 323 | 21 |  | 900 | 20 | 20
A227 | Classroom | 830 | 55 |  | 960 | 21 | 21
A231 | Classroom | 260 | 17 |  | 1320 | 30 | 17
A236 | Classroom | 8 | 0 |  | 120 | 2 | 0
A237 | Classroom | 9 | 0 |  | 104 | 2 | 0
A238 | Classroom | 207 | 13 |  | 1680 | 38 | 13
A239 | Classroom | 1272 | 84 |  | 1376 | 31 | 31
A240 | Classroom | 249 | 16 |  | 224 | 5 | 5
A241 | Classroom | 1797 | 119 |  | 1364 | 31 | 31
A242 | Classroom | 1960 | 130 |  | 1320 | 30 | 30
A243 | Classroom | 960 | 64 |  | 1320 | 30 | 30
A244 | Classroom | 1222 | 81 |  | 1505 | 34 | 34
A245 | Classroom | 695 | 46 |  | 1394 | 31 | 31
A248 | Hallway | 0 | 0 |  |  | 0 | 0
A250 | Hallway | 297 | 19 |  |  | 0 | 0
A252 | Hallway | 566 | 37 |  |  | 0 | 0
A255 | Classroom | 0 | 0 |  | 120 | 2 | 0
B100 | Classroom | 0 | 0 |  | 930 | 21 | 0
B102 | Classroom | 0 | 0 |  | 961 | 21 | 0
B103 | Classroom | 0 | 0 |  | 1023 | 23 | 0
B105 | Classroom | 0 | 0 |  | 1311 | 29 | 0
B106 | Classroom | 0 | 0 |  | 280 | 6 | 0
B107 | Classroom | 0 | 0 |  | 1265 | 28 | 0
B108 | Classroom | 0 | 0 |  | 961 | 21 | 0
B109 | Classroom | 0 | 0 |  | 961 | 21 | 0
B117 | Classroom | 0 | 0 |  | 576 | 13 | 0
B118 | Classroom | 0 | 0 |  | 961 | 21 | 0
B120 | Classroom | 0 | 0 |  | 208 | 4 | 0
B123 | Classroom | 0 | 0 |  | 990 | 22 | 0
B124 | Classroom | 0 | 0 |  | 990 | 22 | 0
B125 | Hallway | 0 | 0 |  |  | 0 | 0
B126 | Hallway | 0 | 0 |  |  | 0 | 0
B127 | Hallway | 0 | 0 |  |  | 0 | 0
B128 | Hallway | 0 | 0 |  |  | 0 | 0
B200 | Classroom | 0 | 0 |  | 930 | 21 | 0
B201 | Classroom | 0 | 0 |  | 1316 | 29 | 0
B201B | Classroom | 0 | 0 |  | 224 | 5 | 0
B202 | Classroom | 0 | 0 |  | 961 | 21 | 0
B203 | Classroom | 0 | 0 |  | 1023 | 23 | 0
B204 | Classroom | 0 | 0 |  | 1311 | 29 | 0
B205 | Classroom | 0 | 0 |  | 1265 | 28 | 0
B208 | Classroom | 0 | 0 |  | 961 | 21 | 0
B209 | Classroom | 0 | 0 |  | 961 | 21 | 0
B210 | Classroom | 0 | 0 |  | 144 | 3 | 0
B218 | Classroom | 0 | 0 |  | 990 | 22 | 0
B219 | Classroom | 0 | 0 |  | 990 | 22 | 0
B222 | Hallway | 0 | 0 |  |  | 0 | 0
B223 | Hallway | 0 | 0 |  |  | 0 | 0
B224 | Hallway | 0 | 0 |  |  | 0 | 0
B225 | Hallway | 0 | 0 |  |  | 0 | 0
C101 | Front of house | 160 | 10 |  | 384 | 8 | 8
C103 | Auditorium | 12689 | 845 |  | 9310 | 211 | 211
C105 | Stage | 770 | 51 |  | 3400 | 77 | 51
C106 | Classroom | 0 | 0 |  | 1302 | 29 | 0
C107 | Backstage | 59 | 3 |  | 870 | 19 | 3
C108 | Classroom | 39 | 2 |  | 870 | 19 | 2
C109 | Classroom | 77 | 5 |  | 870 | 19 | 5
C110 | Classroom | 89 | 5 |  | 870 | 19 | 5
C111 | Classroom | 576 | 38 |  | 870 | 19 | 19
C112 | Classroom | 112 | 7 |  | 870 | 19 | 7
C113 | Classroom | 1414 | 94 |  | 2016 | 45 | 45
C114 | Classroom | 20 | 1 |  | 870 | 19 | 1
C115 | Classroom | 18 | 1 |  | 840 | 19 | 1
C116 | Classroom | 20 | 1 |  | 840 | 19 | 1
C117 | Classroom | 18 | 1 |  | 840 | 19 | 1
C118 | Classroom | 210 | 14 |  | 840 | 19 | 14
C119 | Classroom | 168 | 11 |  | 840 | 19 | 11
C121 | Classroom | 0 | 0 |  | 840 | 19 | 0
D104 | Locker room | 4 | 0 |  | 1680 | 38 | 0
D105 | Locker room | 5 | 0 |  | 1680 | 38 | 0
D106 | Office | 25 | 1 |  | 120 | 2 | 1
D109 | Locker room | 12 | 0 |  | 522 | 11 | 0
D111 | Locker room | 8 | 0 |  | 522 | 11 | 0
D112 | Office | 22 | 1 |  | 240 | 5 | 1
D113 | Office | 26 | 1 |  | 240 | 5 | 1
D114 | Locker room | 39 | 2 |  | 720 | 16 | 2
D115 | Office | 0 | 0 |  | 260 | 5 | 0
D116 | Weight room | 181 | 12 |  | 1392 | 31 | 12
D119 | Classroom | 91 | 6 |  | 1240 | 28 | 6
D126 | Vestibule | 42 | 2 |  |  | 0 | 0
D128 | Hallway | 249 | 16 |  |  | 0 | 0
E100A | Library | 274 | 18 |  | 9200 | 209 | 18
E100B | Office | 28 | 1 |  | 225 | 5 | 1
E101 | Classroom | 17 | 1 |  | 992 | 22 | 1
E102 | Office | 12 | 0 |  | 225 | 5 | 0
E103 | Office | 14 | 0 |  | 225 | 5 | 0
E104 | Office | 0 | 0 |  | 150 | 3 | 0
E105A | Storage | 6 | 0 |  |  | 0 | 0
E105B | Storage | 8 | 0 |  |  | 0 | 0
E107 | Office | 52 | 3 |  | 286 | 6 | 3
E111 | Office | 0 | 0 |  | 368 | 8 | 0
E112 | Hallway | 0 | 0 |  |  | 0 | 0
E113 | Office | 0 | 0 |  | 132 | 3 | 0
E114 | Office | 0 | 0 |  | 84 | 1 | 0
E115 | Office | 0 | 0 |  | 180 | 4 | 0
E116 | Office | 0 | 0 |  | 72 | 1 | 0
E117 | Office | 0 | 0 |  | 120 | 2 | 0
E118 | Hallway | 0 | 0 |  |  | 0 | 0
E119 | Office | 0 | 0 |  | 400 | 9 | 0
E120 | Office | 0 | 0 |  | 180 | 4 | 0
E121 | Office | 0 | 0 |  | 180 | 4 | 0
E123 | Office | 0 | 0 |  | 220 | 5 | 0
E124 | Office | 0 | 0 |  | 220 | 5 | 0
E125 | Office | 0 | 0 |  | 150 | 3 | 0
E126 | Office | 0 | 0 |  | 216 | 4 | 0
E127 | Office | 0 | 0 |  | 90 | 2 | 0
E128 | Office | 0 | 0 |  | 150 | 3 | 0
E129 | Office | 0 | 0 |  | 216 | 4 | 0
E130 | Office | 0 | 0 |  | 285 | 6 | 0
E131 | Office | 0 | 0 |  | 195 | 4 | 0
E132 | Office | 0 | 0 |  | 195 | 4 | 0
E133 | Office | 0 | 0 |  | 315 | 7 | 0
E134 | Office | 0 | 0 |  | 315 | 7 | 0
E137 | Office | 0 | 0 |  | 420 | 9 | 0
E139 | Office | 0 | 0 |  | 264 | 6 | 0
E144 | Server room | 0 | 0 |  | 368 | 8 | 0
E146 | Hallway | 0 | 0 |  |  | 0 | 0
E147 | Hallway | 0 | 0 |  |  | 0 | 0
E148 | Hallway | 0 | 0 |  |  | 0 | 0
E149 | Vestibule | 0 | 0 |  |  | 0 | 0
E150 | Vestibule | 0 | 0 |  |  | 0 | 0
E151 | Hallway | 0 | 0 |  |  | 0 | 0
E152 | Hallway | 0 | 0 |  |  | 0 | 0
E157 | Hallway | 0 | 0 |  |  | 0 | 0
E201 | Office | 0 | 0 |  | 126 | 2 | 0
E202 | Office | 0 | 0 |  | 126 | 2 | 0
E203B | Office | 0 | 0 |  | 266 | 6 | 0
E204 | Office | 0 | 0 |  | 126 | 2 | 0
E205 | Office | 0 | 0 |  | 126 | 2 | 0
E209 | Office | 0 | 0 |  | 1040 | 23 | 0
E210 | Hallway | 0 | 0 |  |  | 0 | 0
F100 | Cafeteria | 8136 | 542 |  | 8448 | 192 | 192
F101 | Kitchen | 1521 | 101 |  | 1636 | 37 | 37
F104 | Kitchen | 81 | 5 |  | 230 | 5 | 5
F106 | Kitchen | 99 | 6 |  | 306 | 6 | 6
F107 | Kitchen | 0 | 0 |  | 401 | 9 | 0
F108 | Kitchen | 199 | 13 |  | 836 | 19 | 13
F109 | Maintenance | 59 | 3 |  | 686 | 15 | 3
F110 | Maintenance | 40 | 2 |  | 256 | 5 | 2
F111 | Maintenance | 69 | 4 |  | 162 | 3 | 3
F112 | Maintenance | 89 | 5 |  | 340 | 7 | 5
F116 | Kitchen | 0 | 0 |  | 1636 | 37 | 0
F119 | Engineer's office | 135 | 9 |  | 176 | 4 | 4
F120 | Hallway | 149 | 9 |  |  | 0 | 0
F121 | Hallway | 1306 | 87 |  |  | 0 | 0
- | Gym | 2098 | 139 |  | 13184 | 299 | 139
- | Office | 0 | 0 |  | 120 | 2 | 0
- | Storage | 0 | 0 |  |  | 0 | 0
- | Pool | 5277 | 351 |  | 6426 | 146 | 146
- | Principal Office | 0 | 0 |  | 288 | 6 | 0
- | Stage | 3751 | 250 |  | 3400 | 77 | 77

## Feltonville A&S
Sheet Last Modified: | 2021-04-06
School: | Feltonville Arts & Sciences Middle School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
104 | Classroom | 256 | 17 |  | 774.56 | 17 | 17
105 | Classroom | 614 | 40 |  | 810.43 | 18 | 18
106 | Classroom | 599 | 39 |  | 802.43 | 18 | 18
107 | Classroom | 428 | 28 |  | 803.93 | 18 | 18
108 | Classroom | 352 | 23 |  | 802.07 | 18 | 18
109 | Classroom | 699 | 46 |  | 791.18 | 17 | 17
110 | Classroom | 311 | 20 |  | 837.81 | 19 | 19
111 | Classroom | 232 | 15 |  | 953.28 | 21 | 15
112 | Classroom | 311 | 20 |  | 632.55 | 14 | 14
205 | Classroom | 455 | 30 |  | 773.66 | 17 | 17
206 | Classroom | 398 | 26 |  | 759.35 | 17 | 17
207 | Classroom | 352 | 23 |  | 748.96 | 17 | 17
208 | Classroom | 313 | 20 |  | 811.86 | 18 | 18
210 | Classroom | 0 | 0 | Yes | 807.56 | 18 | 18
211 | Classroom | 650 | 43 |  | 764.62 | 17 | 17
212 | Classroom | 283 | 18 |  | 802.2 | 18 | 18
214 | Classroom | 605 | 40 |  | 632.47 | 14 | 14
301 | Classroom | 288 | 19 |  | 775.54 | 17 | 17
302 | Classroom | 297 | 19 |  | 760.03 | 17 | 17
303 | Classroom | 305 | 20 |  | 816.97 | 18 | 18
304 | Classroom | 700 | 46 |  | 811.04 | 18 | 18
305 | Classroom | 357 | 23 |  | 807.88 | 18 | 18
306 | Classroom | 490 | 32 |  | 783.38 | 17 | 17
307 | Classroom | 309 | 20 |  | 802.84 | 18 | 18
308 | Classroom | 211 | 14 | Yes | 808.55 | 18 | 18
309 | Classroom | 1419 | 94 |  | 2222.6 | 50 | 50
- | Basement | 4061 | 270 |  | 4615.44 | 104 | 104
- | Cafeteria, Kitchen, Faculty Room | 761 | 50 |  | 5110.25 | 116 | 50
- | Classroom above 214 | 403 | 26 |  | 630.96 | 14 | 14
- | Classroom Art Lab Computer Lab | 315 | 21 | Yes | 1016.7 | 23 | 23
- | Classroom Science Lab 1 | 345 | 23 |  | 992.97 | 22 | 22
- | Classroom Science Lab 2 3rd Floor | 344 | 22 |  | 989.1 | 22 | 22
- | Classroom Science Lab 2 Right | 455 | 30 |  | 989 | 22 | 22
- | Classroom Science Lab STEM Lab Left | 740 | 49 |  | 1631.1 | 37 | 37
- | Dean's Office 1st Floor | 31 | 2 | Yes | 170.48 | 3 | 3
- | Dean's Office 2nd Floor | 18 | 1 | Yes | 169.62 | 3 | 3
- | Dean's Office 3rd Floor | 38 | 2 | Yes | 168.4 | 3 | 3
- | Drama Room | 747 | 49 |  | 3095 | 70 | 49
- | First Floor | 5315 | 354 |  | 6973.77 | 158 | 158
- | First Floor Multi-Purpose Room | 572 | 38 |  | 3094.6 | 70 | 38
- | Gym | 1186 | 79 |  | 5236.7 | 119 | 79
- | Health Room | 0 | 0 | Yes | 594.4 | 13 | 13
- | Second Floor | 1094 | 72 |  | 4743.17 | 107 | 72

## Feltonville Intermediate
Sheet Last Modified: | 2021-04-29
School: | Feltonville Intermediate Elementary School
Vendor: | EMCOR | Exhaust Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | - |  | 0 | Yes | 462 | 10 | 10
101 | - |  | 0 |  | 948 | 21 | 0
101A | - |  | 0 |  | 127 | 2 | 0
102 | - |  | 0 | Yes | 243 | 5 | 5
103 | - |  | 0 |  | 101 | 2 | 0
103A | - |  | 0 |  | 125 | 2 | 0
104 | - |  | 0 | Yes | 967 | 21 | 21
106 | - |  | 0 | Yes | 1120 | 25 | 25
107 | - |  | 0 |  | 213 | 4 | 0
108 | Room |  | 0 | Yes | 1436 | 32 | 32
109 | Room | 0 | 0 | Yes | 893 | 20 | 20
110 | Room | 647 | 43 |  | 1479 | 33 | 33
112 | Room |  | 0 | Yes | 1415 | 32 | 32
112A | - |  | 0 |  | 129 | 2 | 0
113 | Room |  | 0 |  | 1200 | 27 | 0
114 | - |  | 0 | Yes | 976 | 22 | 22
116 | - |  | 0 |  | 1064 | 24 | 0
118 | Gym Office | 0 | 0 |  | 1027 | 23 | 0
153A | Small Office Inside M/O |  | 0 |  | 108 | 2 | 0
156B | Counselor #2 |  | 0 |  | 182 | 4 | 0
157 | - |  | 0 |  | 108 | 2 | 0
200 | - |  | 0 |  | 478 | 10 | 0
201 | - |  | 0 | Yes | 1071 | 24 | 24
202 | - |  | 0 |  | 578 | 13 | 0
202A | - |  | 0 |  | 179 | 4 | 0
203 | - |  | 0 | Yes | 677 | 15 | 15
203A | - |  | 0 |  | 436 | 9 | 0
204 | - |  | 0 | Yes | 574 | 13 | 13
205 | - |  | 0 |  | 829 | 18 | 0
206 | - |  | 0 | Yes | 629 | 14 | 14
206A | - |  | 0 |  | 220 | 5 | 0
207 | - |  | 0 | Yes | 818 | 18 | 18
207A | - |  | 0 |  | 126 | 2 | 0
208 | - |  | 0 | Yes | 752 | 17 | 17
208A | - |  | 0 |  | 113 | 2 | 0
209 | - |  | 0 | Yes | 788 | 17 | 17
210 | - | 225 | 15 | Yes | 740 | 16 | 16
300 | - |  | 0 | Yes | 858 | 19 | 19
301 | - |  | 0 | Yes | 491 | 11 | 11
302 | - |  | 0 | Yes | 765 | 17 | 17
303 | - |  | 0 | Yes | 667 | 15 | 15
304 | - |  | 0 |  | 505 | 11 | 0
305 | - |  | 0 | Yes | 626 | 14 | 14
306 | - |  | 0 | Yes | 769 | 17 | 17
307 | - |  | 0 | Yes | 1108 | 25 | 25
307A | - |  | 0 |  | 73 | 1 | 0
307B | - |  | 0 |  | 127 | 2 | 0
309 | - |  | 0 |  | 488 | 11 | 0
309A | - |  | 0 |  | 135 | 3 | 0
311 | - |  | 0 | Yes | 842 | 19 | 19
313 | - |  | 0 | Yes | 662 | 15 | 15
315 | - |  | 0 | Yes | 735 | 16 | 16
- | Bradham Office |  | 0 |  | 141 | 3 | 0
- | Cafeteria (2nd Floor) |  | 0 |  | 5423 | 123 | 0
- | Confrence Room |  | 0 |  | 216 | 4 | 0
- | Counselor |  | 0 |  | 132 | 3 | 0
- | Custodial Staff Room |  | 0 |  | 118 | 2 | 0
- | Food Service Locker Room |  | 0 |  | 83 | 1 | 0
- | Food Service Manager's Office |  | 0 |  | 56 | 1 | 0
- | Gymnasium |  | 0 |  | 4006 | 91 | 0
- | Kitchen |  | 0 |  | 954 | 21 | 0
- | Main Office |  | 0 |  | 505 | 11 | 0
- | MPR / Auditorium |  | 0 | Yes | 2669 | 60 | 60
- | Nurse |  | 0 |  | 191 | 4 | 0
- | Nurse Waiting Area |  | 0 |  | 159 | 3 | 0
- | Principal's Office |  | 0 |  | 351 | 7 | 0
- | Psychologist's Office |  | 0 |  | 66 | 1 | 0
- | Storage |  | 0 |  | 107 | 2 | 0
- | Storage Room #2 |  | 0 |  | 99 | 2 | 0
- | Supply Closet |  | 0 |  | 126 | 2 | 0
- | Teacher's Lounge |  | 0 |  | 226 | 5 | 0
- | 1st Floor Lunchroom | 0 | 0 |  | 2677 | 60 | 0
- | Closet | 34 | 2 |  | 40 | 0 | 0
- | 3rd Floor Lunchroom |  | 0 |  | 4452 | 101 | 0
- | Cafeteria Manager's Office | 75 | 5 |  | 55 | 1 | 1

## Feltonville Headstart
Sheet Last Modified: | 2021-02-23
School: | Feltonville Headstart |  |  | House Fan Abated
Vendor: | N/A
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit

## Finletter
Sheet Last Modified: | 2021-03-24
School: | Thomas Finletter Academics Plus Elementary School |  |  |  | House fan Abated
Vendor: | Devine |  | Devine Brothers Retest
School: | Finletter LSH
Vendor: | Chadwick
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Finletter Main Building
101 | Classroom | 535 | 35 |  | 1056 | 24 | 24 | House Fan
102 | Classroom | 458 | 30 |  | 1056 | 24 | 24 | House Fan
103 | Classroom | 621 | 41 |  | 1056 | 24 | 24 | House Fan
104 | Classroom | 595 | 39 |  | 870 | 19 | 19 | House Fan
105 | Classroom | 554 | 36 |  | 870 | 19 | 19 | House Fan
106 | Classroom | 1227 | 81 |  | 870 | 19 | 19 | House Fan
107 | Classroom | 980 | 65 |  | 870 | 19 | 19 | House Fan
108 | Classroom | 817 | 54 |  | 899 | 20 | 20 | House Fan
109 | Classroom | 876 | 58 |  | 899 | 20 | 20 | House Fan
110 | Classroom | 535 | 35 |  | 928 | 21 | 21 | House Fan
201 | Classroom | 477 | 31 |  | 1056 | 24 | 24 | House Fan
202 | Classroom | 334 | 22 |  | 1056 | 24 | 22 | House Fan
203 | Classroom | 411 | 27 |  | 1056 | 24 | 24 | House Fan
204 | Classroom | 916 | 61 |  | 870 | 19 | 19 | House Fan
205 | Classroom | 1018 | 67 |  | 870 | 19 | 19 | House Fan
206 | Classroom | 1222 | 81 |  | 870 | 19 | 19 | House Fan
207 | Classroom | 1203 | 80 |  | 870 | 19 | 19 | House Fan
208 | Classroom | 450 | 30 |  | 899 | 20 | 20 | House Fan
209 | Classroom | 363 | 24 |  | 899 | 20 | 20 | House Fan
210 | Classroom | 434 | 28 |  | 928 | 21 | 21 | House Fan
211 | Classroom | 0 | 0 |  | 195 | 4 | 0 | N/A
212 | Classroom | 0 | 0 |  | 384 | 8 | 0 | N/A
301 | Classroom | 278 | 18 |  | 1056 | 24 | 18 | House Fan
302 | Classroom | 458 | 30 |  | 1056 | 24 | 24 | House Fan
303 | Classroom | 125 | 8 |  | 1056 | 24 | 8 | House Fan
304 | Classroom | 288 | 19 |  | 870 | 19 | 19 | House Fan
305 | Classroom | 645 | 43 |  | 870 | 19 | 19 | House Fan
306 | Classroom | 289 | 19 |  | 870 | 19 | 19 | House Fan
307 | Classroom | 654 | 43 |  | 870 | 19 | 19 | House Fan
308 | Classroom | 345 | 23 |  | 899 | 20 | 20 | House Fan
309 | Classroom | 319 | 21 |  | 899 | 20 | 20 | House Fan
310 | Classroom | 675 | 45 |  | 928 | 21 | 21 | House Fan
311 | Classroom | 705 | 47 |  | 667 | 15 | 15 | House Fan
312 | Classroom | 0 | 0 |  | 275 | 6 | 0 | N/A
402 | Health | 335 | 22 |  | 588 | 13 | 13 | House Fan
403 | Music Room | 491 | 32 |  | 990 | 22 | 22 | House Fan
- | Annex Classroom | 65 | 4 |  | 960 | 21 | 4 | House Fan
- | Art | 882 | 58 |  | 1421 | 32 | 32 | House Fan
- | Auditorium | 3675 | 245 |  | 3431 | 77 | 77 | House Fan
- | Health Classroom | 0 | 0 |  | 250 | 5 | 0 | House Fan
- | Gym/Cafe |  | 0 | Yes | 3432 | 78 | 78
- | Main office | 0 | 0 | Yes | 322 | 7 | 7 | N/A
Finletter LSH
105 | Womens Staff Bathroom |  | 0 |  | 96 | 2 | 0 | AHU
105 | Mens Staff Bathroom |  | 0 |  | 77 | 1 | 0 | AHU
106 | Custodial | 57 | 3 |  | 36 | 0 | 0 | AHU
111 | Lobby |  | 0 |  | 187 | 4 | 0 | AHU
112 | Office | 118 | 7 |  | 110 | 2 | 2 | AHU
113 | Office | 118 | 7 |  | 110 | 2 | 2 | AHU
114 | General Storage | 216 | 14 |  | 54 | 1 | 1 | AHU
115 | Multipurpose Room | 2476 | 165 |  | 2166 | 49 | 49 | AHU
116 | Corridor #2 |  | 0 |  | 120 | 2 | 0 | AHU
123 | Custodial Storage | 76 | 5 |  | 54 | 1 | 1 | AHU
125 | Academic Storage | 66 | 4 |  | 18 | 0 | 0 | AHU
A | Classroom | 341 | 22 |  | 986 | 22 | 22 | AHU
B | Classroom | 332 | 22 |  | 986 | 22 | 22 | AHU
C | Classroom | 341 | 22 |  | 986 | 22 | 22 | AHU
D | Classroom | 332 | 22 |  | 986 | 22 | 22 | AHU
E | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU
F | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU
G | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU
H | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU
I | Classroom | 293 | 19 |  | 986 | 22 | 19 | AHU
J | Classroom | 359 | 23 |  | 986 | 22 | 22 | AHU
K | Classroom | 293 | 19 |  | 986 | 22 | 19 | AHU
L | Classroom | 359 | 23 |  | 986 | 22 | 22 | AHU
- | Custodial Office |  | 0 | Yes |  | 0 | 0 | AHU
- | Teachers Lounge |  | 0 | No | 288 | 6 | 0 | AHU

## Fitler
Sheet Last Modified: | 2021-03-22
School: | Fitler Academic Plus Elementary School
Vendor: | Devine | Meehan | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
105 | Classroom | 707 | 47 |  | 1024 | 23 | 23 | House Fan
106 | Classroom | 796 | 53 |  | 720 | 16 | 16 | House Fan
107 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan
201 | Classroom | 834 | 55 |  | 1024 | 23 | 23 | House Fan
202 | Classroom | 879 | 58 |  | 1024 | 23 | 23 | House Fan
203 | Classroom | 510 | 34 |  | 1024 | 23 | 23 | House Fan
204 | Classroom | 951 | 63 |  | 1024 | 23 | 23 | House Fan
205 | Classroom | 716 | 47 |  | 1024 | 23 | 23 | House Fan
206 | Classroom | 668 | 44 |  | 720 | 16 | 16 | House Fan
207 | Classroom | 78 | 5 | Yes | 720 | 16 | 16 | House Fan
301 | Classroom | 860 | 57 |  | 720 | 16 | 16 | House Fan
302 | Classroom | 550 | 36 |  | 1024 | 23 | 23 | House Fan
303 | Classroom | 538 | 35 |  | 1024 | 23 | 23 | House Fan
304 | Classroom | 957 | 63 |  | 1024 | 23 | 23 | House Fan
305 | Classroom | 746 | 49 |  | 1024 | 23 | 23 | House Fan
306 | Classroom | 637 | 42 |  | 720 | 16 | 16 | House Fan
307 | Classroom | 364 | 24 | Yes | 720 | 16 | 16 | House Fan
- | Combo room | 883 | 58 |  | 1024 | 23 | 23 | House Fan
- | Gym | 1325 | 88 |  | 1344 | 30 | 30 | House Fan
- | Library | 1641 | 109 |  | 2400 | 54 | 54 | House Fan
- | Main office | 850 | 56 |  | 1156 | 26 | 26 | House Fan
- | Restroom | 781 | 52 |  | 660 | 15 | 15 | House Fan
- | Counselors Office | 1062 | 70 |  | 175 | 3 | 3 | ERU
- | Cafeteria | 0 | 0 |  | 1944 | 44 | 0 | NA
- | Nurses Office |  | 0 | Yes | 75 | 1 | 1

## Fitzpatrick
Sheet Last Modified: | 2021-03-12
School: | Aloysius L. Fitzpatrick Elementary School
Vendor: | Devine Brothers | Part 2 | Part 3
School: | Aloysius L. Fitzpatrick Elementary School Annex
Vendor: | Devine Brothers | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
B-10 | Classroom | 313 | 20 |  | 704 | 16 | 16 | Unit Ventilator
100 | Classroom | 298 | 19 |  | 660 | 15 | 15 | Unit Ventilator
101 | Classroom | 281 | 18 |  | 744 | 16 | 16 | Unit Ventilator
102 | Classroom | 315 | 21 |  | 840 | 19 | 19 | Unit Ventilator
103 | Classroom | 289 | 19 |  | 840 | 19 | 19 | Unit Ventilator
104 | Classroom | 337 | 22 |  | 805 | 18 | 18 | Unit Ventilator
105 | Classroom | 306 | 20 |  | 840 | 19 | 19 | Unit Ventilator
106 | Classroom | 293 | 19 |  | 840 | 19 | 19 | Unit Ventilator
107 | Classroom | 287 | 19 |  | 576 | 13 | 13 | Unit Ventilator
108 | Classroom | 409 | 27 |  | 828 | 18 | 18 | Unit Ventilator
109 | Classroom | 26 | 1 | Yes | 600 | 13 | 13 | Unit Ventilator
110 | Classroom | 340 | 22 |  | 840 | 19 | 19 | Unit Ventilator
112 | Classroom | 341 | 22 |  | 828 | 18 | 18 | Unit Ventilator
200 | Classroom | 319 | 21 |  | 840 | 19 | 19 | Unit Ventilator
201 | Classroom | 275 | 18 |  | 840 | 19 | 18 | Unit Ventilator
202 | Classroom | 300 | 20 |  | 840 | 19 | 19 | Unit Ventilator
203 | Classroom | 309 | 20 |  | 840 | 19 | 19 | Unit Ventilator
204 | Classroom | 290 | 19 |  | 840 | 19 | 19 | Unit Ventilator
205 | Classroom | 314 | 20 |  | 840 | 19 | 19 | Unit Ventilator
206 | Library | 656 | 43 |  | 1680 | 38 | 38 | Unit Ventilator
207 | Classroom | 326 | 21 |  | 425 | 9 | 9 | Unit Ventilator
210 | Classroom | 293 | 19 |  | 840 | 19 | 19 | Unit Ventilator
212 | Classroom | 334 | 22 |  | 840 | 19 | 19 | Unit Ventilator
214 | Classroom | 304 | 20 |  | 840 | 19 | 19 | Unit Ventilator
216 | Classroom | 325 | 21 |  | 840 | 19 | 19 | Unit Ventilator
218 | Classroom | 307 | 20 |  | 840 | 19 | 19 | Unit Ventilator
300 | Classroom | 289 | 19 |  | 864 | 19 | 19 | Unit Ventilator
301 | Classroom | 305 | 20 |  | 840 | 19 | 19 | Unit Ventilator
302 | Classroom | 281 | 18 |  | 840 | 19 | 18 | Unit Ventilator
303 | Classroom | 299 | 19 |  | 840 | 19 | 19 | Unit Ventilator
304 | Classroom | 329 | 21 |  | 840 | 19 | 19 | Unit Ventilator
305 | Classroom | 294 | 19 |  | 840 | 19 | 19 | Unit Ventilator
306 | Classroom | 607 | 40 |  | 1704 | 38 | 38 | Unit Ventilator
307 | Classroom | 340 | 22 |  | 425 | 9 | 9 | Unit Ventilator
310 | Classroom | 299 | 19 |  | 840 | 19 | 19 | Unit Ventilator
312 | Classroom | 326 | 21 |  | 840 | 19 | 19 | Unit Ventilator
314 | Classroom | 304 | 20 |  | 840 | 19 | 19 | Unit Ventilator
316 | Classroom | 329 | 21 |  | 840 | 19 | 19 | Unit Ventilator
318 | Classroom | 337 | 22 |  | 840 | 19 | 19 | Unit Ventilator
- | Auditorium | 92 | 6 |  | 1825 | 41 | 6 | AHU
B-1 | Classroom | 466 | 31 |  | 966 | 21 | 21 | Unit Ventilator
B-2 | Classroom | 287 | 19 |  | 966 | 21 | 19 | Unit Ventilator
B-4 | Classroom | 236 | 15 |  | 704 | 16 | 15 | Unit Ventilator
B-8 | Classroom | 269 | 17 |  | 792 | 18 | 17 | Unit Ventilator
- | Cafeteria | 72 | 4 |  | 2835 | 64 | 4 | Unit Ventilator
- | Gymnasium | 72 | 4 | Yes | 3922 | 89 | 89 | AHU
- | Main Office | 284 | 18 |  | 1000 | 22 | 18 | Unit Ventilator
- | Music | 29 | 1 |  | 768 | 17 | 1 | Unit Ventilator
Annex Building
9 | Classroom | 165 | 11 | Yes | 1040 | 23 | 23 | Unit Ventilator
10 | Classroom | 310 | 20 |  | 864 | 19 | 19 | Unit Ventilator
11 | Classroom | 311 | 20 |  | 962 | 21 | 20 | Unit Ventilator
12 | Classroom | 291 | 19 |  | 1040 | 23 | 19 | Unit Ventilator

## Forrest
Sheet Last Modified: | 2021-04-14
School: | Edwin Forrest Elementary School
Vendor: | Devine Brothers
School: | Edwin Forrest Elementary School- Little School House
Vendor: | Devine Brothers | Devine Brothers Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Edwin Forrest Elementary School Main Building
- | Auditorium | 955 | 63 |  | 3552 | 80 | 63 | Unit Ventilator
- | PreK | 281 | 18 |  | 1084 | 24 | 18 | Unit Ventilator
101 | admin |  | 0 | Yes | 920 | 20 | 20 | House Fan
102 | 2nd |  | 0 | Yes | 690 | 15 | 15 | House Fan
103 | admin |  | 0 | Yes | 736 | 16 | 16 | House Fan
104 | Specialist K-6 |  | 0 | Yes | 690 | 15 | 15 | House Fan
105 | 2nd grade |  | 0 | Yes | 690 | 15 | 15 | House Fan
106 | 2nd |  | 0 | Yes | 690 | 15 | 15 | House Fan
107 | 4th |  | 0 | Yes | 690 | 15 | 15 | House Fan
108 | 2nd |  | 0 | Yes | 736 | 16 | 16 | House Fan
109 | 2nd |  | 0 | Yes | 690 | 15 | 15 | House Fan
- | Main Office |  | 0 | Yes | 336 | 7 | 7 | House Fan
110 | 2nd |  | 0 | Yes | 736 | 16 | 16 | House Fan
- | Principal Office |  | 0 | Yes | 210 | 4 | 4 | House Fan
- | Nurses Office |  | 0 | Yes | 264 | 6 | 6 | House Fan
201 | 4th |  | 0 | Yes | 736 | 16 | 16 | House Fan
202 | 4th |  | 0 | Yes | 690 | 15 | 15 | House Fan
203 | 4th |  | 0 | Yes | 736 | 16 | 16 | House Fan
204 | 4th |  | 0 | Yes | 690 | 15 | 15 | House Fan
205 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan
206 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan
207 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan
208 | 3rd |  | 0 | Yes | 736 | 16 | 16 | House Fan
209 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan
210 | 3rd |  | 0 | Yes | 736 | 16 | 16 | House Fan
211 | small group instruction |  | 0 | Yes | 192 | 4 | 4 | House Fan
212 | counselor office |  | 0 | Yes | 108 | 2 | 2 | House Fan
- | Teachers Lounge |  | 0 | Yes | 253 | 5 | 5 | House Fan
301 | 6th |  | 0 | Yes | 736 | 16 | 16 | House Fan
302 | 6th |  | 0 | Yes | 690 | 15 | 15 | House Fan
303 | 6th |  | 0 | Yes | 736 | 16 | 16 | House Fan
304 | 5th |  | 0 | Yes | 690 | 15 | 15 | House Fan
305 | 5th |  | 0 | Yes | 690 | 15 | 15 | House Fan
306 | 6th |  | 0 | Yes | 690 | 15 | 15 | House Fan
307 | 6th |  | 0 | Yes | 690 | 15 | 15 | House Fan
308 | 5th |  | 0 | Yes | 736 | 16 | 16 | House Fan
309 | 5th |  | 0 | Yes | 690 | 15 | 15 | House Fan
310 | 5th |  | 0 | Yes | 736 | 16 | 16 | House Fan
311 | 3rd fl computer room |  | 0 | Yes | 720 | 16 | 16 | House Fan
312 | Small group instruction |  | 0 | Yes | 192 | 4 | 4 | House Fan
314 |  |  |  | Yes | 180 |  |  | House Fan
- | Speech Room |  | 0 | Yes | 180 | 4 | 4 | House Fan
b1 | music room |  | 0 | Yes | 736 | 16 | 16 | House Fan
b2a | Small group instruction |  | 0 | Yes | 352 | 8 | 8 | House Fan
b2 | Small group instruction |  | 0 | Yes | 352 | 8 | 8 | House Fan
b3 | Small group instruction |  | 0 | Yes | 506 | 11 | 11 | House Fan
B4 | Computer Lab |  | 0 | Yes | 968 | 22 | 22 | House Fan
- | Gym/caf |  | 0 | Yes | 3432 | 78 | 78 | N/A
- | Kitchen |  | 0 | Yes | 609 | 13 | 13 | House Fan
- | 2nd Flr Counselor Office |  | 0 | Yes | 195 | 4 | 4 | House Fan
- | 3rd Flr Counselor Office |  | 0 | Yes | 108 | 2 | 2 | House Fan
Edwin Forrest Elementary School- Little School House
P1 | - | 348 | 23 |  | 986 | 22 | 22 | Unit Ventilator
P2 | - | 303 | 20 |  | 986 | 22 | 20 | Unit Ventilator
P3 | - | 362 | 24 |  | 986 | 22 | 22 | Unit Ventilator
P4 | - | 327 | 21 |  | 986 | 22 | 21 | Unit Ventilator
P5 | - | 304 | 20 |  | 986 | 22 | 20 | Unit Ventilator
P6 | - | 390 | 26 |  | 812 | 18 | 18 | Unit Ventilator
P7 | - | 308 | 20 |  | 812 | 18 | 18 | Unit Ventilator
P8 | - | 308 | 20 |  | 812 | 18 | 18 | Unit Ventilator
P9 | - | 382 | 25 |  | 812 | 18 | 18 | Unit Ventilator
P10 | - | 312 | 20 |  | 812 | 18 | 18 | Unit Ventilator
P11 | - | 311 | 20 |  | 812 | 18 | 18 | Unit Ventilator
P12 | - | 316 | 21 |  | 812 | 18 | 18 | Unit Ventilator
P13 | - | 327 | 21 |  | 812 | 18 | 18 | Unit Ventilator
- | Administration and Corridors | 727 | 48 |  | 576 | 13 | 13 | AHU
- | Cafeteria | 78 | 5 | Yes | 2014 | 45 | 45 | AHU
- | Faculty Break Room | 312 | 20 |  | 210 | 4 | 4 | Unit Ventilator

## Fox Chase Farm
Sheet Last Modified: | 2021-04-08
School: | Fox Chase Elementary School
Fox Chase Farm
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Fox Chase Main Building
101 | Classroom | 338 | 22 |  | 840 | 19 | 19 | Unit Ventilator
102 | Classroom | 316 | 21 |  | 1104 | 25 | 21 | Unit Ventilator
103 | Classroom | 291 | 19 |  | 989 | 22 | 19 | Unit Ventilator
104 | Classroom | 302 | 20 |  | 960 | 21 | 20 | Unit Ventilator
105 | Classroom | 312 | 20 |  | 984 | 22 | 20 | Unit Ventilator
105A | Office | 0 | 0 | Yes | 216 | 4 | 4 | Unit Ventilator
107 | Examing Room |  | 0 | Yes | 234 | 5 | 5 | N/A
107A | Office | 0 | 0 | Yes | 225 | 5 | 5 | N/A
108 | Classroom |  | 0 | Yes | 216 | 4 | 4
109 | Classroom | 315 | 21 |  | 1035 | 23 | 21 | Unit Ventilator
110 | Classroom | 300 | 20 |  | 1032 | 23 | 20 | Unit Ventilator
111 | Classroom | 155 | 10 | Yes | 1012 | 23 | 23 | Unit Ventilator
112 | Classroom | 161 | 10 | Yes | 1081 | 24 | 24 | Unit Ventilator
201 | Classroom | 341 | 22 |  | 943 | 21 | 21 | Unit Ventilator
202 | Classroom | 382 | 25 |  | 897 | 20 | 20 | Unit Ventilator
203 | Classroom | 382 | 25 |  | 897 | 20 | 20 | Unit Ventilator
204 | Classroom | 237 | 15 |  | 462 | 10 | 10 | Unit Ventilator
205 | Classroom | 192 | 12 | Yes | 936 | 21 | 21 | Unit Ventilator
206 | Classroom | 391 | 26 |  | 912 | 20 | 20 | Unit Ventilator
207 | Classroom | 0 | 0 | Yes | 943 | 21 | 21 | Unit Ventilator
208 | Classroom | 71 | 4 | Yes | 960 | 21 | 21 | Unit Ventilator
3340 | Ag Room |  | 0 | Yes | 1283 | 29 | 29 | Unit Ventilator
- | 1st Floor Teacher's Lounge | 0 | 0 |  | 336 | 7 | 0 | N/A
A-1 | Classroom | 281 | 18 |  | 836 | 19 | 18 | Unit Ventilator
A-2 | Classroom | 283 | 18 |  | 836 | 19 | 18 | Unit Ventilator
A-3 | Classroom | 319 | 21 |  | 836 | 19 | 19 | Unit Ventilator
A-4 | Classroom | 252 | 16 |  | 836 | 19 | 16 | Unit Ventilator
A-5 | Classroom | 241 | 16 |  | 836 | 19 | 16 | Unit Ventilator
A-6 | Classroom | 295 | 19 |  | 836 | 19 | 19 | Unit Ventilator
C-1 | Classroom |  | 0 | Yes | 1560 | 35 | 35 | N/A
C-4 | Classroom |  | 0 | Yes | 380 | 8 | 8 | N/A
- | Annex | 0 | 0 |  | 1283 | 29 | 0 | Unit Ventilator
- | Auditorium | 0 | 0 |  | 4420 | 100 | 0 | AHU
Instrument Room | Stage Area |  | 0 | Yes | 228 | 5 | 5
- | Cafeteria | 704 | 46 |  | 2340 | 53 | 46 | Unit Ventilator
- | Counselor | 0 | 0 |  | 230 | 5 | 0 | N/A
- | Dental Office | 0 | 0 | Yes | 208 | 4 | 4 | N/A
- | Examining Room | 0 | 0 |  | 234 | 5 | 0 | N/A
- | Gym | 0 | 0 |  | 5429 | 123 | 0 | AHU
- | Kitchen Storage | 296 | 19 |  | 260 | 5 | 5 | Unit Ventilator
- | Main Office | 0 | 0 | Yes | 226 | 5 | 5 | N/A
- | Music Room | 581 | 38 |  | 1400 | 31 | 31 | Unit Ventilator
- | Nurse | 0 | 0 | Yes | 234 | 5 | 5 | N/A
- | Principal | 0 | 0 | Yes | 234 | 5 | 5 | N/A
Fox Chase Farm
- | Data Closet | 14 | 0 |  | 30 | 0 | 0 | AC
- | Kitchen | 190 | 12 |  | 156 | 3 | 3 | AC
- | Men's Bathroom | 56 | 3 |  | 225 | 5 | 3 | AC
- | Teaching Area Classroom | 658 | 43 |  | 1692 | 38 | 38 | AC
- | Women's Bathroom | 55 | 3 |  | 225 | 5 | 3 | AC

## Frank
Sheet Last Modified: | 2021-04-23
School: | Anne Frank Elementary School
Vendor: | Devine Brothers |  | Devine Retest
School: | Anne Frank Elementary School- Little School House
Vendor: | Devine Brothers |  | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Frank Main Building
100 | Classroom | 283 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator
101 | Classroom | 284 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator
102 | Classroom | 236 | 15 | Yes | 864 | 19 | 19 | Unit Ventilator
103 | Classroom | 260 | 17 | Yes | 864 | 19 | 19 | Unit Ventilator
104 | Classroom | 56 | 3 | Yes | 864 | 19 | 19 | Unit Ventilator
106 | Classroom | 0 | 0 |  | 240 | 5 | 0 | Unit Ventilator | UV does not work.
108 | Classroom | 191 | 12 | Yes | 456 | 10 | 10 | Unit Ventilator | Unit low on OA
109 | Classroom | 0 | 0 | Yes | 456 | 10 | 10 | Unit Ventilator | Unit not running
110 | Classroom | 305 | 20 | Yes | 1032 | 23 | 23 | Unit Ventilator
125 | Classroom | 348 | 23 |  | 672 | 15 | 15 | Unit Ventilator
- | Admin Office | 0 | 0 |  | 135 | 3 | 0 | Unit Ventilator | Unit not running
200 | Classroom | 283 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator
201 | Library | 60 | 4 | Yes | 875 | 19 | 19 | Unit Ventilator | Fan going backwards
202 | Classroom | 293 | 19 |  | 864 | 19 | 19 | Unit Ventilator
203 | Classroom | 304 | 20 |  | 864 | 19 | 19 | Unit Ventilator
204 | Classroom | 322 | 21 |  | 864 | 19 | 19 | Unit Ventilator
205 | Classroom | 215 | 14 | Yes | 864 | 19 | 19 | Unit Ventilator
206 | Classroom | 205 | 13 |  | 240 | 5 | 5 | Unit Ventilator
207 | Classroom | 257 | 17 | Yes | 864 | 19 | 19 | Unit Ventilator
208 | Classroom | 299 | 19 |  | 864 | 19 | 19 | Unit Ventilator
209 | Classroom | 203 | 13 | Yes | 864 | 19 | 19 | Unit Ventilator
210 | Classroom | 225 | 15 | Yes | 864 | 19 | 19 | Unit Ventilator
211 | Classroom | 333 | 22 |  | 864 | 19 | 19 | Unit Ventilator
212 | Classroom | 153 | 10 | Yes | 864 | 19 | 19 | Unit Ventilator
213 | Classroom | 226 | 15 | Yes | 864 | 19 | 19 | Unit Ventilator
214 | Classroom |  | 0 | Yes | 864 | 19 | 19
215 | Classroom | 284 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator
- | Library | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
300 | Classroom | 241 | 16 | Yes | 864 | 19 | 19 | Unit Ventilator
301 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
302 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
303 | Classroom | 185 | 12 | Yes | 864 | 19 | 19 | Unit Ventilator
304 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
305 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
306 | Classroom | 0 | 0 | Yes | 240 | 5 | 5 | Unit Ventilator | Unit not running
307 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
308 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
309 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
310 | Classroom | 127 | 8 | Yes | 864 | 19 | 19 | Unit Ventilator
311 | Classroom | 42 | 2 | Yes | 864 | 19 | 19 | Unit Ventilator
312 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
313 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
315 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | Unit not running
| Auditorium | 0 | 0 |  | 3180 | 72 | 0
| Cafeteria | 0 | 0 | Yes | 2720 | 61 | 61 |  | Hyrdroxyl
| Gymnasium | 0 | 0 | Yes | 3657 | 83 | 83 |  | Hydroxyl
| Gymnasium Office |  | 0 |  | 165 | 3 | 0
- | Counselor Office | 0 | 0 | Yes | 132 | 3 | 3 | NA
- | Main Office | 60 | 4 | Yes | 951 | 21 | 21 | Unit Ventilator | Fan going backwards
- | Nurses Office | 0 | 0 | Yes | 304 | 6 | 6 | NA
- | Principals Office | 0 | 0 | Yes | 210 | 4 | 4 | NA
- | Vice Principals Office | 0 | 0 | Yes | 72 | 1 | 1 | NA
Frank LSH
1 | Classroom | 931 | 62 |  | 928 | 21 | 21 | BCU | 90% OA damper 70% RA Damper. OA & RA dampers need to be realigned
2 | Classroom | 595 | 39 |  | 928 | 21 | 21 | BCU | 95% OA damper 70% RA Damper. OA & RA dampers need to be realigned
3 | Classroom | 945 | 63 |  | 928 | 21 | 21 | BCU | 90% OA damper 70% RA Damper. OA & RA dampers need to be realigned
4 | Classroom | 610 | 40 |  | 928 | 21 | 21 | BCU | 95% OA damper 70% RA Damper. OA & RA dampers need to be realigned
5 | Classroom | 322 | 21 |  | 928 | 21 | 21 | BCU | Damper at 35%
6 | Classroom | 307 | 20 | Yes | 928 | 21 | 21 | BCU
7 | Classroom | 310 | 20 | Yes | 928 | 21 | 21 | BCU
8 | Classroom | 305 | 20 | Yes | 928 | 21 | 21 | BCU
9 | Classroom | 370 | 24 |  | 928 | 21 | 21 | BCU | Damper at 35%
10 | Classroom | 329 | 21 |  | 928 | 21 | 21 | BCU | Damper at 35%
11 | Classroom | 396 | 26 |  | 928 | 21 | 21 | BCU
12 | Classroom | 319 | 21 |  | 928 | 21 | 21 | BCU
- | Bathrooms, Corridor and Main Entrance | 284 | 18 |  | 225 | 5 | 5 | FCU | OA damper 5%
- | Corner Facilities/Guidance Office | 0 | 0 |  | 196 | 4 | 0 | FCU | Not running
- | Counselor Office | 0 | 0 | Yes | 100 | 2 | 2 | FCU | Unit not running.
- | Janitor Close and Storage Rooms | 262 | 17 |  | 24 | 0 | 0 | FCU | OA damper 10%
- | Main Office | 587 | 39 |  | 315 | 7 | 7 | FCU | OA damper 0%. BC filter cover plate & filter not installed. Air from boiler room space entering unit. BC coil is very dirty and needs to be cleaned.
- | Cafeteria | 922 | 61 |  | 1696 | 38 | 38 | BCU | Damper at 30%
- | Art Teacher Office | 102 | 6 |  | 100 | 2 | 2 | BCU
- | ESL Teacher Office | 110 | 7 |  | 100 | 2 | 2 | BCU
- | ESL Room | 241 | 16 |  | 80 | 1 | 1 | BCU | Damper at 50%
Frank Annex
7 | Classroom | 36 | 2 | Yes | 1080 | 24 | 24 | Unit Ventilator | Unit needs repairs.
8 | Classroom | 235 | 15 | Yes | 1080 | 24 | 24 | Unit Ventilator
- | gang girlsnboys |  | 0 |  | 480 | 10 | 0 | N/A

## Frankford
Sheet Last Modified: | 2021-03-17
School: | Frankford High School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
9 | Classroom | 122 | 8 |  | 1836 | 41 | 8 | Unit Ventilator
11 | Classroom | 0 | 0 |  | 2011 | 45 | 0 | Unit Ventilator
12 | Classroom | 0 | 0 |  | 2011 | 45 | 0 | Unit Ventilator
14 | Classroom | 167 | 11 |  | 812 | 18 | 11 | Unit Ventilator
15-14 | Classroom | 0 | 0 |  | N/A | 0 | 0 | Unit Ventilator
15A | Classroom | 107 | 7 |  | 812 | 18 | 7 | Unit Ventilator
16 | Classroom | 0 | 0 |  | 476 | 10 | 0 | Unit Ventilator
17 | Classroom | 0 | 0 |  | 952 | 21 | 0 | Unit Ventilator
18 | Classroom | 76 | 5 |  | 884 | 20 | 5 | Unit Ventilator
19 | Classroom | 55 | 3 |  | 576 | 13 | 3 | Unit Ventilator
20 | Classroom | 0 | 0 |  | 1023 | 23 | 0 | Unit Ventilator
124 | Classroom | 210 | 14 |  | 1702 | 38 | 14 | Unit Ventilator
222 | Classroom | 80 | 5 |  | 889 | 20 | 5 | Unit Ventilator
223 | Classroom | 163 | 10 |  | 991 | 22 | 10 | Unit Ventilator
224 | Classroom | 80 | 5 |  | 991 | 22 | 5 | Unit Ventilator
225 | Classroom | 50 | 3 |  | 1005 | 22 | 3 | Unit Ventilator
226 | Classroom | 149 | 9 |  | 991 | 22 | 9 | Unit Ventilator
227 | Classroom | 128 | 8 |  | 864 | 19 | 8 | Unit Ventilator
228 | Classroom | 255 | 17 |  | 899 | 20 | 17 | Unit Ventilator
229 | Classroom | 0 | 0 |  | 462 | 10 | 0 | Unit Ventilator
230 | Classroom | 181 | 12 |  | 1001 | 22 | 12 | Unit Ventilator
231A | Classroom | 286 | 19 |  | 986 | 22 | 19 | Unit Ventilator
232A | Classroom | 80 | 5 |  | 1048 | 23 | 5 | Unit Ventilator
233 | Classroom | 40 | 2 |  | 1120 | 25 | 2 | Unit Ventilator
326 | Classroom | 91 | 6 |  | 775 | 17 | 6 | Unit Ventilator
327 | Classroom | 48 | 3 |  | 775 | 17 | 3 | Unit Ventilator
330-331 | Classroom | 166 | 11 |  | 969 | 22 | 11 | Unit Ventilator
332 | Classroom | 84 | 5 |  | 1505 | 34 | 5 | Unit Ventilator
333 | Classroom | 0 | 0 |  | 1505 | 34 | 0 | Unit Ventilator
335 | Classroom | 0 | 0 |  | 1120 | 25 | 0 | Unit Ventilator
- | IMC | 264 | 17 |  | 5398 | 122 | 17 | Unit Ventilator

## Franklin ES
Sheet Last Modified: | 2021-04-21
School: | Benjamin Franklin Elementary School
Vendor: | Devine | Devine 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Basement Boy's Restroom | 0 | 0 |  | 234 | 5 | 0 | AHU
- | Basement Girl's Restroom | 0 | 0 |  | 234 | 5 | 0 | AHU
- | 1st Floor Boy's Restroom | 27 | 1 |  | 234 | 5 | 1 | AHU
- | 1st Floor Girl's Restroom | 40 | 2 |  | 234 | 5 | 2 | AHU
- | 2nd Floor Girl's Restroom | 28 | 1 |  | 234 | 5 | 1 | AHU
- | 2nd Floor Boy's Restroom | 40 | 2 |  | 234 | 5 | 2 | AHU
1 | Classroom |  | 0 | Yes | 304 | 6 | 6 | Unit Ventilator
1B | Classroom |  | 0 | Yes | 667 | 15
6 | Classroom | 350 | 23 |  | 780 | 17 | 17 | Unit Ventilator
7 | Cafeteria | 1972 | 131 |  | 2800 | 63 | 63 | AHU
8 | Classroom | 299 | 19 |  | 780 | 17 | 17 | Unit Ventilator
- | Kitchen | 1585 | 105 |  | 1023 | 23 | 23 | AHU
- | Kitchen Office | 225 | 15 |  | 80 | 1 | 1 | AHU
101 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
102 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
103 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
104 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan
105 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan
106 | Classroom |  | 0 | Yes | 650 | 14 | 14
107 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan
110 | Classroom | 352 | 23 |  | 780 | 17 | 17 | House Fan
111 | Classroom | 321 | 21 |  | 780 | 17 | 17 | Unit Ventilator
112 | Classroom | 300 | 20 |  | 780 | 17 | 17 | Unit Ventilator
113 | Classroom | 312 | 20 |  | 780 | 17 | 17 | Unit Ventilator
114 | Classroom | 410 | 27 |  | 780 | 17 | 17 | Unit Ventilator
115 | Classroom | 346 | 23 |  | 780 | 17 | 17 | Unit Ventilator
116 | Asst Principals Office | 352 | 23 |  | 207 | 4 | 4 | Unit Ventilator
117 | Classroom | 332 | 22 |  | 609 | 13 | 13 | Unit Ventilator
201 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
202 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
203 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
204 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan
205 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan
206 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan
207 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan
208 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
209 | Library | 568 | 37 | Yes | 1600 | 36 | 36 | Unit Ventilator
210 | Trs Lounge | 330 | 22 |  | 380 | 8 | 8 | Unit Ventilator
212 | TECH LAB | 487 | 32 |  | 1600 | 36 | 32 | Unit Ventilator
214 | Classroom | 305 | 20 |  | 780 | 17 | 17 | Unit Ventilator
215 | Classroom | 325 | 21 |  | 780 | 17 | 17 | Unit Ventilator
216 | Classroom | 325 | 21 |  | 780 | 17 | 17 | Unit Ventilator
217 | Classroom | 287 | 19 |  | 780 | 17 | 17 | Unit Ventilator
218 | Classroom | 323 | 21 |  | 780 | 17 | 17 | Unit Ventilator
219 | Classroom | 291 | 19 |  | 780 | 17 | 17 | Unit Ventilator
220 | Counselor's Office | 287 | 19 |  | 207 | 4 | 4 | Unit Ventilator
221 | Classroom | 314 | 20 |  | 605 | 13 | 13 | Unit Ventilator
- | Faculty Lounge | 0 | 0 |  | 160 | 3 | 0 | Unit Ventilator
- | Nurses Office |  | 0 | Yes | 132 | 3 | 3
- | Psychology Office | 33 | 2 |  | 90 | 2 | 2 | Unit Ventilator
- | Main Office |  | 0 | Yes | 220 | 5 | 5

## Franklin HS
Sheet Last Modified: | 2021-04-19
School: | Benjamin Franklin High School
Vendor: | Devine | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Weight room | 63 | 4 |  | 713 | 16 | 4 | HV+ AHU
2 | Weight room | 0 | 0 |  | 775 | 17 | 0 | HV
3 | Weight room | 0 | 0 |  | 1632 | 37 | 0 | HV
4 | Welding | 9254 | 616 |  | 2176 | 49 | 49 | MUA
4A | Classroom | 280 | 18 |  | 640 | 14 | 14 | AC
6 | Classroom | 0 | 0 | Yes | 2655 | 60 | 60 | AHU
7 | Classroom | 0 | 0 |  | 216 | 4 | 0 | AHU
8 | Classroom | 0 | 0 |  | 588 | 13 | 0 | AHU
9 | Classroom | 0 | 0 |  | 621 | 14 | 0 | AHU
10 | Machine Shop | 810 | 54 |  | 2961 | 67 | 54 | HV
11 | Classroom | 176 | 11 |  | 1740 | 39 | 11 | AC
12 | Classroom | 842 | 56 |  | 1581 | 35 | 35 | HV
13 | Classroom | 175 | 11 |  | 1239 | 28 | 11 | AC
13A | Classroom | 93 | 6 |  | 552 | 12 | 6 | AC
14 | Classroom | 136 | 9 |  | 756 | 17 | 9 | AC
15 | Classroom | 155 | 10 |  | 912 | 20 | 10 | AC
15A | Practice Room | 77 | 5 |  | 77 | 1 | 1 | HV
15B | Practice Room | 188 | 12 |  | 77 | 1 | 1 | HV
15C | Practice Room | 143 | 9 |  | 77 | 1 | 1 | HV
15D | Music Office | 142 | 9 |  | 180 | 4 | 4 | HV
16 | Lecture Hall | 2049 | 136 |  | 2068 | 47 | 47 | HV
17 | Lecture Hall | 387 | 25 |  | 2280 | 51 | 25 | HV
18 | Classroom | 803 | 53 |  | 1080 | 24 | 24 | AC
19 | Classroom | 781 | 52 |  | 1344 | 30 | 30 | AC
20 | Classroom | 635 | 42 |  | 828 | 18 | 18 | AC
100 | Classroom | 280 | 18 |  | 775 | 17 | 17 | UV
102 | Classroom | 382 | 25 |  | 961 | 21 | 21 | UV
110 | Room | 0 | 0 |  | 195 | 4 | 0 | FC
111A | Room | 0 | 0 |  | 104 | 2 | 0 | FC
113 | Room | 0 | 0 |  | 315 | 7 | 0 | FC
115 | Room | 0 | 0 |  | 352 | 8 | 0 | FC
116 | Room | 0 | 0 |  | 196 | 4 | 0 | FC
150 | Kitchen | 0 | 0 |  | 1955 | 44 | 0 | RTU
152 | Cafeteria | 0 | 0 |  | 3363 | 76 | 0 | RTU
200 | Living Room | 140 | 9 |  | 819 | 18 | 9 | UV
201 | Classroom | 217 | 14 |  | 792 | 18 | 14 | UV
202 | Office-A | 201 | 13 |  | 600 | 13 | 13 | UV
202 | Office-B | 171 | 11 |  | 396 | 9 | 9 | UV
204 | Principal Office | 41 | 2 |  | 180 | 4 | 2 | OAS-1A & OAS-1B
206 | Co-Principal | 40 | 2 |  | 120 | 2 | 2 | OAS-1A & OAS-1B
207 | Classroom | 257 | 17 |  | 792 | 18 | 17 | UV
209 | Storage | 189 | 12 |  | 165 | 3 | 3 | UV
209B | Office | 287 | 19 |  | 180 | 4 | 4 | UV
211 | Classroom | 358 | 23 |  | 713 | 16 | 16 | UV
212 | Work Room | 49 | 3 |  | 297 | 6 | 3 | OAS-1A & OAS-1B
214 | Office | 57 | 3 |  | 121 | 2 | 2 | OAS-1A & OAS-1B
215 | Classroom | 295 | 19 |  | 806 | 18 | 18 | UV
216 | Conference | 44 | 2 |  | 72 | 1 | 1 | OAS-1A & OAS-1B
217 | Learning Lounge | 263 | 17 |  | 572 | 13 | 13 | UV
218 | College Office | 50 | 3 |  | 132 | 3 | 3 | OAS-1A & OAS-1B
220 | College | 49 | 3 |  | 120 | 2 | 2 | OAS-1A & OAS-1B
222 | Health Suite | 45 | 3 |  | 256 | 5 | 3 | OAS-1A & OAS-1B
222A | Nurse Office | 50 | 3 |  | 108 | 2 | 2 | OAS-1A & OAS-1B
222B | Exam | 48 | 3 |  | 99 | 2 | 2 | OAS-1A & OAS-1B
223A | Dining | 856 | 57 |  | 1760 | 40 | 40 | UV
229 | Classroom |  | 0 | Yes | 589 | 13 | 13
231 | Office | 150 | 10 |  | 210 | 4 | 4 | UV
232 | Health Suite | 221 | 14 |  | 464 | 10 | 10 | OAS-1A & OAS-1B
232B | Storage | 0 | 0 |  | 45 | 1 | 0 | OAS-1A & OAS-1B
232C | Nurse Health | 0 | 0 |  | 99 | 2 | 0 | AC
232D | Nurse Health | 0 | 0 |  | 106 | 2 | 0 | AC
238 | Conference | 119 | 7 |  | 228 | 5 | 5 | OAS-1A & OAS-1B
240 | Office | 131 | 8 |  | 143 | 3 | 3 | OAS-1A & OAS-1B
242 | Storage | 146 | 9 |  | 71 | 1 | 1 | OAS-1A & OAS-1B
244 | Office | 124 | 8 |  | 143 | 3 | 3 | OAS-1A & OAS-1B
246 | Open Work Area | 119 | 7 |  | 252 | 5 | 5 | OAS-1A & OAS-1B
248 | Office | 135 | 9 |  | 143 | 3 | 3 | OAS-1A & OAS-1B
250 | Main Office | 408 | 27 |  | 675 | 15 | 15 | UV
300 | Collaboration | 25 | 1 |  | 264 | 6 | 1 | OAS-1A & OAS-1B
301 | Classroom | 192 | 12 |  | 792 | 18 | 12 | UV
302 | Classroom | 233 | 15 |  | 900 | 20 | 15 | UV
304 | Classroom | 255 | 17 |  | 851 | 19 | 17 | UV
306 | Classroom | 218 | 14 |  | 897 | 20 | 14 | UV
308 | Classroom | 206 | 13 |  | 759 | 17 | 13 | UV
309 | Classroom | 308 | 20 |  | 736 | 16 | 16 | UV
311 | Classroom | 301 | 20 |  | 576 | 13 | 13 | UV
315 | Classroom | 138 | 9 |  | 759 | 17 | 9 | UV
316 | Classroom | 482 | 32 |  | 759 | 17 | 17 | UV
317 | Classroom | 182 | 12 | Yes | 1173 | 26 | 26 | UV
318 | Classroom | 146 | 9 | Yes | 713 | 16 | 16 | UV
319 | Classroom | 209 | 13 |  | 736 | 16 | 13 | UV
320 | Classroom | 165 | 11 |  | 736 | 16 | 11 | UV
321A | Office | 96 | 6 |  | 154 | 3 | 3 | UV
321B | Storage | 289 | 19 |  | 154 | 3 | 3 | UV
322 | Classroom | 154 | 10 | Yes | 736 | 16 | 16 | UV
324 | Classroom | 0 | 0 |  | 558 | 12 | 0 | UV
326 | Classroom | 225 | 15 |  | 900 | 20 | 15 | UV
327 | Office | 236 | 15 |  | 240 | 5 | 5 | UV
328 | LSS Community Rm | 43 | 2 |  | 288 | 6 | 2 | OAS-1A & OAS-1B
329 | Classroom | 224 | 14 |  | 936 | 21 | 14 | UV
400 | Collaboration | 0 | 0 |  | 264 | 6 | 0 | OAS-1A & OAS-1B
401 | Classroom | 0 | 0 |  | 759 | 17 | 0 | UV
402 | Classroom | 264 | 17 |  | 1311 | 29 | 17 | UV
404 | Classroom | 250 | 16 |  | 345 | 7 | 7 | UV
406 | Classroom | 330 | 22 |  | 1311 | 29 | 22 | UV
407 | Classroom | 258 | 17 |  | 736 | 16 | 16 | UV
409 | Classroom | 97 | 6 |  | 736 | 16 | 6 | UV
411 | Classroom | 648 | 43 |  | 552 | 12 | 12 | UV
415 | Classroom | 178 | 11 |  | 759 | 17 | 11 | UV
416 | Classroom | 155 | 10 |  | 851 | 19 | 10 | UV
417 | Classroom | 3 | 0 |  | 713 | 16 | 0 | UV
418 | Classroom | 182 | 12 |  | 851 | 19 | 12 | UV
419 | Classroom | 219 | 14 |  | 736 | 16 | 14 | UV
420 | Classroom | 162 | 10 |  | 828 | 18 | 10 | UV
421 | Office | 86 | 5 |  | 529 | 12 | 5 | UV
422 | Classroom | 132 | 8 |  | 828 | 18 | 8 | UV
424 | Office | 158 | 10 |  | 99 | 2 | 2 | UV
426 | Classroom | 73 | 4 |  | 900 | 20 | 4 | UV
427 | Classroom | 339 | 22 |  | 1200 | 27 | 22 | UV
428 | Collaboration | 62 | 4 |  | 444 | 10 | 4 | OAS-1A & OAS-1B
500 | Collaboration | 22 | 1 |  | 322 | 7 | 1 | OAS-1A & OAS-1B
501 | Classroom | 201 | 13 |  | 825 | 18 | 13 | UV
502 | Classroom | 681 | 45 |  | 1380 | 31 | 31 | UV
504 | Storage | 216 | 14 |  | 352 | 8 | 8 | UV
506 | Classroom | 477 | 31 |  | 1357 | 30 | 30 | UV
507 | Classroom | 155 | 10 |  | 851 | 19 | 10 | UV
509 | Classroom | 194 | 12 |  | 805 | 18 | 12 | UV
515 | Classroom | 269 | 17 |  | 920 | 20 | 17 | UV
516 | Classroom | 162 | 10 |  | 1012 | 23 | 10 | UV
517 | Classroom | 647 | 43 |  | 943 | 21 | 21 | UV
518 | Classroom | 73 | 4 |  | 851 | 19 | 4 | UV
519 | Classroom | 201 | 13 |  | 693 | 15 | 13 | UV
520 | Classroom | 515 | 34 |  | 858 | 19 | 19 | UV
522A | Office | 21 | 1 |  | 100 | 2 | 1 | OAS-1A & OAS-1B
523 | Classroom | 950 | 63 |  | 1344 | 30 | 30 | UV
524 | Staff Lounge | 527 | 35 |  | 375 | 8 | 8 | UV
526 | Classroom | 1235 | 82 |  | 1175 | 26 | 26 | UV
601 | Classroom | 231 | 15 |  | 936 | 21 | 15 | UV
602 | Classroom | 325 | 21 |  | 920 | 20 | 20 | UV
603 | Production Studio | 25 | 1 |  | 160 | 3 | 1 | OAS-1A & OAS-1B
603A | Control Rm | 25 | 1 |  | 96 | 2 | 1 | OAS-1A & OAS-1B
604 | Classroom | 568 | 37 |  | 460 | 10 | 10 | UV
605 | Classroom | 609 | 40 |  | 1152 | 26 | 26 | UV
606 | Classroom | 140 | 9 |  | 621 | 14 | 9 | UV
609 | Classroom | 614 | 40 |  | 900 | 20 | 20 | UV
611 | Classroom | 256 | 17 |  | 900 | 20 | 17 | UV
612 | Classroom | 208 | 13 |  | 714 | 16 | 13 | UV
613 | Classroom | 564 | 37 |  | 792 | 18 | 18 | UV
614 | Classroom | 290 | 19 |  | 756 | 17 | 17 | UV
615 | Storage | 261 | 17 |  | 336 | 7 | 7 | UV
616 | Classroom | 265 | 17 |  | 900 | 20 | 17 | UV
617 | Office | 92 | 6 |  | 300 | 6 | 6 | UV
620 | Classroom | 750 | 50 |  | 900 | 20 | 20 | UV
620 | Classroom | 567 | 37 |  | 2304 | 52 | 37 | UV
- | Auditorium | 1102 | 73 |  | 8648 | 196 | 73 | AHU
- | Faculty/Office | 0 | 0 |  | 330 | 7 | 0 | AC
- | Practice Room 1 | 0 | 0 |  | 77 | 1 | 0 | HV
- | Practice Room 2 | 0 | 0 |  | 77 | 1 | 0 | HV
- | Practice Room 3 | 0 | 0 |  | 77 | 1 | 0 | HV
- | Kitchen Office | 15 | 1 |  | 99 | 2 | 1 | RTU
- | Weight Room | 163 | 10 |  | 1632 | 37 | 10 | AHU

## Franklin Learning Center
Sheet Last Modified: | 2021-04-27
School: | Franklin Learning Center
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 318 | 21 |  | 840 | 19 | 19
101/102 | Classroom | 144 | 9 |  | 1426 | 32 | 9
103 / 104 | Conference | 811 | 54 |  | 1612 | 36 | 36
105 | Classroom | 186 | 12 |  | 690 | 15 | 12
108 | ESOL |  | 0 |  | 242 | 5 | 0
111 | Classroom | 44 | 2 |  | 221 | 5 | 2
120 | Classroom | 528 | 35 |  | 625 | 14 | 14
121 | Classroom | 486 | 32 |  | 806 | 18 | 18
122 | Classroom | 640 | 42 |  | 744 | 16 | 16
123 | Classroom | 705 | 47 |  | 660 | 15 | 15
124 | Classroom | 504 | 33 |  | 266 | 6 | 6
125 | Classroom | 615 | 41 |  | 575 | 13 | 13
126 | Classroom | 615 | 41 |  | 275 | 6 | 6
129 | Classroom | 238 | 15 |  | 675 | 15 | 15
132 | Classroom | 264 | 17 |  | 414 | 9 | 9
132a | Classroom | 391 | 26 |  | 690 | 15 | 15
133 | Classroom | 730 | 48 |  | 759 | 17 | 17
200 | Classroom | 447 | 29 |  | 950 | 21 | 21
201 | Classroom | 372 | 24 |  | 713 | 16 | 16
202 | Classroom | 349 | 23 |  | 690 | 15 | 15
203 / 204 | Classroom | 655 | 43 |  | 1426 | 32 | 32
205 | Classroom | 294 | 19 |  | 713 | 16 | 16
206 | Classroom | 0 | 0 |  | 198 | 4 | 0
207 | Classroom | 37 | 2 |  | 925 | 21 | 2
208 | Classroom | 314 | 20 |  | 782 | 17 | 17
209 | Classroom | 638 | 42 |  | 875 | 19 | 19
210 | Classroom | 661 | 44 |  | 782 | 17 | 17
212 | Classroom | 621 | 41 |  | 851 | 19 | 19
213 | Classroom | 0 | 0 |  | 165 | 3 | 0
214 | Classroom | 580 | 38 |  | 625 | 14 | 14
215 | Classroom | 446 | 29 |  | 720 | 16 | 16
216 | Classroom | 486 | 32 |  | 960 | 21 | 21
217 | Classroom | 410 | 27 |  | 960 | 21 | 21
218 | Classroom | 377 | 25 |  | 600 | 13 | 13
220 | Classroom | 174 | 11 |  | 980 | 22 | 11
221 | IMC/ Library | 433 | 28 |  | 1536 | 34 | 28
221 | Office | 210 | 14 |  | 154 | 3 | 3
300 | Classroom | 88 | 5 |  | 900 | 20 | 5
301 | Classroom | 215 | 14 |  | 506 | 11 | 11
302 | Classroom | 403 | 26 |  | 975 | 22 | 22
303 | Classroom | 368 | 24 |  | 936 | 21 | 21
304 | Classroom | 287 | 19 |  | 575 | 13 | 13
305 | Classroom | 392 | 26 |  | 713 | 16 | 16
306 | Classroom | 168 | 11 |  | 297 | 6 | 6
307 | Classroom | 729 | 48 |  | 700 | 15 | 15
309 | Classroom | 443 | 29 |  | 480 | 10 | 10
310 | Medical Classroom | 1312 | 87 |  | 1403 | 31 | 31
310 | Doctor's Office | 3 | 0 |  | 77 | 1 | 0
310 | Bathroom | 12 | 0 |  | 120 | 2 | 0
310 | Storage | 11 | 0 |  | 140 | 3 | 0
312 | Classroom | 538 | 35 |  | 575 | 13 | 13
312 | Councelor | 0 | 0 |  | 950 | 21 | 0
315 | Classroom | 255 | 17 |  | 675 | 15 | 15
316 | Classroom | 353 | 23 |  | 644 | 14 | 14
317 | Classroom | 465 | 31 |  | 950 | 21 | 21
318 | Classroom | 465 | 31 |  | 897 | 20 | 20
318 | Prep Room / Chemistry |  | 0 |  | 156 | 3 | 0
318 | Secure Closet |  | 0 |  |  | 0 | 0
319 | Classroom | 263 | 17 |  | 575 | 13 | 13
321 | Classroom | 506 | 33 |  | 588 | 13 | 13
322 | Computer | 0 | 0 |  | 299 | 6 | 0
323 | Classroom | 374 | 24 |  | 598 | 13 | 13
324 | Classroom | 104 | 6 |  | 552 | 12 | 6
325 | Classroom | 118 | 7 |  | 594 | 13 | 7
- | Cafeteria | 1320 | 88 |  | 2808 | 63 | 63
- | Gym |  | 0 |  | 3649 | 82 | 0
- | Office | 58 | 3 |  | 230 | 5 | 3
- | Office | 223 | 14 |  | 567 | 12 | 12

## Furness
Sheet Last Modified: | 2021-04-29
School: | Horace H. Furness High School
Vendor: | Chadwick | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom |  | 0 |  | 1224 | 27 | 0
3 | Classroom |  | 0 |  | 672 | 15 | 0
4 | Classroom |  | 0 |  | 840 | 19 | 0
5 | Classroom |  | 0 |  | 840 | 19 | 0
101 | Classroom | 306 | 20 |  | 667 | 15 | 15
102 | Classroom |  | 0 |  | 768 | 17 | 0
103 | classroom | 297 | 19 |  | 667 | 15 | 15
104 | Classroom |  | 0 |  | 896 | 20 | 0
105 | classroom |  | 0 |  | 667 | 15 | 0
106 | classroom | 326 | 21 |  | 667 | 15 | 15
107 | Library | 1463 | 97 |  | 2448 | 55 | 55
112 | Classroom |  | 0 |  | 448 | 10 | 0
201 | classroom | 272 | 18 |  | 735 | 16 | 16
201A | Room |  | 0 |  | 448 | 10 | 0
202 | Classroom |  | 0 |  | 1536 | 34 | 0
203 | classroom | 540 | 36 |  | 874 | 19 | 19
204 | classroom | 443 | 29 |  | 814 | 18 | 18
205 | classroom | 392 | 26 |  | 667 | 15 | 15
206 | classroom |  | 0 |  | 667 | 15 | 0
207 | classroom |  | 0 |  | 720 | 16 | 0
208 | classroom | 328 | 21 |  | 660 | 15 | 15
209 | classroom |  | 0 |  | 725 | 16 | 0
210 | classroom |  | 0 |  | 696 | 15 | 0
211 | classroom | 319 | 21 |  | 696 | 15 | 15
212 | classroom | 359 | 23 |  | 696 | 15 | 15
213 | classroom | 316 | 21 |  | 696 | 15 | 15
214 | classroom |  | 0 |  | 696 | 15 | 0
215 | Classroom |  | 0 |  | 576 | 13 | 0
218 | classroom | 367 | 24 |  | 720 | 16 | 16
219A | classroom |  | 0 |  | 783 | 17 | 0
219B | classroom | 275 | 18 |  | 1100 | 25 | 18
220 | classroom | 292 | 19 |  | 690 | 15 | 15
221 | classroom | 490 | 32 |  | 770 | 17 | 17
221A | classroom | 380 | 25 |  | 770 | 17 | 17
222 | classroom |  | 0 |  | 161 | 3 | 0
222A | Room |  | 0 |  | 560 | 12 | 0
301A | classroom 301 | 360 | 24 |  | 690 | 15 | 15
301B | classroom 301 | 345 | 23 |  | 672 | 15 | 15
302A | classroom 302 | 272 | 18 |  | 1056 | 24 | 18
302B | classroom 302 | 356 | 23 |  | 624 | 14 | 14
303 | classroom | 438 | 29 |  | 770 | 17 | 17
304 | classroom |  | 0 |  | 690 | 15 | 0
305 | classroom |  | 0 |  | 672 | 15 | 0
306 | classroom |  | 0 |  | 720 | 16 | 0
307 | classroom |  | 0 |  | 720 | 16 | 0
308 | classroom | 246 | 16 |  | 720 | 16 | 16
309 | classroom |  | 0 |  | 720 | 16 | 0
310A | classroom |  | 0 |  | 1008 | 22 | 0
310b | classroom |  | 0 |  | 1344 | 30 | 0
311A | classroom | 201 | 13 |  | 1008 | 22 | 13
311B | classroom |  | 0 |  | 1148 | 26 | 0
312A | classroom |  | 0 |  | 960 | 21 | 0
312B | classroom |  | 0 |  | 400 | 9 | 0
313A | classroom | 175 | 11 |  | 1008 | 22 | 11
313B | classroom |  | 0 |  | 480 | 10 | 0
314 | Classroom |  | 0 |  | 448 | 10 | 0
315 | Classroom |  | 0 |  | 392 | 8 | 0
316 | classroom | 73 | 4 |  | 696 | 15 | 4
317A | classroom |  | 0 |  | 1137 | 25 | 0
317B | classroom | 117 | 7 |  | 1008 | 22 | 7
318A | classroom |  | 0 |  | 1152 | 26 | 0
318B | classroom |  | 0 |  | 720 | 16 | 0
319A | classroom | 392 | 26 |  | 1056 | 24 | 24
319B | classroom | 215 | 14 |  | 320 | 7 | 7
320A | classroom |  | 0 |  | 920 | 20 | 0
320B | classroom |  | 0 |  | 1056 | 24 | 0
321A | classroom |  | 0 |  | 1056 | 24 | 0
321B | classroom | 302 | 20 |  | 1056 | 24 | 20
- | Cafeteria | 153 | 10 |  | 3665 | 83 | 10
Main Office | Office |  | 0 |  | 1248 | 28 | 0
Assistant Principal | Office |  | 0 |  | 360 | 8 | 0
Burke | Office |  | 0 |  | 728 | 16 | 0
SSO | Office |  | 0 |  | 240 | 5 | 0
Nurse | Suite |  | 0 |  | 960 | 21 | 0

## GAMP
Sheet Last Modified: | 2021-04-23
School: | Girard Academic Music Program (GAMP) High School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | CAFE | 9130 | 608 |  | 977 | 22 | 22
- | GYM |  | 0 |  | 6667 | 151 | 0
- | GYM OFFICE |  | 0 |  | 99 | 2 | 0
- | LOWER HALF OF AUDITORIUM | 13845 | 923 |  | 6498 | 147 | 147
- | UPPER HALF OF AUDITORIUM | 14721 | 981 |  | 3247 | 73 | 73
Principal | Office | 0 | 0 | Yes | 363 | 8 | 8
Assistant Principal | Office | 0 | 0 |  | 169 | 3 | 0
Main Office | Office | 0 | 0 | Yes | 266 | 6 | 6
Counselor 1 | Office | 0 | 0 | Yes | 134 | 3 | 3
Counselor 2 | Office | 0 | 0 | Yes | 246 | 5 | 5
Nurse | Office | 0 | 0 | Yes | 88 | 2 | 2
Lunch Room | Lunch Room | 0 | 0 |  | 2580 | 58 | 0
Orchestra Room | Orchestra Room | 0 | 0 | Yes | 1082 | 24 | 24
Orchestra Room | Office |  | 0 |  | 330 | 7
Band Room | Band Room | 0 | 0 | Yes | 1221 | 27 | 27
102 | Classroom | 0 | 0 | Yes | 685 | 15 | 15
103 | Classroom | 0 | 0 | Yes | 722 | 16 | 16
104/105 | Classroom | 0 | 0 | Yes | 1063 | 24 | 24
107 | Classroom | 0 | 0 | Yes | 735 | 16 | 16
108 | Classroom | 0 | 0 | Yes | 695 | 15 | 15
109 | Classroom | 0 | 0 | Yes | 685 | 15 | 15
201 | Classroom | 0 | 0 | Yes | 679 | 15 | 15
202 | Classroom | 0 | 0 | Yes | 679 | 15 | 15
203 | Classroom | 0 | 0 | Yes | 715 | 16 | 16
204 | Classroom | 0 | 0 | Yes | 683 | 15 | 15
205 | Classroom | 0 | 0 | Yes | 680 | 15 | 15
206 | Classroom | 0 | 0 | Yes | 711 | 16 | 16
207 | Classroom | 0 | 0 | Yes | 734 | 16 | 16
208 | Classroom | 0 | 0 | Yes | 634 | 14 | 14
209 | Classroom | 0 | 0 | Yes | 686 | 15 | 15
211 | Classroom | 0 | 0 |  | 394 | 8 | 0
301 | Classroom | 0 | 0 | Yes | 689 | 15 | 15
302 | Classroom | 0 | 0 | Yes | 645 | 14 | 14
303 | Classroom | 0 | 0 | Yes | 669 | 15 | 15
304 | Classroom | 0 | 0 | Yes | 725 | 16 | 16
305 | Classroom | 0 | 0 | Yes | 729 | 16 | 16
306 | Classroom | 0 | 0 | Yes | 950 | 21 | 21
307A | Classroom | 0 | 0 | Yes | 292 | 6 | 6
308 | Classroom | 0 | 0 | Yes | 900 | 20 | 20
309 | Classroom | 0 | 0 | Yes | 687 | 15 | 15
311 | Classroom | 0 | 0 | Yes | 348 | 7 | 7

## Gideon
Sheet Last Modified: | 2021-03-12
School: | Edward Gideon Elementary School
Vendor: | Emcor Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 309 | 20 |  | 814.55 | 18 | 18 | Unit Ventilator
102 | Classroom | 380 | 25 |  | 745.36 | 16 | 16 | Unit Ventilator
Hallway @ 102 | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator
- | Girls Bathroom next to Room 102 |  | 0 |  | 262.3 | 5 | 0 | N/A
- | Boys Bathroom next to Room 102 |  | 0 |  | 293.8 | 6 | 0 | N/A
103 | Classroom | 247 | 16 |  |  | 0 | 0 | Unit Ventilator
103 A | - |  | 0 |  | 207.09 | 4 | 0 | Unit Ventilator
103 B | - |  | 0 |  | 175 | 3 | 0 | Unit Ventilator
104 | Classroom | 226 | 15 |  | 450 | 10 | 10 | Unit Ventilator
104 A | - |  | 0 |  | 96.65 | 2 | 0 | Unit Ventilator
104 B | - |  | 0 |  | 150.96 | 3 | 0 | Unit Ventilator
104 C | - |  | 0 |  | 134.31 | 3 | 0 | Unit Ventilator
104 | Counselor |  | 0 |  | 450.66 | 10 | 0 | Unit Ventilator
105 | Classroom | 323 | 21 |  | 872 | 19 | 19 | Unit Ventilator
Hallway @ 105 | Hallway | 325 | 21 |  |  | 0 | 0 | Unit Ventilator
106A | Main Office |  | 0 | Yes | 393.55 | 8 | 8 | Unit Ventilator
106E | Principal Office |  | 0 | Yes | 165.77 | 3 | 3 | Unit Ventilator
109 | Classroom | 351 | 23 |  | 858 | 19 | 19 | Unit Ventilator
110 | Classroom | 374 | 24 |  | 811 | 18 | 18 | Unit Ventilator
111 | Classroom | 253 | 16 |  | 866 | 19 | 16 | Unit Ventilator
113 A | School police |  | 0 |  | 316.8 | 7 | 0 | Unit Ventilator
113 b | inner office |  | 0 |  | 153.45 | 3 | 0 | Unit Ventilator
113 c | inner office |  | 0 | Yes | 163.68 | 3 | 3 | Unit Ventilator
201 | Classroom | 154 | 10 |  | 1019 | 23 | 10 | Unit Ventilator
Hallway @ 201 | Hallway | 225 | 15 |  |  | 0 | 0 | Unit Ventilator
202 | Classroom | 537 | 35 |  | 924 | 21 | 21 | Unit Ventilator
203 | Classroom | 0 | 0 | Yes | 938.05 | 21 | 21 | Unit Ventilator
204 | Classroom | 319 | 21 |  | 787.94 | 17 | 17 | Unit Ventilator
205 | Classroom | 296 | 19 |  | 822.36 | 18 | 18 | Unit Ventilator
206 | Classroom | 310 | 20 |  | 822.36 | 18 | 18 | Unit Ventilator
Hallway @ 206 | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator
207 | Classroom | 350 | 23 |  | 822 | 18 | 18 | Unit Ventilator
- | Boys Bathroom outside Room 207 |  | 0 |  | 164.4 | 3 | 0 | N/A
208 | Classroom | 328 | 21 |  | 824.67 | 18 | 18 | Unit Ventilator
- | Female Staff Bathroom outside Room 208 |  | 0 |  | 61 | 1 | 0 | N/A
- | Girls Bathroom outside Room 208 |  | 0 |  | 127.07 | 2 | 0 | N/A
209 | Classroom | 310 | 20 |  | 822.36 | 18 | 18 | Unit Ventilator
210 | Classroom | 253 | 16 |  | 810.81 | 18 | 16 | Unit Ventilator
211 | Classroom | 262 | 17 |  | 829.29 | 18 | 17 | Unit Ventilator
212 | Classroom | 365 | 24 |  | 824.67 | 18 | 18 | Unit Ventilator
Hallway @ 212 | Hallway | 215 | 14 |  |  | 0 | 0 | Unit Ventilator
213 | Classroom | 357 | 23 |  | 425.92 | 9 | 9 | Unit Ventilator
301 | Classroom | 189 | 12 | Yes | 829.29 | 18 | 18 | Unit Ventilator
302 | Classroom | 298 | 19 |  | 822.36 | 18 | 18 | Unit Ventilator
302 A | Bathroom |  | 0 |  | 231.68 | 5 | 0 | N/A
302 B | Bathroom |  | 0 |  | 147.14 | 3 | 0 | N/A
303 | Classroom | 0 | 0 | Yes | 894.14 | 20 | 20 | Unit Ventilator
304 | Classroom | 316 | 21 |  | 787.94 | 17 | 17 | Unit Ventilator
305 | Classroom | 422 | 28 |  | 820.05 | 18 | 18 | Unit Ventilator
306 | Classroom | 288 | 19 |  | 822.36 | 18 | 18 | Unit Ventilator
Hallway @ 306 | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator
307 | Classroom | 351 | 23 |  | 822.36 | 18 | 18 | Unit Ventilator
308 | Classroom | 476 | 31 |  | 825.92 | 18 | 18 | Unit Ventilator
Hallway @ 308 | Hallway | 250 | 16 |  |  | 0 | 0 | Unit Ventilator
309 | Classroom | 349 | 23 |  | 825.92 | 18 | 18 | Unit Ventilator
310 | Classroom | 321 | 21 |  | 810.81 | 18 | 18 | Unit Ventilator
311 | Classroom | 331 | 22 |  | 829.29 | 18 | 18 | Unit Ventilator
312 | Classroom | 367 | 24 |  | 822.36 | 18 | 18 | Unit Ventilator
Hallway @ 312 | Hallway | 215 | 14 |  |  | 0 | 0 | Unit Ventilator
- | Auditorium | 630 | 42 |  |  | 0 | 0 | AHU
GYM | GYM | 572 | 38 |  |  | 0 | 0 | Unit Ventilator
Hallway @ Elevator | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator
Hallway @ Stair D | Hallway | 231 | 15 |  |  | 0 | 0 | Unit Ventilator
- | Nurse | 0 | 0 |  |  | 0 | 0 | Unit Ventilator
- | Teachers Lounge | 0 | 0 |  |  | 0 | 0 | Unit Ventilator
- | Auditorium |  | 0 |  | 2998.47 | 68 | 0 | AHU
- | Auditorium Rear classroom |  | 0 |  | 250.86 | 5 | 0 | AHU
- | Boys bathroom outside main offce |  | 0 |  | 303.36 | 6 | 0 | N/A
- | 3rd floor Boys bathroom |  | 0 |  | 219.97 | 4 | 0 | N/A
- | Building Engineer Office |  | 0 |  | 99.44 | 2 | 0 | N/A
- | 3rd floor Girls bathroom |  | 0 |  | 192.06 | 4 | 0 | N/A
- | Girls bathroom outside main offce |  | 0 |  | 299.88 | 6 | 0 | N/A
- | 3rd floor Gym Teacher office |  | 0 |  | 284.48 | 6 | 0 | N/A
- | 3rd floor Gym/Lunchroom |  | 0 |  | 3603.25 | 81 | 0 | Unit Ventilator
- | Kitchen |  | 0 |  | 509.42 | 11 | 0 | N/A
- | Parent & teacher conf rm |  | 0 |  | 122.92 | 2 | 0 | Unit Ventilator
- | Principal Conf rm |  | 0 |  | 158.63 | 3 | 0 | Unit Ventilator
- | Teacher Lounge |  | 0 |  | 436.21 | 9 | 0 | Unit Ventilator

## Girard
Sheet Last Modified: | 2021-04-29
School: | Stephen Girard Elementary School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | 100 | 51 | 3 | Yes | 672 | 15 | 15 | Unit Ventilator
101 | 101 | 114 | 7 | Yes | 1200 | 27 | 27 | Unit Ventilator
103 | 103 | 27 | 1 | Yes | 840 | 19 | 19 | Unit Ventilator
105 | 105 | 62 | 4 |  | 840 | 19 | 4 | Unit Ventilator
118 | Speech Classroom |  | 0 | Yes | 275 | 6 | 6 | N/A
200 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
201 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
202 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
203 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
204 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
205 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
206 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
207 | Classroom |  | 0 | Yes | 375 | 8 | 8 | Unit Ventilator
208 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
209 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
210 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
216 | Classroom |  | 0 |  | 200 | 4 | 0
300 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
301 | Classroom |  | 0 |  | 840 | 19 | 0 | Unit Ventilator
302 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
303 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
304 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
305 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
306 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
307 / 309 | Classroom |  | 0 | Yes | 1375 | 31 | 31 | Unit Ventilator
308 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
308A | Classroom |  | 0 |  | 364 | 8 | 0
310 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
- | Auditorium | 11536 | 769 |  | 2600 | 59 | 59 | AHU
- | Gymnasium | 1656 | 110 |  | 3550 | 80 | 80 | AHU
- | IMC | 227 | 15 |  | 1846 | 41 | 15 | Unit Ventilator
- | Nurse |  | 0 | Yes | 170 | 3 | 3 | N/A
- | Principal Office |  | 0 | Yes | 294 | 6 | 6
- | Main Office |  | 0 | Yes | 396 | 9 | 9 | Unit Ventilator

## Girls HS
Sheet Last Modified: | 2021-04-27
School: | Philadelphia High School for Girls
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B-12 | Showers | 2144 | 142 |  | 2163 | 49 | 49 | AHU
B-13 | Visitors' Lockers | 0 | 0 |  | 256 | 5 | 0 | Unit Ventilator
B-14 | Home Lockers | 0 | 0 |  | 316 | 7 | 0 | Unit Ventilator
B-16 | Girls' Locker Room | 1254 | 83 |  | 4702 | 106 | 83 | Unit Ventilator
G-1 | Classroom | 292 | 19 |  | 1032 | 23 | 19 | Unit Ventilator
G-3 | Classroom | 459 | 30 |  | 1216 | 27 | 27 | Unit Ventilator
G-6 | - | 0 | 0 |  | 734 | 16 | 0 | Unit Ventilator
G-8 | Dance | 277 | 18 |  | 1275 | 28 | 18 | Unit Ventilator
G-10 | Classroom | 281 | 18 |  | 741 | 16 | 16 | Unit Ventilator
G-11 | Classroom | 274 | 18 |  | 745 | 16 | 16 | Unit Ventilator
G-12 | Classroom | 222 | 14 |  | 714 | 16 | 14 | Unit Ventilator
G-17 | Classroom | 93 | 6 |  | 748 | 17 | 6 | Unit Ventilator
G-19 | Classroom | 277 | 18 |  | 718 | 16 | 16 | Unit Ventilator
1 | Fitness Room | 227 | 15 |  | 1169 | 26 | 15 | Unit Ventilator
2 | Fitness Room | 506 | 33 |  | 2048 | 46 | 33 | Unit Ventilator
100 | Classroom | 306 | 20 |  | 756 | 17 | 17 | Unit Ventilator
101 | Classroom | 275 | 18 |  | 756 | 17 | 17 | Unit Ventilator
102 | Archives | 145 | 9 |  | 689 | 15 | 9 | Unit Ventilator
104 | Classroom | 221 | 14 |  | 756 | 17 | 14 | Unit Ventilator
105 | Instruments | 612 | 40 |  | 2376 | 54 | 40 | Unit Ventilator
106 | Roster Office | 208 | 13 |  | 778 | 17 | 13 | Unit Ventilator
107 | Office | 290 | 19 |  | 799 | 18 | 18 | Unit Ventilator
108 | Office | 0 | 0 |  | 769 | 17 | 0 | Unit Ventilator
109 | Office | 291 | 19 |  | 790 | 17 | 17 | Unit Ventilator
110 | Office | 203 | 13 |  | 768 | 17 | 13 | Unit Ventilator
111 | Poetry | 188 | 12 |  | 1182 | 26 | 12 | Unit Ventilator
111-A | Health Office | 0 | 0 |  | 462 | 10 | 0 | Unit Ventilator
112 | Classroom | 0 | 0 |  | 767 | 17 | 0 | Unit Ventilator
113 | Classroom | 0 | 0 |  | 1655 | 37 | 0 | Unit Ventilator
114 | Classroom | 0 | 0 |  | 769 | 17 | 0 | Unit Ventilator
115 | Classroom | 0 | 0 |  | 1749 | 39 | 0 | Unit Ventilator
116 | Classroom | 0 | 0 |  | 749 | 17 | 0 | Unit Ventilator
118 | Classroom | 0 | 0 |  | 752 | 17 | 0 | Unit Ventilator
200 | Classroom | 0 | 0 |  | 775 | 17 | 0 | Unit Ventilator
201 | Classroom | 221 | 14 |  | 763 | 17 | 14 | Unit Ventilator
202 | Classroom | 213 | 14 |  | 771 | 17 | 14 | Unit Ventilator
204 | Classroom | 0 | 0 |  | 771 | 17 | 0 | Unit Ventilator
205 | Music Office | 472 | 31 |  | 2334 | 53 | 31 | Unit Ventilator
206 | Classroom | 0 | 0 |  | 780 | 17 | 0 | Unit Ventilator
207 | Classroom | 289 | 19 |  | 768 | 17 | 17 | Unit Ventilator
208 | Classroom | 213 | 14 |  | 776 | 17 | 14 | Unit Ventilator
209 | Classroom | 251 | 16 |  | 786 | 17 | 16 | Unit Ventilator
210 | Classroom | 255 | 17 |  | 781 | 17 | 17 | Unit Ventilator
211 | Classroom | 268 | 17 |  | 744 | 16 | 16 | Unit Ventilator
212 | Classroom | 388 | 25 |  | 780 | 17 | 17 | Unit Ventilator
214 | Classroom | 251 | 16 |  | 776 | 17 | 16 | Unit Ventilator
215 | Classroom | 402 | 26 |  | 781 | 17 | 17 | Unit Ventilator
216 | Classroom | 244 | 16 |  | 772 | 17 | 16 | Unit Ventilator
217 | Classroom | 178 | 11 |  | 787 | 17 | 11 | Unit Ventilator
218 | Classroom | 0 | 0 |  | 789 | 17 | 0 | Unit Ventilator
219 | Classroom | 54 | 3 |  | 783 | 17 | 3 | Unit Ventilator
221 | Classroom | 290 | 19 |  | 841 | 19 | 19 | Unit Ventilator
223 | Classroom | 0 | 0 |  | 891 | 20 | 0 | Unit Ventilator
300 | Classroom | 270 | 18 |  | 786 | 17 | 17 | Unit Ventilator
302 | Classroom | 416 | 27 |  | 996 | 22 | 22 | Unit Ventilator
303 | Classroom | 555 | 37 |  | 1052 | 23 | 23 | Unit Ventilator
304 | Classroom | 525 | 35 |  | 1007 | 22 | 22 | Unit Ventilator
305 | Classroom | 279 | 18 |  | 791 | 17 | 17 | Unit Ventilator
306 | Classroom | 378 | 25 |  | 1034 | 23 | 23 | Unit Ventilator
307 | Classroom | 0 | 0 |  | 781 | 17 | 0 | Unit Ventilator
308 | Classroom | 158 | 10 |  | 1048 | 23 | 10 | Unit Ventilator
309 | Classroom | 188 | 12 |  | 787 | 17 | 12 | Unit Ventilator
310 | Classroom | 403 | 26 |  | 1115 | 25 | 25 | Unit Ventilator
311 | Classroom | 186 | 12 |  | 792 | 18 | 12 | Unit Ventilator
312 | Classroom | 240 | 16 |  | 1015 | 23 | 16 | Unit Ventilator
313 | Classroom | 202 | 13 |  | 779 | 17 | 13 | Unit Ventilator
314 | Classroom | 329 | 21 |  | 1008 | 22 | 21 | Unit Ventilator
315 | Classroom | 289 | 19 |  | 790 | 17 | 17 | Unit Ventilator
316 | Classroom | 326 | 21 |  | 788 | 17 | 17 | Unit Ventilator
317 | Classroom | 169 | 11 |  | 780 | 17 | 11 | Unit Ventilator
319 | Classroom | 351 | 23 |  | 706 | 16 | 16 | Unit Ventilator
321 | Classroom | 293 | 19 |  | 716 | 16 | 16 | Unit Ventilator
- | Auditorium | 946 | 63 |  | 10546 | 239 | 63 | AHU
- | Gymnasium | 287 | 19 |  | 10449 | 237 | 19 | AHU
- | Main Cafeteria | 2523 | 168 |  | 12220 | 277 | 168 | Unit Ventilator
- | Faculty Cafeteria | 549 | 36 |  | 1172 | 26 | 26 | Unit Ventilator
- | Main Office | 192 | 12 |  | 1054 | 23 | 12 | Unit Ventilator
- | Library | 538 | 35 |  | 5853 | 133 | 35 | Unit Ventilator

## Gompers
Sheet Last Modified: | 2021-04-23
School: | Samuel Gompers Elementary-Middle School
Vendor: | Capital
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Kindergarten | 334 | 22 |  | 2002 | 45 | 22 | Unit Ventilator
102 | Classroom | 429 | 28 |  | 1106 | 25 | 25 | Unit Ventilator
104 | Classroom | 450 | 30 |  | 1099 | 24 | 24 | Unit Ventilator
105 | Classroom | 444 | 29 |  | 1094 | 24 | 24 | Unit Ventilator
106 | Classroom | 436 | 29 |  | 1095 | 24 | 24 | Unit Ventilator
107 | Classroom | 432 | 28 |  | 1102 | 25 | 25 | Unit Ventilator
B-107 | Library | 492 | 32 |  | 1241 | 28 | 28 | Unit Ventilator
B-107A | Workroom | 28 | 1 |  | 204 | 4 | 1 | Unit Ventilator
A-108 | Teacher Room | 138 | 9 |  | 387 | 8 | 8 | Unit Ventilator
A-112 | Infirmary | 21 | 1 |  | 198 | 4 | 1 | Unit Ventilator
A-113 | Waiting | 80 | 5 |  | 155 | 3 | 3 | FCU
A-114 | Nurse’s Office | 339 | 22 |  | 186 | 4 | 4 | FCU
A-121 | Examination | 226 | 15 |  | 310 | 7 | 7 | FCU
A-122 | Office | 22 | 1 |  | 133 | 3 | 1 | Unit Ventilator
A-124 | Counselor Office | 34 | 2 |  | 178 | 4 | 2 | Unit Ventilator
A-131 | General Office | 51 | 3 |  | 488 | 11 | 3 | Unit Ventilator
A-133 | Principal Office | 32 | 2 |  | 232 | 5 | 2 | Unit Ventilator
A-137 | Conference | 96 | 6 |  | 333 | 7 | 6 | Unit Ventilator
A-150 | Office | 117 | 7 |  | 324 | 7 | 7 | FCU
A-153 | Office | 122 | 8 |  | 322 | 7 | 7 | FCU
201 | Classroom | 429 | 28 |  | 1083 | 24 | 24 | Unit Ventilator
202 | Classroom | 431 | 28 |  | 1074 | 24 | 24 | Unit Ventilator
203 | Classroom | 432 | 28 |  | 1075 | 24 | 24 | Unit Ventilator
204 | Classroom | 265 | 17 |  | 544 | 12 | 12 | Unit Ventilator
205 | Classroom | 418 | 27 |  | 1109 | 25 | 25 | Unit Ventilator
A-205 | Teachers Room | 156 | 10 |  | 353 | 8 | 8 | Unit Ventilator
206 | Classroom | 433 | 28 |  | 1110 | 25 | 25 | Unit Ventilator
207 | Classroom | 435 | 29 |  | 1112 | 25 | 25 | Unit Ventilator
208 | Classroom | 438 | 29 |  | 1095 | 24 | 24 | Unit Ventilator
A-208 | After School Programs | 65 | 4 |  | 441 | 10 | 4 | Unit Ventilator
B-209 | Classroom | 262 | 17 |  | 537 | 12 | 12 | Unit Ventilator
B-210 | Classroom | 437 | 29 |  | 1093 | 24 | 24 | Unit Ventilator
B-211 | Classroom | 435 | 29 |  | 1095 | 24 | 24 | Unit Ventilator
212 | Classroom | 419 | 27 |  | 1084 | 24 | 24 | Unit Ventilator
213 | Classroom | 454 | 30 |  | 1087 | 24 | 24 | Unit Ventilator
A-217 | Cafeteria | 466 | 31 |  | 1943 | 44 | 31 | AHU
A-218 | Gymnasium | 1290 | 86 |  | 3950 | 89 | 86 | AHU
Portable | R1 |  | 0 | Yes | 843 | 19 | 19
Portable | R2 |  | 0 | Yes | 842 | 19 | 19
Portable | R3 |  | 0 | Yes | 852 | 19 | 19
Portable | R4 |  | 0 | Yes | 1033 | 23 | 23
Portable | R5 |  | 0 | Yes | 1022 | 23 | 23

## Greenberg
Sheet Last Modified: | 2021-04-22
School: | Joseph Greenberg Elementary-Middle School
Vendor: | Devine Borthers | Devine Brothers Retest
Devine Brothers 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 325 | 21 |  | 828 | 18 | 18 | Unit Ventilator
101 | Classroom | 335 | 22 |  | 828 | 18 | 18 | Unit Ventilator
102 | Classroom | 380 | 25 |  | 828 | 18 | 18 | Unit Ventilator
103 | Classroom | 288 | 19 |  | 828 | 18 | 18 | Unit Ventilator
104 | Classroom | 284 | 18 |  | 384 | 8 | 8 | Unit Ventilator
105 | Nurse | 300 | 20 |  | 432 | 9 | 9 | Unit Ventilator
106 | Classroom | 530 | 35 |  | 1012 | 23 | 23 | Unit Ventilator
107 | Classroom | 671 | 44 |  | 864 | 19 | 19 | Unit Ventilator
107A | Meeting room |  | 0 | Yes | 432 | 9 | 9 | Unit Ventilator
108 | Classroom | 441 | 29 |  | 1012 | 23 | 23 | Unit Ventilator
109 | Classroom | 298 | 19 |  | 828 | 18 | 18 | Unit Ventilator
111 | Classroom | 291 | 19 |  | 828 | 18 | 18 | Unit Ventilator
200 | Classroom | 308 | 20 |  | 828 | 18 | 18 | Unit Ventilator
201 | Classroom | 281 | 18 |  | 828 | 18 | 18 | Unit Ventilator
202 | Classroom | 295 | 19 |  | 828 | 18 | 18 | Unit Ventilator
203 | Classroom | 351 | 23 |  | 828 | 18 | 18 | Unit Ventilator
204 | Classroom | 317 | 21 |  | 828 | 18 | 18 | Unit Ventilator
205 | Classroom | 326 | 21 |  | 828 | 18 | 18 | Unit Ventilator
207 | Classroom | 320 | 21 |  | 828 | 18 | 18 | Unit Ventilator
209 | Classroom | 345 | 23 |  | 828 | 18 | 18 | Unit Ventilator
210 | Classroom | 316 | 21 |  | 384 | 8 | 8 | Unit Ventilator
211 | Classroom | 281 | 18 |  | 368 | 8 | 8 | Unit Ventilator
211a | Classroom | 375 | 25 |  | 621 | 14 | 14 | Unit Ventilator
211b | Classroom | 307 | 20 |  | 828 | 18 | 18 | Unit Ventilator
212 | Classroom | 351 | 23 |  | 828 | 18 | 18 | Unit Ventilator
213 | Classroom | 344 | 22 |  | 828 | 18 | 18 | Unit Ventilator
214 | Classroom | 345 | 23 |  | 828 | 18 | 18 | Unit Ventilator
215 | Classroom | 375 | 25 |  | 828 | 18 | 18 | Unit Ventilator
216 | Classroom | 312 | 20 |  | 828 | 18 | 18 | Unit Ventilator
217 | Classroom | 326 | 21 |  | 828 | 18 | 18 | Unit Ventilator
300 | Classroom | 325 | 21 |  | 828 | 18 | 18 | Unit Ventilator
301 | Classroom | 291 | 19 |  | 828 | 18 | 18 | Unit Ventilator
302 | Classroom | 285 | 19 |  | 552 | 12 | 12 | Unit Ventilator
303 | Classroom | 330 | 22 |  | 828 | 18 | 18 | Unit Ventilator
304 | Classroom | 325 | 21 |  | 828 | 18 | 18 | Unit Ventilator
305 | Classroom | 321 | 21 |  | 828 | 18 | 18 | Unit Ventilator
306 | Classroom | 289 | 19 |  | 384 | 8 | 8 | Unit Ventilator
307 | Classroom | 345 | 23 |  | 828 | 18 | 18 | Unit Ventilator
309 | Classroom | 350 | 23 |  | 1242 | 28 | 23 | Unit Ventilator
313 | Classroom | 302 | 20 |  | 828 | 18 | 18 | Unit Ventilator
314 | Classroom | 289 | 19 |  | 828 | 18 | 18 | Unit Ventilator
315 | Classroom | 321 | 21 |  | 828 | 18 | 18 | Unit Ventilator
316 | Classroom | 311 | 20 |  | 828 | 18 | 18 | Unit Ventilator
317 | Classroom | 331 | 22 |  | 828 | 18 | 18 | Unit Ventilator
318 | Classroom | 314 | 20 |  | 828 | 18 | 18 | Unit Ventilator
319 | Classroom | 311 | 20 |  | 828 | 18 | 18 | Unit Ventilator
321 | Classroom | 288 | 19 |  | 828 | 18 | 18 | Unit Ventilator
400 | Classroom | 375 | 25 |  | 864 | 19 | 19 | Unit Ventilator
401 | IMC Classroom | 310 | 20 |  | 828 | 18 | 18 | Unit Ventilator
- | Auditorium | 12200 | 813 |  | 3213 | 73 | 73 | AHU
- | Cafeteria | 7911 | 527 |  | 5250 | 119 | 119 | AHU
- | Gym | 8800 | 586 |  | 3978 | 90 | 90 | AHU
- | IMC Classroom | 220 | 14 |  | 828 | 18 | 14 | Unit Ventilator
- | Teacher Lounge | 448 | 29 |  | 168 | 3 | 3 | Unit Ventilator
- | Main Office | 280 | 18 |  | 1134 | 25 | 18 | Unit Ventilator
- | Dean's office |  | 0 | Yes | 135 | 3 | 3 | Unit Ventilator
- | Assistant principal office |  | 0 | Yes | 135 | 3 | 3 | Unit Ventilator
- | Principal's Office |  | 0 | Yes | 432 | 9 | 9 | Unit Ventilator
- | Kitchen |  | 0 | Yes | 864 | 19 | 19 | N/A
- | BE office | 275 | 18 |  | 441 | 10 | 10 | N/A
- | Custodial office | 95 | 6 |  | 195 | 4 | 4 | N/A

## Greenfield
Sheet Last Modified: | 2021-04-26
School: | Albert M. Greenfield Elementary School
Vendor: | Meehan | Devine | Capital Part I
Vendor: | Capital Part II | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B06 | Music rm. | 329 | 21 |  | 416 | 9 | 9 | AHU
B17 | Storage | 229 | 15 |  | 320 | 7 | 7 | N/A
B36 | Music main | 452 | 30 |  | 962 | 21 | 21 | AHU
B37 | Music Office | 151 | 10 |  | 168 | 3 | 3 | AHU
B38 | Practice rm | 44 | 2 |  | 64 | 1 | 1 | AHU
B40 | Music Ensamble | 163 | 10 |  | 312 | 7 | 7 | AHU
101 | Reception | 121 | 8 |  | 360 | 8 | 8 | AHU
102 |  | 0 |  | Yes | 120 |  |  | N/A
103 | Offices | 0 | 0 | Yes | 120 | 2 | 2 | AHU
104 | Offices | 0 | 0 | Yes | 120 | 2 | 2 | AHU
105 | Sensory Room | 46 | 3 |  | 120 | 2 | 2 | AHU
106 | Office | 76 | 5 |  | 231 | 5 | 5 | AHU
107 | Nurse Reception | 0 | 0 | Yes | 81 | 1 | 1 | AHU
107A | Nurse Office | 48 | 3 | Yes | 189 | 4 | 4 | AHU
107B | Offices | 0 | 0 | Yes | 99 | 2 | 2 | AHU
107C | Storage | 0 | 0 |  | 110 | 2 | 0 | N/A
108 | Conference | 65 | 4 |  | 238 | 5 | 4 | AHU
109 | Admin | 0 | 0 | Yes | 130 | 2 | 2 | AHU
110 | Classroom | 340 | 22 |  | 936 | 21 | 21 | Unit Ventilator
111 | Classroom | 491 | 32 |  | 936 | 21 | 21 | Unit Ventilator
112 | Classroom | 366 | 24 |  | 936 | 21 | 21 | Unit Ventilator
113A | Classroom | 1038 | 69 |  | 676 | 15 | 15 | Unit Ventilator
126 | Lobby | 55 | 3 |  | 676 | 15 | 3 | Unit Ventilator
128 | Corridor | 60 | 4 |  | 456 | 10 | 4 | Unit Ventilator
129 | Principal Office | 94 | 6 |  | 220 | 5 | 5 | Unit Ventilator
201 | Classroom | 150 | 10 |  | 260 | 5 | 5 | Unit Ventilator
202 | Classroom | 390 | 26 |  | 884 | 20 | 20 | Unit Ventilator
203 | Classroom | 302 | 20 |  | 884 | 20 | 20 | Unit Ventilator
204 | Classroom | 493 | 32 |  | 725 | 16 | 16 | Unit Ventilator
205 | Classroom | 475 | 31 |  | 850 | 19 | 19 | Unit Ventilator
206 | Classroom | 488 | 32 |  | 918 | 20 | 20 | Unit Ventilator
207 | Classroom | 570 | 38 |  | 990 | 22 | 22 | Unit Ventilator
208 | Classroom | 407 | 27 |  | 362 | 8 | 8 | Unit Ventilator
208A | Classroom | 74 | 4 |  | 195 | 4 | 4 | Unit Ventilator
209 | Classroom | 461 | 30 |  | 672 | 15 | 15 | Unit Ventilator
210 | Classroom | 357 | 23 |  | 957 | 21 | 21 | Unit Ventilator
211 | Classroom | 545 | 36 |  | 990 | 22 | 22 | Unit Ventilator
212 | Classroom | 416 | 27 |  | 812 | 18 | 18 | Unit Ventilator
213 | Classroom | 444 | 29 |  | 924 | 21 | 21 | Unit Ventilator
214 | Classroom | 430 | 28 |  | 864 | 19 | 19 | Unit Ventilator
215 | Classroom | 429 | 28 |  | 952 | 21 | 21 | Unit Ventilator
216 | Classroom | 180 | 12 |  | 325 | 7 | 7 | Unit Ventilator
217 | Classroom | 206 | 13 |  | 420 | 9 | 9 | Unit Ventilator
218 | Classroom | 0 | 0 |  |  | 0 | 0 | Unit Ventilator
225 | Library | 1255 | 83 |  | 3628 | 82 | 82 | Unit Ventilator
301 | Classroom | 570 | 38 |  | 957 | 21 | 21 | Unit Ventilator
302 | Classroom | 289 | 19 |  | 864 | 19 | 19 | Unit Ventilator
303 | Classroom | 328 | 21 |  | 957 | 21 | 21 | Unit Ventilator
304 | Classroom | 501 | 33 |  | 754 | 17 | 17 | Unit Ventilator
305 | Classroom | 336 | 22 |  | 1020 | 23 | 22 | Unit Ventilator
306 | Classroom | 545 | 36 |  | 1020 | 23 | 23 | Unit Ventilator
307 | Classroom | 374 | 24 |  | 506 | 11 | 11 | Unit Ventilator
308 | Classroom | 418 | 27 |  | 460 | 10 | 10 | Unit Ventilator
309 | Classroom | 550 | 36 |  | 924 | 21 | 21 | Unit Ventilator
310 | Classroom | 441 | 29 |  | 1020 | 23 | 23 | Unit Ventilator
311 | Classroom | 439 | 29 |  | 924 | 21 | 21 | Unit Ventilator
312 | Classroom | 401 | 26 |  | 696 | 15 | 15 | Unit Ventilator
313 | Classroom | 530 | 35 |  | 957 | 21 | 21 | Unit Ventilator
314 | Classroom | 325 | 21 |  | 858 | 19 | 19 | Unit Ventilator
315 | Classroom | 568 | 37 |  | 1650 | 37 | 37 | Unit Ventilator
316 | Classroom | 318 | 21 |  | 1650 | 37 | 21 | Unit Ventilator
317 | Classroom | 300 | 20 |  | 1664 | 37 | 20 | Unit Ventilator
318 | Classroom | 62 | 4 |  |  | 0 | 0 | Unit Ventilator
- | B.E. Office | 139 | 9 |  | 88 | 2 | 2 | AHU
- | GYM | 1357 | 90 |  | 6110 | 138 | 90 | AHU
- | Stage/Auditorium/Cafeteria | 0 | 0 |  | 4588 | 104 | 0 | AHU
- | Kitchen | 47 | 3 |  | 403 | 9 | 3 | AHU

## Hackett
Sheet Last Modified: | 2021-04-07
School: | Horatio Hackett Elementary School
Vendor: | Devine Brothers | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
104 | Library | 501 | 33 | Yes | 1920 | 43 | 43 | Unit Ventilator
106 | Gym Mechanical | 497 | 33 |  | 624 | 14 | 14 | AHU
107 | Gym Mechanical | 959 | 63 |  | 1400 | 31 | 31 | AHU
108 | Lounge | 299 | 19 |  | 560 | 12 | 12 | Unit Ventilator
109 | Classroom | 394 | 26 |  | 1136 | 25 | 25 | Unit Ventilator
110 | Classroom | 323 | 21 |  | 1024 | 23 | 21 | Unit Ventilator
111 | Classroom | 284 | 18 |  | 776 | 17 | 17 | Unit Ventilator
112 | Classroom | 280 | 18 |  | 720 | 16 | 16 | Unit Ventilator
201 | Classroom | 279 | 18 |  | 840 | 19 | 18 | Unit Ventilator
202 | Classroom | 658 | 43 |  | 784 | 17 | 17 | Unit Ventilator
203 | Classroom | 335 | 22 |  | 784 | 17 | 17 | Unit Ventilator
204 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | Unit Ventilator
205 | Classroom | 475 | 31 |  | 840 | 19 | 19 | Unit Ventilator
205A | Sm office / Speech Room | 223 | 14 |  | 304 | 6 | 6 | Unit Ventilator
206 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 | Unit Ventilator
207 | Classroom | 0 | 0 | Yes | 488 | 11 | 11 | Unit Ventilator
207A | Small Office | 120 | 8 |  | 248 | 5 | 5 | Unit Ventilator
208 | Classroom | 278 | 18 |  | 784 | 17 | 17 | Unit Ventilator
209 | Classroom | 362 | 24 |  | 672 | 15 | 15 | Unit Ventilator
210 | Classroom | 0 | 0 | Yes | 784 | 17 | 17 | Unit Ventilator
211 | Classroom | 334 | 22 |  | 784 | 17 | 17 | Unit Ventilator
212 | Classroom | 355 | 23 |  | 840 | 19 | 19 | Unit Ventilator
212A | Office/Councelors |  | 0 |  | 336 | 7 | 0 | N/A
214 | Classroom | 455 | 30 |  | 864 | 19 | 19 | AHU
215 | Classroom | 405 | 27 |  | 920 | 20 | 20 | AHU
216 | Classroom | 505 | 33 |  | 832 | 18 | 18 | AHU
217 | Classroom | 390 | 26 |  | 768 | 17 | 17 | Unit Ventilator
218 | Classroom | 311 | 20 | Yes | 976 | 22 | 22 | AHU
219 | Classroom | 405 | 27 |  | 880 | 20 | 20 | AHU
219c | Classroom | 123 | 8 |  | 288 | 6 | 6 | Unit Ventilator
305 | Classroom | 400 | 26 |  | 1000 | 22 | 22 | Unit Ventilator
306 | Classroom | 0 | 0 | Yes | 936 | 21 | 21 | Unit Ventilator
307 | Classroom | 315 | 21 |  | 824 | 18 | 18 | Unit Ventilator
308 | Classroom | 329 | 21 |  | 824 | 18 | 18 | Unit Ventilator
308D | Councelors | 38 | 2 | Yes | 384 | 8 | 8 | Unit Ventilator
309 | Classroom | 395 | 26 |  | 944 | 21 | 21 | Unit Ventilator
- | Caf/Auditorium | 1435 | 95 |  | 6914 | 157 | 95 | AHU
- | GYM | 964 | 64 |  | 4770 | 108 | 64 | AHU
- | Kitchen | 413 | 27 |  | 954 | 21 | 21 | AHU
- | Main Office | 304 | 20 |  | 832 | 18 | 18 | Unit Ventilator
- | Nurses Office | 50 | 3 | Yes | 564 | 12 | 12 | Unit Ventilator

## Hamilton
Sheet Last Modified: | 2021-04-08
School: | Andrew Hamilton Elementary School
Vendor: | Capital | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
104 | Classroom | 398 | 26 |  | 598 | 13 | 13 | Unit Ventilator
106 | Classroom | 407 | 27 |  | 755 | 17 | 17 | Unit Ventilator
107 | Classroom | 376 | 25 |  | 599 | 13 | 13 | Unit Ventilator
111 | Cafeteria | 1724 | 114 |  | 2444 | 55 | 55 | AHU
112 | Auditorium | 813 | 54 |  | 3875 | 88 | 54 | AHU
119 | Music | 391 | 26 |  | 827 | 18 | 18 | AHU
121 | Gym | 1663 | 110 |  | 4628 | 105 | 105 | AHU
127 | Classroom | 595 | 39 |  | 1186 | 26 | 26 | Unit Ventilator
128 | Classroom | 628 | 41 |  | 1370 | 31 | 31 | Unit Ventilator
129 | Classroom | 565 | 37 |  | 1112 | 25 | 25 | Unit Ventilator
130 | Classroom | 608 | 40 |  | 1378 | 31 | 31 | Unit Ventilator
131 | Classroom | 575 | 38 |  | 1169 | 26 | 26 | Unit Ventilator
200 | Classroom | 415 | 27 |  | 763 | 17 | 17 | Unit Ventilator
201 | Classroom | 527 | 35 |  | 776 | 17 | 17 | Unit Ventilator
202 | Teachers Lounge | 300 | 20 |  | 469 | 10 | 10 | Unit Ventilator
205 | Team Planning | 353 | 23 |  | 431 | 9 | 9 | Unit Ventilator
206 | Classroom | 454 | 30 |  | 595 | 13 | 13 | Unit Ventilator
207 | Classroom | 454 | 30 |  | 847 | 19 | 19 | Unit Ventilator
209 | General Office | 750 | 50 |  | 866 | 19 | 19 | Unit Ventilator
223 | Classroom | 432 | 28 |  | 847 | 19 | 19 | Unit Ventilator
224 | Classroom | 426 | 28 |  | 837 | 19 | 19 | Unit Ventilator
225 | Classroom | 394 | 26 |  | 837 | 19 | 19 | Unit Ventilator
226 | Classroom | 393 | 26 |  | 840 | 19 | 19 | Unit Ventilator
227 | Classroom | 395 | 26 |  | 832 | 18 | 18 | Unit Ventilator
228 | Classroom | 477 | 31 |  | 847 | 19 | 19 | Unit Ventilator
300 | Classroom | 400 | 26 |  | 793 | 18 | 18 | Unit Ventilator
301 | Classroom | 421 | 28 |  | 791 | 17 | 17 | Unit Ventilator
302 | Classroom | 393 | 26 |  | 786 | 17 | 17 | Unit Ventilator
303 | Classroom | 365 | 24 |  | 640 | 14 | 14 | Unit Ventilator
306 | Classroom | 413 | 27 |  | 793 | 18 | 18 | Unit Ventilator
307 | Classroom | 464 | 30 |  | 793 | 18 | 18 | Unit Ventilator
309 | Classroom | 306 | 20 |  | 597 | 13 | 13 | Unit Ventilator
310 | Classroom | 0 | 0 | Yes | 708 | 16 | 16
311J | Janitors | 173 | 11 |  | 59 | 1 | 1 | Unit Ventilator
314 | Office | 551 | 36 |  | 214 | 4 | 4 | Unit Ventilator
315 | Office | 724 | 48 |  | 214 | 4 | 4 | Unit Ventilator
318 | Classroom | 382 | 25 |  | 911 | 20 | 20 | Unit Ventilator
319 | Classroom | 0 | 0 | Yes | 616 | 14 | 14 | Unit Ventilator
320 | Team Planning | 0 | 0 | Yes | 235 | 5 | 5 | Unit Ventilator
321 | Team Planning | 300 | 20 |  | 243 | 5 | 5 | Unit Ventilator
322 | Classroom | 450 | 30 |  | 820 | 18 | 18 | Unit Ventilator
323 | Classroom | 0 | 0 | Yes | 620 | 14 | 14 | Unit Ventilator
327 | Office | 432 | 28 |  | 201 | 4 | 4 | Unit Ventilator
328 | Office | 735 | 49 |  | 233 | 5 | 5 | Unit Ventilator
331 | Classroom | 0 | 0 | Yes | 667 | 15 | 15 | Unit Ventilator
332 | Classroom | 339 | 22 |  | 625 | 14 | 14 | Unit Ventilator
333 | Classroom | 423 | 28 |  | 894 | 20 | 20 | Unit Ventilator
334 | Classroom | 393 | 26 |  | 800 | 18 | 18 | Unit Ventilator
335 | Classroom | 838 | 55 |  | 1684 | 38 | 38 | Unit Ventilator
336 | Classroom | 375 | 25 |  | 908 | 20 | 20 | Unit Ventilator
337 | Classroom | 0 | 0 | Yes | 932 | 21 | 21 | Unit Ventilator
- | Library | 2442 | 162 |  | 3672 | 83 | 83 | Unit Ventilator

## Hancock
Sheet Last Modified: | 2021-04-21
School: | John Hancock Demonstrative Elementary School
Vendor: | Devine Brothers | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 127 | 8 |  | 528 | 12 | 8 | Unit Ventilator
102 | Classroom | 416 | 27 |  | 750 | 17 | 17 | Unit Ventilator
103 | Classroom | 123 | 8 |  | 567 | 12 | 8 | Unit Ventilator
104 | Classroom | 283 | 18 |  | 483 | 10 | 10 | Unit Ventilator
105 | Classroom | 0 | 0 | Yes | 567 | 12 | 12 | Unit Ventilator
106 | Classroom | 171 | 11 |  | 756 | 17 | 11 | Unit Ventilator
107 | Classroom | 237 | 15 |  | 806 | 18 | 15 | Unit Ventilator
108 | Classroom | 0 | 0 | Yes | 648 | 14 | 14 | Unit Ventilator
109 | Classroom | 173 | 11 |  | 638 | 14 | 11 | Unit Ventilator
110 | Classroom | 233 | 15 |  | 812 | 18 | 15 | Unit Ventilator
111 | Classroom | 168 | 11 |  | 588 | 13 | 11 | Unit Ventilator
200 | Classroom | 323 | 21 | Yes | 510 | 11 | 11 | Unit Ventilator
200A | Office |  | 0 | Yes |  | 0 | 0
202 | Classroom | 432 | 28 |  | 1271 | 28 | 28 | Unit Ventilator
203 | Classroom | 299 | 19 |  | 588 | 13 | 13 | Unit Ventilator
204 | Classroom | 324 | 21 |  | 575 | 13 | 13 | Unit Ventilator
205 | Classroom | 255 | 17 |  | 616 | 14 | 14 | Unit Ventilator
206 | Classroom | 324 | 21 |  | 1116 | 25 | 21 | Unit Ventilator
207 | Classroom | 310 | 20 |  | 864 | 19 | 19 | Unit Ventilator
208 | Classroom | 308 | 20 |  | 837 | 19 | 19 | Unit Ventilator
209 | Classroom | 312 | 20 |  | 868 | 19 | 19 | Unit Ventilator
210 | Classroom | 303 | 20 |  | 728 | 16 | 16 | Unit Ventilator
211 | Classroom | 298 | 19 |  | 754 | 17 | 17 | Unit Ventilator
212 | Classroom |  | 0 | Yes | 744 | 16 | 16 | Unit Ventilator
213 | Classroom | 174 | 11 | Yes | 806 | 18 | 18 | Unit Ventilator
214 | Computer Lab | 312 | 20 |  | 462 | 10 | 10 | Unit Ventilator
215 | Classroom | 0 | 0 | Yes | 364 | 8 | 8 | Unit Ventilator
216 | Classroom | 0 | 0 |  | 364 | 8 | 0 | Unit Ventilator
217 | Classroom | 334 | 22 |  | 875 | 19 | 19 | Unit Ventilator
219 | Classroom | 294 | 19 |  | 792 | 18 | 18 | Unit Ventilator
218 | Nurse Office |  | 0 | Yes | 252 | 5 | 5
220 | Office | 0 | 0 | Yes | 126 | 2 | 2 | Unit Ventilator
B213 | Classroom |  | 0 | Yes | 363 | 8 | 8
B3 | Faculty Lounge | 184 | 12 | Yes | 540 | 12 | 12 | Unit Ventilator
B13 | Classroom |  | 0 | Yes |  | 0 | 0
HS215 | Classroom |  | 0 | Yes | 608 | 13 | 13
HS216 | Classroom |  | 0 | Yes | 608 | 13 | 13
- | Classroom Behind kitchen | 37 | 2 |  | 224 | 5 | 2 | Unit Ventilator
- | Gym Office | 0 | 0 | Yes | 100 | 2 | 2 | Unit Ventilator
- | Gym |  | 0 |  | 288 | 6 | 0 | AHU
- | Cafeteria | 0 | 0 |  | 4600 | 104 | 0 | AHU
- | Kitchen | 0 | 0 | Yes | 448 | 10 | 10 | Unit Ventilator
- | Main Lobby | 0 | 0 |  | 720 | 16 | 0 | Unit Ventilator
- | Main Office | 201 | 13 |  | 340 | 7 | 7 | Unit Ventilator
- | Main Office Side Office | 0 | 0 |  | 104 | 2 | 0 | Unit Ventilator
- | Principals Office | 196 | 13 |  | 238 | 5 | 5 | Unit Ventilator
Assistant Principal | Office |  | 0 | Yes |  | 0 | 0
Dean | Office |  | 0 | Yes |  | 0 | 0
- | Library | 692 | 46 |  | 1520 | 34 | 34 | Unit Ventilator
- | Office Across from 210 | 0 | 0 |  | 120 | 2 | 0 | N/A
- | Office across from gym | 0 | 0 |  | 204 | 4 | 0 | Unit Ventilator
- | Office across from Room 107 | 76 | 5 |  | 140 | 3 | 3 | Unit Ventilator
- | Office across from room 110 | 115 | 7 |  | 140 | 3 | 3 | Unit Ventilator
- | Office Next to gym | 0 | 0 |  | 80 | 1 | 0 | Unit Ventilator

## Harding
Sheet Last Modified: | 2021-05-03
School: | Warren G. Harding Middle School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | - |  | 0 |  | 288 | 6 | 0
101a | - |  | 0 |  | 288 | 6 | 0
102 | - |  | 0 | Yes | 1128 | 25 | 25
102a | - |  | 0 |  | 100 | 2 | 0
103 | - |  | 0 |  | 720 | 16 | 0
104 | - |  | 0 | Yes | 888 | 20 | 20
104a | - |  | 0 |  | 110 | 2 | 0
105 | - |  | 0 |  | 648 | 14 | 0
105b | - |  | 0 |  | 770 | 17 | 0
106c | - |  | 0 |  | 248 | 5 | 0
107 | - |  | 0 |  | 936 | 21 | 0
107a | - |  | 0 |  | 248 | 5 | 0
107b | - |  | 0 |  | 50 | 1 | 0
107c | - |  | 0 |  | 25 | 0 | 0
108 | - |  | 0 | Yes | 886 | 20 | 20
108a | - |  | 0 |  | 130 | 2 | 0
108b | - |  | 0 |  | 25 | 0 | 0
108c | - |  | 0 |  | 50 | 1 | 0
109 | - |  | 0 |  | 576 | 13 | 0
109a | - |  | 0 |  | 135 | 3 | 0
110 | - |  | 0 |  | 912 | 20 | 0
110a | - |  | 0 |  | 40 | 0 | 0
111 | - |  | 0 |  | 624 | 14 | 0
112 | - |  | 0 |  | 576 | 13 | 0
112a | - |  | 0 |  | 308 | 7 | 0
113 | - |  | 0 |  | 360 | 8 | 0
113a | - |  | 0 |  | 242 | 5 | 0
113b | - |  | 0 |  | 352 | 8 | 0
114 | - |  | 0 | Yes | 204 | 4 | 4
116 | - |  | 0 |  | 2120 | 48 | 0
116a | - |  | 0 |  | 416 | 9 | 0
117 | - |  | 0 |  | 2700 | 61 | 0
201 | - |  | 0 | Yes | 360 | 8 | 8
201a | - |  | 0 |  | 432 | 9 | 0
202 | - |  | 0 | Yes | 768 | 17 | 17
203 | - |  | 0 |  | 288 | 6 | 0
203B | - |  | 0 | Yes | 200 | 4 | 4
204 | - |  | 0 | Yes | 720 | 16 | 16
205 | - |  | 0 | Yes | 768 | 17 | 17
206 | - |  | 0 |  | 319 | 7 | 0
206a | - |  | 0 |  | 224 | 5 | 0
206b | - |  | 0 |  | 112 | 2 | 0
208 | - |  | 0 | Yes | 792 | 18 | 18
209 | IMC |  | 0 | Yes | 2160 | 49 | 49
211 | - |  | 0 |  | 936 | 21 | 0
212 | - |  | 0 |  | 888 | 20 | 0
213 | - |  | 0 |  | 336 | 7 | 0
214 | - |  | 0 |  | 696 | 15 | 0
215 | - |  | 0 | Yes | 648 | 14 | 14
216 | - |  | 0 |  | 744 | 16 | 0
217 | - |  | 0 |  | 638 | 14 | 0
218 | - |  | 0 |  | 792 | 18 | 0
219 | - |  | 0 |  | 768 | 17 | 0
220 | - |  | 0 |  | 744 | 16 | 0
221 | - |  | 0 |  | 744 | 16 | 0
222 | - |  | 0 | Yes | 768 | 17 | 17
223 | - |  | 0 | Yes | 816 | 18 | 18
224 | - |  | 0 | Yes | 638 | 14 | 14
225 | - |  | 0 |  | 144 | 3 | 0
301 | - |  | 0 |  | 648 | 14 | 0
302 | - |  | 0 |  | 768 | 17 | 0
303 | - |  | 0 | Yes | 390 | 8 | 8
304 | - |  | 0 |  | 720 | 16 | 0
305 | - |  | 0 |  | 768 | 17 | 0
306 | - |  | 0 |  | 966 | 21 | 0
307a | - |  | 0 |  | 360 | 8 | 0
307b | - |  | 0 |  | 600 | 13 | 0
308a | - |  | 0 |  | 480 | 10 | 0
308b | - |  | 0 |  | 336 | 7 | 0
309 | - |  | 0 |  | 816 | 18 | 0
310 | - |  | 0 |  | 1056 | 24 | 0
311 | - |  | 0 |  | 960 | 21 | 0
311a | - |  | 0 |  | 143 | 3 | 0
312 | - |  | 0 | Yes | 936 | 21 | 21
313 | - |  | 0 |  | 984 | 22 | 0
314 | - |  | 0 |  | 768 | 17 | 0
315 | - |  | 0 |  | 360 | 8 | 0
316 | - |  | 0 |  | 720 | 16 | 0
317 | - |  | 0 | Yes | 720 | 16 | 16
318 | - |  | 0 |  | 744 | 16 | 0
320 | - |  | 0 |  | 816 | 18 | 0
321 | - |  | 0 |  | 768 | 17 | 0
322 | - |  | 0 |  | 768 | 17 | 0
323 | - |  | 0 |  | 768 | 17 | 0
324 | - |  | 0 | Yes | 768 | 17 | 17
325 | - |  | 0 |  | 816 | 18 | 0
326 | - |  | 0 |  | 638 | 14 | 0
- | Main Office |  | 0 | Yes | 468 | 10 | 10
- | Nurse Office |  | 0 | Yes | 144 | 3 | 3
- | Auditorium |  | 0 |  | 1944 | 44 | 0
- | Girls Lunchroom |  | 0 |  | 2173 | 49 | 0
- | Girls Gym |  | 0 |  | 1419 | 32 | 0
- | Boy's Lunchroom |  | 0 |  | 2173 | 49 | 0
- | Boy's Gym |  | 0 |  | 1419 | 32 | 0

## Harrington
Sheet Last Modified: | 2021-04-21
School: | Avery D. Harrington Elementary-Middle School
Vendor: | EMCOR Fluidics | Devine Retest
EMCOR Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B1 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | House Fan
B2 | Classroom | 0 | 0 | Yes | 594 | 13 | 13 | House Fan
B3 | Classroom | 530 | 35 |  | 1122 | 25 | 25 | Unit Ventilator
B4 | B4 | 295 | 19 |  | 1064 | 24 | 19 | Unit Ventilator
B5 | Classroom | 299 | 19 |  | 910 | 20 | 19 | Unit Ventilator
B6 | - | 363 | 24 |  | 812 | 18 | 18 | Unit Ventilator
B8 | Classroom | 0 | 0 | Yes | 651 | 14 | 0 | House Fan
B9 | - |  | 0 | Yes | 600 | 13 | 13
10A | Classroom |  | 0 | Yes | 253 | 5
101 | Classroom | 0 | 0 | Yes | 968 | 22 | 22 | House Fan
102 | Teachers Lounge |  | 0 |  | 216 | 4 | 0 | House Fan
103 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
104 | Classroom |  | 0 | Yes | 840 | 19 | 19 | House Fan
106 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan
107 | Classroom | 0 | 0 | Yes | 725 | 16 | 16 | House Fan
108 | Classroom | 0 | 0 | Yes | 750 | 17 | 17 | House Fan
109 | Classroom | 651 | 43 |  | 1120 | 25 | 25 | Unit Ventilator
109A | Classroom |  | 0 | Yes | 168 | 3
109B | Classroom |  | 0 | Yes | 170 | 3
201 | Classroom |  | 0 | Yes | 775 | 17 | 17 | House Fan
202 | Classroom |  | 0 | Yes | 750 | 17 | 17 | House Fan
203 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan
203a | Asst Princ Office |  | 0 | Yes | 403 | 9 | 9 | House Fan
204 | Classroom |  | 0 | Yes | 900 | 20 | 20 | House Fan
205 | Classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan
206 | Classroom |  | 0 | Yes | 840 | 19 | 19 | House Fan
207 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
208 | Classroom |  | 0 | Yes | 696 | 15 | 15 | House Fan
301 | Classroom |  | 0 | Yes | 900 | 20 | 20 | House Fan
302 | Classroom |  | 0 | Yes | 780 | 17 | 17 | House Fan
303 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan
303a | Counselor Office |  | 0 | Yes | 403 | 9 | 9 | House Fan
304 | Classroom |  | 0 | Yes | 930 | 21 | 21 | House Fan
305 | Classroom |  | 0 | Yes | 810 | 18 | 18 | House Fan
306 | Classroom |  | 0 | Yes | 870 | 19 | 19 | House Fan
307 | Classroom |  | 0 | Yes | 725 | 16 | 16 | House Fan
308 | Classroom |  | 0 | Yes | 754 | 17 | 17 | House Fan
- | Library | 1190 | 79 |  | 3822 | 86 | 79 | Unit Ventilator
- | Auditorium | 130 | 8 |  | 90 | 2 | 2 | AHU
- | Gym |  | 0 |  | 2760 | 62 | 0
- | Gym / Storeroom | 0 | 0 |  | 513 | 11 | 0 | AHU
| Kitchen |  | 0 | Yes | 120 | 2
- | Nurse Office |  | 0 | Yes | 190 | 4 | 4 | House Fan
- | Main Office |  | 0 | Yes | 420 | 9 | 9 | House Fan
- | Principal Office |  | 0 | Yes | 377 | 8 | 8 | House Fan

## Hartranft
Sheet Last Modified: | 2021-04-06
School: | John F. Hartranft Elementary-Middle School
Vendor: | Devine Brothers | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 560 | 37 |  | 1519 | 34 | 34 | Unit Ventilator
100A | Office | 0 | 0 |  | 108 | 2 | 0 | AHU
100C | Office |  | 0 | Yes | 144 | 3 | 3
100E | Office | 0 | 0 |  | 304 | 6 | 0 | AHU
100G | Office |  | 0 | Yes | 304 | 6 | 6 | AHU
100J | Office | 0 | 0 | Yes | 77 | 1 | 1 | AHU
101 | Classroom | 310 | 20 |  | 840 | 19 | 19 | Unit Ventilator
102 | Classroom | 309 | 20 | Yes | 1302 | 29 | 29 | Unit Ventilator
103 | Classroom | 344 | 22 | Yes | 1302 | 29 | 29 | Unit Ventilator
104 | Classroom | 440 | 29 |  | 1178 | 26 | 26 | Unit Ventilator
105 | Classroom | 348 | 23 |  | 1178 | 26 | 23 | Unit Ventilator
106 | Classroom | 258 | 17 | Yes | 1302 | 29 | 29 | Unit Ventilator
107 | Classroom | 488 | 32 |  | 1302 | 29 | 29 | Unit Ventilator
108 | Classroom | 346 | 23 |  | 1178 | 26 | 23 | Unit Ventilator
109 | Classroom | 226 | 15 | Yes | 1178 | 26 | 26 | Unit Ventilator
110 | Classroom | 277 | 18 | Yes | 1302 | 29 | 29 | Unit Ventilator
111 | Classroom | 519 | 34 |  | 966 | 21 | 21 | Unit Ventilator
112 | Classroom | 500 | 33 |  | 1302 | 29 | 29 | Unit Ventilator
113 | Classroom | 485 | 32 |  | 874 | 19 | 19 | Unit Ventilator
114 | Classroom | 407 | 27 |  | 950 | 21 | 21 | Unit Ventilator
115 | Classroom | 316 | 21 | Yes | 1305 | 29 | 29 | Unit Ventilator
116 | Classroom | 261 | 17 | Yes | 1305 | 29 | 29 | Unit Ventilator
117 | Classroom | 313 | 20 | Yes | 1305 | 29 | 29 | Unit Ventilator
118 | Classroom | 473 | 31 |  | 1305 | 29 | 29 | Unit Ventilator
118A | Classroom | 12 | 0 | Yes | 680 | 15 | 15 | AHU
121 | Classroom | 55 | 3 | Yes | 792 | 18 | 18 | AHU
121 | Backroom | 59 | 3 |  | 310 | 7 | 3 | AHU
200 | Classroom | 368 | 24 | Yes | 1462 | 33 | 33 | Unit Ventilator
201 | Classroom | 647 | 43 |  | 1178 | 26 | 26 | Unit Ventilator
202 | Classroom | 454 | 30 |  | 1302 | 29 | 29 | Unit Ventilator
203 | Classroom | 355 | 23 | Yes | 1302 | 29 | 29 | Unit Ventilator
204 | Classroom | 258 | 17 | Yes | 1178 | 26 | 26 | Unit Ventilator
205 | Classroom | 491 | 32 |  | 1178 | 26 | 26 | Unit Ventilator
206 | Classroom | 282 | 18 | Yes | 1302 | 29 | 29 | Unit Ventilator
207 | Classroom | 225 | 15 | Yes | 1302 | 29 | 29 | Unit Ventilator
208 | Classroom | 247 | 16 | Yes | 1179 | 26 | 26 | Unit Ventilator
209 | Classroom | 274 | 18 | Yes | 1179 | 26 | 26 | Unit Ventilator
210 | Classroom | 485 | 32 |  | 1302 | 29 | 29 | Unit Ventilator
211 | Classroom | 519 | 34 |  | 1302 | 29 | 29 | Unit Ventilator
212 | Classroom | 309 | 20 | Yes | 1178 | 26 | 26 | Unit Ventilator
214 | Classroom | 325 | 21 |  | 782 | 17 | 17 | Unit Ventilator
- | Cafeteria | 2300 | 153 |  | 1593 | 36 | 36 | AHU
- | Cafeteria Entrance Hallway | 0 | 0 |  | 730 | 16 | 0 | AHU
- | Conference/Office | 0 | 0 |  | 304 | 6 | 0 | AHU
- | Engineer Office | 0 | 0 |  | 112 | 2 | 0 | AHU
- | Engineer Breakroom | 0 | 0 |  | 99 | 2 | 0 | AHU
- | Gym | 3499 | 233 |  | 6160 | 140 | 140 | AHU
- | Kitchen | 0 | 0 |  | 864 | 19 | 0 | AHU
- | Main Office | 0 | 0 | Yes | 1056 | 24 | 24 | AHU
- | Nurse Office | 0 | 0 | Yes | 425 | 9 | 9 | AHU
- | Principal Office | 0 | 0 | Yes | 228 | 5 | 5 | AHU
- | Rear Entrance Hallway | 0 | 0 |  | 736 | 16 | 0 | AHU
- | Teacher Office | 0 | 0 |  | 77 | 1 | 0 | AHU

## Haverford Child Center
Sheet Last Modified: | 2021-04-23
School: | Haverford Child Development Center
Vendor: | Devine Brothers | Devine Brothers Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
2 | Classroom | 291 | 19 | Yes | 1058 | 24 | 24 | RTU
3 | Classroom | 323 | 21 | Yes | 1058 | 24 | 24 | RTU
4 | Classroom | 277 | 18 | Yes | 1058 | 24 | 24 | RTU
5 | Classroom | 374 | 24 |  | 1058 | 24 | 24 | RTU
5A | Office | 15 | 1 |  | 170 | 3 | 1 | RTU
6 | Conference | 418 | 27 |  | 621 | 14 | 14 | RTU
7 | Conference | 415 | 27 |  | 621 | 14 | 14 | RTU
8 | Classroom | 287 | 19 |  | 560 | 12 | 12 | RTU
8A | Office | 336 | 22 |  | 210 | 4 | 4 | RTU
9 | Classroom | 723 | 48 |  | 962 | 21 | 21 | RTU
10A | Lounge | 34 | 2 |  | 216 | 4 | 2 | RTU
10B | Book Storage | 11 | 0 |  | 288 | 6 | 0 | RTU
- | Gym | 1065 | 71 |  | 2204 | 50 | 50 | RTU
- | Lobby | 18 | 1 |  | 608 | 13 | 1 | RTU
- | Storage | 89 | 5 |  | 572 | 13 | 5 | RTU
- | BE Office | 18 | 1 |  | 128 | 2 | 1 | RTU

## Henry
Sheet Last Modified: | 2021-04-05
School: | Charles W. Henry Elementary School
Vendor: | Devine | Devine Part 2 | Devine Part 3 | Devine Part 4
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 0 | 0 | Yes | 649.9 | 14 | 14 | Unit Ventilator
102 | Classroom | 443 | 29 |  | 837 | 19 | 19 | Unit Ventilator
103 | Classroom | 371 | 24 |  | 817.15 | 18 | 18 | Unit Ventilator
104 | Classroom | 374 | 24 |  | 818 | 18 | 18 | Unit Ventilator
104A | Office | 0 | 0 | Yes | 57 | 1 | 1
105 | Classroom | 397 | 26 |  | 950.7 | 21 | 21 | Unit Ventilator
106 | Classroom | 308 | 20 |  | 815.2 | 18 | 18 | Unit Ventilator
108 | Classroom | 481 | 32 |  | 649.9 | 14 | 14 | Unit Ventilator
109 | Classroom | 763 | 50 |  | 712.2 | 16 | 16 | Unit Ventilator
110 | Classroom | 756 | 50 |  | 649.9 | 14 | 14 | Unit Ventilator
110A | Office | 0 | 0 | Yes | 98 | 2 | 2
114 | Classroom | 773 | 51 |  | 749 | 17 | 17
201 | Classroom | 289 | 19 |  | 775.4 | 17 | 17 | Unit Ventilator
202 | Classroom | 314 | 20 |  | 765.3 | 17 | 17 | Unit Ventilator
203 | Classroom | 282 | 18 |  | 781.4 | 17 | 17 | Unit Ventilator
203A | Office | 0 | 0 | Yes | 115 | 2 | 2
204 | Classroom | 262 | 17 | Yes | 847.2 | 19 | 19 | Unit Ventilator
206 | Classroom | 285 | 19 |  | 545.6 | 12 | 12 | Unit Ventilator
207 | Classroom | 273 | 18 |  | 815.2 | 18 | 18 | Unit Ventilator
208 | Classroom | 265 | 17 |  | 787.4 | 17 | 17 | Unit Ventilator
208A | Office | 0 | 0 | Yes | 170 | 3 | 3
209 | Classroom | 0 | 0 | Yes | 799.5 | 18 | 18 | Unit Ventilator
210 | Classroom | 398 | 26 |  | 946 | 21 | 21 | Unit Ventilator
214 | Classroom | 282 | 18 | Yes | 1736 | 39 | 39 | Unit Ventilator
215 | Classroom | 387 | 25 |  | 1127.8 | 25 | 25 | Unit Ventilator
216 | Classroom | 284 | 18 |  | 546 | 12 | 12 | Unit Ventilator
217 | Classroom | 393 | 26 |  | 544 | 12 | 12 | Unit Ventilator
218 | Classroom | 307 | 20 | Yes | 1023 | 23 | 23 | Unit Ventilator
- | Art Classroom | 249 | 16 |  | 777.5 | 17 | 16 | Unit Ventilator
- | Auditorium | 1908 | 127 |  | 2417 | 54 | 54 | Unit Ventilator
- | Cafe | 0 | 0 | Yes | 2104 | 47 | 47 | Unit Ventilator
- | Gym | 1076 | 71 | Yes | 3199 | 72 | 72 | Unit Ventilator
- | Janitor Office | 0 | 0 |  |  | 0 | 0 | N/A
- | Music Classroom | 292 | 19 |  | 833 | 18 | 18 | Unit Ventilator
- | Sensory Classroom | 0 | 0 | Yes | 377 | 8 | 8 | Unit Ventilator
- | Counselor's Office | 0 | 0 |  | 299 | 6 | 0
- | Nurse's Office | 0 | 0 | Yes | 263 | 5 | 5
- | Medical Waiting Room | 0 | 0 | Yes | 177 | 4 | 4
- | Principal's Office | 0 | 0 | Yes | 307 | 6 | 6

## Heston
Sheet Last Modified: | 2021-04-16
School: | Edward Heston Elementary School
Vendor: | Devine Brothers | Devine Brothers 2nd Retest
Devine Brothers 3rd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 148 | 9 |  | 440 | 10 | 9 | AHU
102 | Office | 44 | 2 |  | 180 | 4 | 2 | AHU
103 | Classroom | 70 | 4 |  | 308 | 7 | 4 | AHU
103B | Office | 53 | 3 |  | 418 | 9 | 3 | AHU
104 | Vestible | 25 | 1 |  | 220 | 5 | 1 | Unit Ventilator
104A | Office | 36 | 2 |  | 102 | 2 | 2 | AHU
104B | Security Office | 56 | 3 |  | 123 | 2 | 2 | AHU
104C | Office | 27 | 1 |  | 99 | 2 | 1 | AHU
106 | Classroom | 328 | 21 | Yes | 1540 | 35 | 35 | Unit Ventilator
107 | Classroom | 35 | 2 | Yes | 440 | 10 | 10 | AHU
107A | Office | 74 | 4 |  | 840 | 19 | 4 | AHU
107B | Storage | 17 | 1 |  | 196 | 4 | 1 | AHU
108 | Classroom | 296 | 19 | Yes | 1540 | 35 | 35 | Unit Ventilator
109 | Classroom | 275 | 18 |  | 440 | 10 | 10 | AHU
110 | Classroom | 322 | 21 | Yes | 1056 | 24 | 24 | Unit Ventilator
112 | Classroom | 312 | 20 |  | 836 | 19 | 19 | Unit Ventilator
114 | Classroom | 276 | 18 |  | 1012 | 23 | 18 | Unit Ventilator
116 | Classroom | 279 | 18 | Yes | 968 | 22 | 22 | Unit Ventilator
127 | Kitchen | 169 | 11 |  | 972 | 22 | 11 | AHU
200 | Classroom | 296 | 19 |  | 264 | 6 | 6 | Unit Ventilator
202 | Classroom | 276 | 18 |  | 704 | 16 | 16 | Unit Ventilator
204 | Classroom | 316 | 21 |  | 396 | 9 | 9 | Unit Ventilator
206 | Classroom | 317 | 21 |  | 704 | 16 | 16 | Unit Ventilator
208 | Classroom | 281 | 18 |  | 748 | 17 | 17 | Unit Ventilator
210 | Classroom | 318 | 21 |  | 528 | 12 | 12 | Unit Ventilator
212 | Classroom | 329 | 21 |  | 748 | 17 | 17 | Unit Ventilator
214 | Classroom | 318 | 21 |  | 748 | 17 | 17 | Unit Ventilator
216 | Classroom | 270 | 18 |  | 748 | 17 | 17 | Unit Ventilator
218 | Classroom | 291 | 19 |  | 748 | 17 | 17 | Unit Ventilator
220 | Classroom | 424 | 28 |  | 748 | 17 | 17 | AHU
222 | Classroom | 289 | 19 |  | 748 | 17 | 17 | Unit Ventilator
224 | Classroom | 284 | 18 |  | 792 | 18 | 18 | Unit Ventilator
228 | Room | 55 | 3 | Yes | 264 | 6 | 6 | Unit Ventilator
232 | Classroom | 285 | 19 |  | 264 | 6 | 6 | Unit Ventilator
300 | Lounge | 347 | 23 |  | 264 | 6 | 6 | Unit Ventilator
301 | Classroom | 175 | 11 | Yes | 1568 | 35 | 35 | AHU
302 | Classroom | 291 | 19 |  | 704 | 16 | 16 | Unit Ventilator
304 | Classroom | 284 | 18 |  | 748 | 17 | 17 | Unit Ventilator
306 | Classroom | 327 | 21 |  | 748 | 17 | 17 | Unit Ventilator
308 | Classroom | 321 | 21 |  | 704 | 16 | 16 | Unit Ventilator
310 | Room | 0 | 0 | Yes | 748 | 17 | 17 | Unit Ventilator
312 | Classroom | 289 | 19 |  | 748 | 17 | 17 | Unit Ventilator
314 | Room | 53 | 3 | Yes | 792 | 18 | 18 | Unit Ventilator
316 | Classroom | 290 | 19 |  | 792 | 18 | 18 | Unit Ventilator
318 | Room | 0 | 0 | Yes | 748 | 17 | 17 | Unit Ventilator
320 | Classroom | 303 | 20 |  | 748 | 17 | 17 | Unit Ventilator
322 | Room | 249 | 16 |  | 748 | 17 | 16 | Unit Ventilator
324 | Classroom | 302 | 20 |  | 748 | 17 | 17 | Unit Ventilator
328 | Classroom | 298 | 19 |  | 264 | 6 | 6 | Unit Ventilator
- | Copy Room | 38 | 2 |  | 44 | 1 | 1 | Unit Ventilator
- | Main office | 78 | 5 | Yes | 484 | 11 | 11 | Unit Ventilator
- | Nurse | 30 | 2 |  | 176 | 4 | 2 | Unit Ventilator
- | Nurse Examination | 76 | 5 |  | 88 | 2 | 2 | Unit Ventilator
- | Principal | 43 | 2 |  | 176 | 4 | 2 | Unit Ventilator
- | Cafeteria/Aud | 4461 | 297 |  | 4268 | 97 | 97 | AHU
- | Gym | 2645 | 176 |  | 4620 | 105 | 105 | AHU
- | IMC | 1002 | 66 |  | 2948 | 67 | 66 | AHU
- | IMC/Classrooms | 58 | 3 |  | 176 | 4 | 3 | AHU
- | Teachers Lounge | 52 | 3 | Yes | 296 | 6 | 6 | AHU
- | Dean's Office | 31 | 2 |  | 117 | 2 | 2 | AHU

## Hill-Freedman @ Leeds
Sheet Last Modified: | 2021-04-23
School: | Hill-Freedman World Academy at Leeds Campus
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Room |  | 0 |  | 775 | 17 | 0
2 | Room |  | 0 |  | 1008 | 22 | 0
3 | Room | 0 | 0 |  | 832 | 18 | 0
4 | Room |  | 0 |  | 784 | 17 | 0
5 | Office |  | 0 |  | 240 | 5 | 0
5 | Room |  | 0 |  | 1300 | 29 | 0
6 | Office |  | 0 |  | 64 | 1 | 0
6 | Room | 0 | 0 |  | 300 | 6 | 0
7 | Room | 0 | 0 |  | 672 | 15 | 0
8 | Room |  | 0 |  | 500 | 11 | 0
9 | Room |  | 0 |  | 1300 | 29 | 0
10 | Room |  | 0 |  | 840 | 19 | 0
119 | Classroom |  | 0 | Yes | 504 | 11 | 11
121 | Classroom |  | 0 | Yes | 525 | 11 | 11
124 | Classroom |  | 0 | Yes | 616 | 14 | 14
131 | Classroom |  | 0 | Yes | 735 | 16 | 16
134 | Classroom |  | 0 | Yes | 1224 | 27 | 27
- | Auditorium |  | 0 |  | 8760 | 199 | 0
Main Office | Office |  | 0 |  | 588 | 13 | 0
Principal | Office |  | 0 |  | 154 | 3 | 0
Nurse | Office Suite |  | 0 | Yes | 892 | 20 | 20
- | Boys Gym | 1074 | 71 |  | 5760 | 130 | 71
- | Boys Locker Room |  | 0 |  | 3420 | 77 | 0
- | Cafeteria |  | 0 |  | 11360 | 258 | 0
- | Conference Room |  | 0 |  | 390 | 8 | 0
- | Girls Gym |  | 0 |  | 5760 | 130 | 0
- | Girls Locker Room |  | 0 |  | 3420 | 77 | 0

## Holme
Sheet Last Modified: | 2021-04-28
School: | Thomas Holme Elementary School
Vendor: | Devine Brothers | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 619 | 41 |  | 989 | 22 | 22 | Unit Ventilator
2 | Classroom | 524 | 34 |  | 989 | 22 | 22 | Unit Ventilator
3 | Classroom | 285 | 19 |  | 920 | 20 | 19 | Unit Ventilator
4 | Classroom | 576 | 38 |  | 1058 | 24 | 24 | Unit Ventilator
5 | Classroom | 550 | 36 |  | 1058 | 24 | 24 | Unit Ventilator
61 | Classroom | 214 | 14 | Yes | 1040 | 23 | 23 | Unit Ventilator
62 | Truancy Court | 207 | 13 | Yes | 520 | 11 | 11 | Unit Ventilator
63 | Classroom | 312 | 20 | Yes | 1040 | 23 | 23 | Unit Ventilator
64 | Classroom | 527 | 35 |  | 1040 | 23 | 23 | Unit Ventilator
65 | Classroom | 300 | 20 | Yes | 1040 | 23 | 23 | Unit Ventilator
66 | Classroom | 423 | 28 |  | 1040 | 23 | 23 | Unit Ventilator
101 | Classroom | 679 | 45 |  | 920 | 20 | 20 | Unit Ventilator
102 | Classroom | 626 | 41 |  | 920 | 20 | 20 | Unit Ventilator
103 | Classroom | 500 | 33 |  | 920 | 20 | 20 | Unit Ventilator
104 | Classroom | 615 | 41 |  | 920 | 20 | 20 | Unit Ventilator
105 | Classroom | 628 | 41 |  | 920 | 20 | 20 | Unit Ventilator
106 | Classroom | 697 | 46 |  | 690 | 15 | 15 | Unit Ventilator
107 | Classroom | 321 | 21 |  | 960 | 21 | 21 | Unit Ventilator
108 | Classroom |  | 0 | Yes | 108 | 2 | 2
109 | Classroom | 503 | 33 |  | 920 | 20 | 20 | Unit Ventilator
110 | Classroom | 483 | 32 |  | 920 | 20 | 20 | Unit Ventilator
111 | Classroom | 553 | 36 |  | 920 | 20 | 20 | Unit Ventilator
112 | Classroom | 568 | 37 |  | 920 | 20 | 20 | Unit Ventilator
113 | Classroom | 622 | 41 |  | 920 | 20 | 20 | Unit Ventilator
201 | Classroom | 649 | 43 |  | 920 | 20 | 20 | Unit Ventilator
202 | Classroom | 320 | 21 |  | 920 | 20 | 20 | Unit Ventilator
203 | Classroom | 261 | 17 |  | 920 | 20 | 17 | Unit Ventilator
204 | Classroom | 469 | 31 |  | 920 | 20 | 20 | Unit Ventilator
205 | Classroom | 658 | 43 |  | 920 | 20 | 20 | Unit Ventilator
206 | Classroom | 624 | 41 |  | 920 | 20 | 20 | Unit Ventilator
207 | Classroom | 607 | 40 |  | 920 | 20 | 20 | Unit Ventilator
208 | Classroom | 626 | 41 |  | 920 | 20 | 20 | Unit Ventilator
209 | Classroom | 764 | 50 |  | 920 | 20 | 20 | Unit Ventilator
210 | Classroom | 589 | 39 |  | 920 | 20 | 20 | Unit Ventilator
211 | Classroom | 279 | 18 |  | 920 | 20 | 18 | Unit Ventilator
212 | Classroom | 597 | 39 |  | 920 | 20 | 20 | Unit Ventilator
213 | Classroom | 664 | 44 |  | 920 | 20 | 20 | Unit Ventilator
214 | Classroom | 681 | 45 |  | 920 | 20 | 20 | Unit Ventilator
215 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator
216 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator
- | Auditorium | 0 | 0 |  | 2880 | 65 | 0 | AHU
- | Cafeteria | 127 | 8 |  | 2250 | 51 | 8 | Unit Ventilator
- | Kitchen |  | 0 | Yes | 475 | 10 | 10
- | Main Office |  | 0 | Yes | 231 | 5 | 5 | Purifier
- | Principal Office |  | 0 | Yes | 150 | 3 | 3
- | Vice Principal Office |  | 0 | Yes | 84 | 1 | 1
- | Nurse Office |  | 0 | Yes | 204 | 4 | 4
- | Counselor Office |  | 0 | Yes | 135 | 3 | 3
- | Admin Office |  | 0 | Yes | 156 | 3 | 3
- | Dean Office |  | 0 | Yes | 140 | 3 | 3
- | School Police Office |  | 0 | Yes | 99 | 2 | 2
- | Gym | 189 | 12 | Yes | 3950 | 89 | 89 | Unit Ventilator
- | Music | 0 | 0 |  | 2340 | 53 | 0 | AHU

## Hopkinson
Sheet Last Modified: | 2021-04-23
School: | Francis Hopkinson Elementary School
Vendor: | Devine Brothers | Main Building Retest
School: | Francis Hopkinson Elementary School- Little School House
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
101 | Classrooms | 1030 | 68 |  | 687 | 15 | 15 | House Fan
102 | Classrooms | 873 | 58 |  | 627 | 14 | 14 | House Fan
103 | Classrooms | 276 | 18 |  | 696 | 15 | 15 | House Fan
104 | Classrooms | 1044 | 69 |  | 643 | 14 | 14 | House Fan
105 | Classrooms | 562 | 37 |  | 638 | 14 | 14 | House Fan
106 | Classroom | 953 | 63 |  | 648 | 14 | 14 | House Fan
107 | Classroom | 1035 | 69 |  | 638 | 14 | 14 | House Fan
108 | Classrooms | 432 | 28 |  | 675 | 15 | 15 | House Fan
109 | Classrooms | 635 | 42 |  | 631 | 14 | 14 | House Fan
110 | Classroom | 322 | 21 |  | 695 | 15 | 15 | House Fan
201 | Classrooms | 707 | 47 |  | 696 | 15 | 15 | House Fan
202 | Classroom | 767 | 51 |  | 656 | 14 | 14 | House Fan
203 | Classrooms | 734 | 48 |  | 693 | 15 | 15 | House Fan
204 | Classrooms | 787 | 52 |  | 647 | 14 | 14 | House Fan
205 | Classroom | 737 | 49 |  | 674 | 15 | 15 | House Fan
206 | Classroom | 792 | 52 |  | 657 | 14 | 14 | House Fan
207 | Classrooms | 618 | 41 |  | 679 | 15 | 15 | House Fan
208 | Classroom | 702 | 46 |  | 686 | 15 | 15 | House Fan
209 | Classroom | 892 | 59 |  | 667 | 15 | 15 | House Fan
210 | Classroom | 386 | 25 |  | 687 | 15 | 15 | House Fan
300 | Office |  | 0 | Yes | 275 | 6 | 6 | House Fan
301 | Classrooms | 425 | 28 |  | 677 | 15 | 15 | House Fan
302 | Classroom | 0 | 0 | Yes | 668 | 15 | 15 | House Fan
303 | Classrooms | 263 | 17 |  | 694 | 15 | 15 | House Fan
304 | Classrooms | 612 | 40 |  | 614 | 13 | 13 | House Fan
305 | Classroom | 437 | 29 |  | 672 | 15 | 15 | House Fan
306 | Classroom | 497 | 33 |  | 696 | 15 | 15 | House Fan
307 | Classrooms | 1017 | 67 |  | 661 | 15 | 15 | House Fan
308 | Classroom | 604 | 40 |  | 664 | 15 | 15 | House Fan
309 | Classroom | 702 | 46 |  | 673 | 15 | 15 | House Fan
310 | Classroom | 321 | 21 |  | 668 | 15 | 15 | House Fan
311 | Classrooms | 393 | 26 |  | 638 | 14 | 14 | House Fan
- | Auditorium | 1307 | 87 |  | 3184 | 72 | 72 | House Fan
- | B Art Room | 242 | 16 |  | 570 | 12 | 12 | House Fan
- | B Café / Gym | 0 | 0 | Yes | 3572 | 81 | 81 | N/A
- | B ESOL Room | 269 | 17 |  | 683 | 15 | 15 | House Fan
- | B Music Room | 603 | 40 |  | 688 | 15 | 15 | House Fan
- | B Science Room | 864 | 57 |  | 704 | 16 | 16 | House Fan
- | Main Office |  | 0 | Yes | 345 | 7 | 7
- | Vice Principal's Office |  | 0 | Yes | 126 | 2 | 2
- | Nurse Office |  | 0 | Yes | 275 | 6 | 6
P1 | Classroom | 198 | 13 | Yes | 1184 | 26 | 26 | Unit Ventilator
P2 | Classroom | 348 | 23 |  | 747 | 16 | 16 | Unit Ventilator
Hopkinson LSH
1 | Room | 308 | 20 |  | 877 | 19 | 19 | AHU
2 | Room | 323 | 21 |  | 900 | 20 | 20 | AHU
3 | Room | 318 | 21 |  | 885 | 20 | 20 | AHU
4 | Room | 349 | 23 |  | 908 | 20 | 20 | AHU
5 | Room | 308 | 20 |  | 863 | 19 | 19 | AHU
6 | Room | 256 | 17 | Yes | 876 | 19 | 19 | AHU
- | Corridor and Bathrooms | 46 | 3 |  |  | 0 | 0 | AHU
- | Multi-Purpose Room | 626 | 41 |  | 2003 | 45 | 41 | AHU
- | Office Area | 204 | 13 |  | 352 | 8 | 8 | AHU

## Houston
Sheet Last Modified: | 2021-04-01
School: | Henry H. Houston Elementary School
Vendor: | EMCOR | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 783.52 | 17 | 17 | House Fan
102 | Classroom |  | 0 | Yes | 650.78 | 14 | 14 | House Fan
103 | Classroom |  | 0 | Yes | 664.07 | 15 | 15 | House Fan
103A | Classroom |  | 0 |  | 157 | 3 | 0 | House Fan
104 | Classroom |  | 0 | Yes | 675.28 | 15 | 15 | House Fan
105 | Office/Principal |  | 0 |  | 354 | 8 | 0 | House Fan
106 | Classroom |  | 0 | Yes | 651.15 | 14 | 14 | House Fan
107 | Classroom |  | 0 | Yes | 458.77 | 10 | 10 | House Fan
108 | Classroom |  | 0 | Yes | 681.17 | 15 | 15 | House Fan
109 | Classroom |  | 0 | Yes | 950.26 | 21 | 21 | House Fan
111 | Classroom | 276 | 18 |  | 374.67 | 8 | 8 | House Fan and Univent
112 | Classroom | 350 | 23 |  | 312.08 | 7 | 7 | House Fan and Univent
201 | Classroom |  | 0 |  | 561 | 12 | 0 | House Fan
202 | Classroom |  | 0 |  | 701 | 15 | 0 | House Fan
203 | Classroom |  | 0 |  | 207 | 4 | 0 | House Fan
204 | Classroom |  | 0 |  | 710 | 16 | 0 | House Fan
205 | Classroom |  | 0 |  | 653 | 14 | 0 | House Fan
206 | Classroom |  | 0 |  | 660 | 15 | 0 | House Fan
207 | Classroom |  | 0 |  | 769 | 17 | 0 | House Fan
208 | Classroom |  | 0 |  | 750 | 17 | 0 | House Fan
209 | Classroom |  | 0 |  | 693 | 15 | 0 | House Fan
210 | Classroom |  | 0 |  | 437 | 9 | 0 | N/A
211 | Classroom | 329 | 21 |  | 795 | 18 | 18 | Unit Ventilator
212 | Classroom | 309 | 20 |  | 396 | 9 | 9 | Unit Ventilator
213 | Classroom | 274 | 18 |  |  | 0 | 0 | Unit Ventilator
301 | Classroom |  | 0 |  | 666.85 | 15 | 0 | House Fan
302 | Classroom |  | 0 | Yes | 660.81 | 15 | 15 | House Fan
303 | Classroom |  | 0 |  | 664.04 | 15 | 0 | House Fan
304 | Classroom |  | 0 |  | 728.5 | 16 | 0 | House Fan
305 | Classroom |  | 0 |  | 673.65 | 15 | 0 | House Fan
306 | Classroom |  | 0 |  | 669.78 | 15 | 0 | House Fan
307 | Classroom |  | 0 |  | 757.88 | 17 | 0 | House Fan
308 | Classroom |  | 0 |  | 715.92 | 16 | 0 | House Fan
309 | Classroom |  | 0 |  | 612.5 | 13 | 0 | House Fan
309A | Small Office |  | 0 |  | 201 | 4 | 0 | House Fan
- | Kitchen | 0 | 0 |  | 638 | 14 | 0 | N/A
- | Auditorium | 1853 | 123 |  | 1500 | 34 | 34 | AHU 1 and 2
- | Library | 0 | 0 |  | 1404 | 31 | 0 | RTU
- | Gym |  | 0 | Yes | 2231.81 | 50 | 50 | N/A
- | Old Art Room |  | 0 |  | 630.75 | 14 | 0 | N/A
- | Cafeteria | 0 | 0 |  | 4500.2 | 102 | 0 | Nesbitt Unit Ventilator
- | Old School Store A | 230 | 15 |  | 863 | 19 | 15 | Nesbitt Unit Ventilator
- | Old School Store B | 345 | 23 |  | 311 | 7 | 7 | Nesbitt Unit Ventilator
- | New School Store | 347 | 23 |  | 291 | 6 | 6 | Nesbitt Unit Ventilator
- | Medical Suite Large |  | 0 |  | 242 | 5
- | Medical Suite Small |  | 0 |  | 126 | 2
- | Medical Suite Medium |  | 0 |  | 238 | 5 | 0 | House Fan

## Howe
Sheet Last Modified: | 2021-04-21
School: | Julia Ward Howe Academics Plus Elementary School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B-1 | Art | 751 | 50 |  | 754 | 17 | 17 | House Fan
1 | Classroom | 1269 | 84 |  | 690 | 15 | 15 | House Fan
2 | Classroom | 1240 | 82 |  | 690 | 15 | 15 | House Fan
3 | Classroom | 344 | 22 |  | 690 | 15 | 15 | House Fan
4 | Classroom | 455 | 30 |  | 690 | 15 | 15 | House Fan
5 | Classroom | 1500 | 100 |  | 196 | 4 | 4 | House Fan
6 | Classroom | 479 | 31 |  | 713 | 16 | 16 | House Fan
7 | Classroom | 1470 | 98 |  | 690 | 15 | 15 | House Fan
8 | Classroom | 1454 | 96 |  | 690 | 15 | 15 | House Fan
9 | Classroom | 564 | 37 |  | 720 | 16 | 16 | House Fan
10 | Classroom | 1739 | 115 |  | 690 | 15 | 15 | House Fan
11 | Classroom | 628 | 41 |  | 690 | 15 | 15 | House Fan
12 | Classroom | 829 | 55 |  | 720 | 16 | 16 | House Fan
13 | Library | 0 | 0 |  | 720 | 16 | 0 | House Fan
14 | Classroom | 1302 | 86 |  | 690 | 15 | 15 | House Fan
15 | Classroom | 1044 | 69 |  | 690 | 15 | 15 | House Fan
16 | Computer Lab | 0 | 0 |  | 690 | 15 | 0 | House Fan
17 | Classroom | 548 | 36 |  | 690 | 15 | 15 | House Fan
18 | Classroom | 824 | 54 |  | 690 | 15 | 15 | House Fan
19 | Classroom | 869 | 57 |  | 690 | 15 | 15 | House Fan
20 | Classroom | 0 | 0 |  | 690 | 15 | 0 | House Fan
21 | Classroom | 149 | 9 | Yes | 690 | 15 | 15 | House Fan
22 | Classroom | 898 | 59 |  | 690 | 15 | 15 | House Fan
23 | Classroom | 210 | 14 |  | 690 | 15 | 14 | House Fan
23A | - |  | 0 | Yes | 91 | 2 | 2 | House Fan
24 | Classroom | 0 | 0 |  | 350 | 7 | 0 | House Fan
- | Cafeteria | 0 | 0 | Yes | 1566 | 35 | 35 | House Fan
- | Gym |  | 0 | Yes | 1060 | 24 | 24 | House Fan
- | Jugg Room |  | 0 |  | 195 | 4 | 0 | House Fan
- | Main Office |  | 0 |  | 238 | 5 | 0 | House Fan
- | Principals Office |  | 0 | Yes | 180 | 4 | 4 | House Fan
- | Counselors Office |  | 0 |  | 162 | 3 | 0 | House Fan
- | Psychologists Office |  | 0 | Yes | 99 | 2 | 2 | House Fan
- | Lounge |  | 0 |  | 266 | 6 | 0 | House Fan
- | Security |  | 0 | Yes | 91 | 2 | 2 | House Fan

## Hunter
Sheet Last Modified: | 2021-04-06
School: | New William H. Hunter Elementary School
Vendor: | Devine Brothers | Devine Retest
Devine 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Office | 40 | 2 |  | 149 | 3 | 2 | AHU-3
2 | Office | 33 | 2 |  | 143 | 3 | 2 | AHU-3
3 | Office | 24 | 1 |  | 72 | 1 | 1 | AHU-3
4 | Office | 48 | 3 |  | 92 | 2 | 2 | AHU-3
101A | Classroom | 363 | 24 |  | 695 | 15 | 15 | AHU-1
101B | Classroom | 378 | 25 |  | 695 | 15 | 15 | AHU-1 + UV
101C | Classroom | 358 | 23 |  | 650 | 14 | 14 | AHU-1
101D | Classroom | 551 | 36 |  | 650 | 14 | 14 | AHU-1 + UV
101E | Classroom | 351 | 23 |  | 610 | 13 | 13 | AHU-1
101F | Classroom | 393 | 26 |  | 650 | 14 | 14 | AHU-1 + UV
102 | Classroom | 375 | 25 |  | 410 | 9 | 9 | AHU-1 and UV
107 | Main Office Entry | 103 | 6 |  | 350 | 7 | 6 | AHU-3
107 | Main Office | 195 | 13 | Yes | 1125 | 25 | 25 | AHU-3
108 | Classroom | 666 | 44 |  | 715 | 16 | 16 | AHU-5 + UV
109 | Classroom | 497 | 33 |  | 695 | 15 | 15 | AHU-5 + UV
110 | Classroom | 477 | 31 |  | 695 | 15 | 15 | AHU-5 + UV
111 | Classroom | 632 | 42 |  | 695 | 15 | 15 | AHU-5 + UV
112 | Classroom | 496 | 33 |  | 695 | 15 | 15 | AHU-5 + UV
113 | Music Room | 456 | 30 |  | 1430 | 32 | 30 | AHU-7
113 | Practice Rm 1 | 23 | 1 |  | 72 | 1 | 1 | AHU-7
113 | Practice Rm 2 | 27 | 1 |  | 78 | 1 | 1 | AHU-7
201 | IMC | 1373 | 91 |  | 2995 | 68 | 68 | AHU-10 + UV
202 | Classroom | 467 | 31 |  | 1125 | 25 | 25 | Unit Ventilator and AHU
202 | Media | 0 | 0 | Yes | 385 | 8 | 8 | Unit Ventilator and AHU
BAS 205 | IMC - Reading Small Classroom | 303 | 20 |  | 102 | 2 | 2 | Tightened damper Actuator to the shaft
BAS 206 | IMC - Reading Small Classroom | 317 | 21 |  | 859 | 19 | 19 | Tightened damper Actuator to the shaft
206 | Classroom | 464 | 30 |  | 842 | 19 | 19 | AHU-1 + UV
207 | Classroom | 610 | 40 |  | 1325 | 30 | 30 | Unit Ventilator and AHU
208 | Classroom | 318 | 21 | Yes | 1395 | 31 | 31 | Unit Ventilator and AHU
208 | Computer Lab | 81 | 5 |  | 1210 | 27 | 5
209 | Classroom | 293 | 19 |  | 750 | 17 | 17 | AHU-1 + UV
210 | Classroom | 526 | 35 |  | 754 | 17 | 17 | Unit Ventilator and AHU
211 | Classroom | 551 | 36 |  | 754 | 17 | 17 | Unit Ventilator and AHU
212 | Classroom | 426 | 28 |  | 753 | 17 | 17 | Unit Ventilator and AHU
213 | Classroom | 497 | 33 |  | 753 | 17 | 17 | Unit Ventilator and AHU
214 | Classroom | 478 | 31 |  | 724 | 16 | 16 | Unit Ventilator and AHU
215 | Art Room | 367 | 24 | Yes | 1324 | 30 | 30 | AHU-12
304 | Classroom | 367 | 24 |  | 725 | 16 | 16 | Unit Ventilator and AHU
305 | Classroom | 431 | 28 |  | 754 | 17 | 17 | Unit Ventilator and AHU
306 | Classroom | 395 | 26 |  | 754 | 17 | 17 | Unit Ventilator and AHU
307 | Classroom | 315 | 21 |  | 753 | 17 | 17 | Unit Ventilator and AHU
308 | Classroom | 350 | 23 |  | 753 | 17 | 17 | Unit Ventilator and AHU
309 | Classroom | 340 | 22 |  | 754 | 17 | 17 | Unit Ventilator and AHU
310 | Classroom | 361 | 24 |  | 754 | 17 | 17 | Unit Ventilator and AHU
311 | Classroom | 317 | 21 |  | 753 | 17 | 17 | Unit Ventilator and AHU
312 | Classroom | 427 | 28 |  | 753 | 17 | 17 | Unit Ventilator and AHU
313 | Classroom | 387 | 25 |  | 754 | 17 | 17 | Unit Ventilator and AHU
314 | Classroom | 411 | 27 |  | 715 | 16 | 16 | Unit Ventilator and AHU
315 | Classroom | 363 | 24 |  | 810 | 18 | 18 | Unit Ventilator and AHU
- | Auditorium | 2966 | 197 |  | 2910 | 66 | 66 | AHU-6
- | Cafeteria | 2006 | 133 |  | 3590 | 81 | 81 | AHU
- | Kitchen | 35 | 2 | Yes | 1116 | 25 | 25 | AHU-3
- | Nurses Office | 98 | 6 |  | 105 | 2 | 2 | FC 5-1
- | Nurse Exam Room | 110 | 7 |  | 94 | 2 | 2 | FC 5-1
- | Nurses Waiting Room | 108 | 7 |  | 130 | 2 | 2 | FC 5-1
- | Principal Office | 74 | 4 | Yes | 322 | 7 | 7 | AHU-3
- | Conference Room | 147 | 9 |  | 429 | 9 | 9 | AHU-3
- | Gym | 1430 | 95 |  | 4969 | 112 | 95 | AHU-8 + AHU-9

## Jackson
Sheet Last Modified: | 2021-04-13
School: | Andrew Jackson Elementary School |  |  | House fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B1 | Music Room | 324 | 21 |  | 1036 | 23 | 21 | AHU
101 | Classroom | 536 | 35 |  | 1190 | 27 | 27 | AHU
102 | Classroom | 436 | 29 |  | 638 | 14 | 14 | AHU
103 | Classroom | 567 | 37 |  | 805 | 18 | 18 | AHU
104 | Classroom | 363 | 24 |  | 840 | 19 | 19 | AHU
105 | Classroom | 398 | 26 |  | 828 | 18 | 18 | AHU
106 | Classroom | 740 | 49 |  | 748 | 17 | 17 | AHU
107 | Classroom | 567 | 37 |  | 736 | 16 | 16 | AHU
107B | - |  | 0 | Yes | 132 | 3 | 3 | N/A
107C | - |  | 0 | Yes | 220 | 5 | 5 | N/A
108 | Classroom | 396 | 26 |  | 841 | 19 | 19 | AHU
109 | Classroom | 669 | 44 |  | 1218 | 27 | 27 | AHU
110 | Classroom | 482 | 32 |  | 848 | 19 | 19 | AHU
201 | Classroom | 581 | 38 |  | 1225 | 27 | 27 | AHU
202 | Classroom | 346 | 23 |  | 726 | 16 | 16 | AHU
203 | Classroom | 384 | 25 |  | 864 | 19 | 19 | AHU
204 | Classroom | 453 | 30 |  | 850 | 19 | 19 | AHU
204A | Office | 0 | 0 | Yes | 468 | 10 | 10
205 | Classroom | 304 | 20 |  | 840 | 19 | 19 | AHU
206 | Classroom | 531 | 35 |  | 864 | 19 | 19 | AHU
207 | Classroom | 614 | 40 |  | 805 | 18 | 18 | AHU
208 | Classroom | 367 | 24 |  | 850 | 19 | 19 | AHU
209/210 | Classroom | 1387 | 92 |  | 1680 | 38 | 38 | AHU
211 | Classroom | 490 | 32 |  | 840 | 19 | 19 | AHU
301 | Classroom | 530 | 35 |  | 980 | 22 | 22 | AHU
302 | Classroom | 303 | 20 |  | 816 | 18 | 18 | AHU
303 | Classroom | 88 | 5 | Yes | 828 | 18 | 18
304 | Classroom | 427 | 28 |  | 805 | 18 | 18 | AHU
304A | Office | 0 | 0 | Yes | 442 | 10 | 10
305 | Classroom | 619 | 41 |  | 840 | 19 | 19 | AHU
306 | Classroom | 528 | 35 |  | 840 | 19 | 19 | AHU
307 | Classroom | 375 | 25 |  | 782 | 17 | 17 | AHU
308 | Classroom | 417 | 27 |  | 816 | 18 | 18 | AHU
- | Gym/Cafeteria | 2408 | 160 |  | 3005 | 68 | 68 | AHU
- | Library | 740 | 49 |  | 2320 | 52 | 49 | AHU
- | I.M.C. Office | 160 | 10 |  | 400 | 9 | 9 | AHU
- | Main Office | 0 | 0 | Yes | 484 | 11 | 11
- | Princpal's Office |  | 0 | Yes | 308 | 7 | 7 | N/A
- | Nurse's Office |  | 0 | Yes | 264 | 6 | 6 | N/A

## Amy @ James Martin
Sheet Last Modified: | 2021-04-26
School: | James Martin- Alternative Middle Years (Middle School)
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 0 | 0 | Yes | 696 | 15 | 15
106 | Classroom | 280 | 18 |  | 720 | 16 | 16
107 | Classroom | 313 | 20 |  | 720 | 16 | 16
108 | Classroom | 0 | 0 | Yes | 696 | 15 | 15
109 | Classroom | 0 | 0 | Yes | 672 | 15 | 15
201 | Classroom | 0 | 0 | Yes | 720 | 16 | 16
202 | Classroom | 0 | 0 | Yes | 750 | 17 | 17
203 | Classroom | 306 | 20 |  | 750 | 17 | 17
204 | Lounge | 371 | 24 |  | 480 | 10 | 10
205 | Classroom | 345 | 23 |  | 912 | 20 | 20
206 | School Store | 291 | 19 |  | 384 | 8 | 8
207 | Classroom | 309 | 20 |  | 750 | 17 | 17
208 | Classroom | 331 | 22 |  | 720 | 16 | 16
209 | Classroom | 303 | 20 |  | 667 | 15 | 15
210 | Classroom | 292 | 19 |  | 667 | 15 | 15
211 | Classroom | 0 | 0 | Yes | 672 | 15 | 15
214 | Security Office | 0 | 0 | Yes | 256 | 5 | 5
301 | Classroom | 0 | 0 | Yes | 696 | 15 | 15
302 | Classroom | 0 | 0 | Yes | 696 | 15 | 15
303 | Classroom | 301 | 20 |  | 720 | 16 | 16
304 | Classroom | 275 | 18 |  | 720 | 16 | 16
305 | Classroom | 297 | 19 |  | 696 | 15 | 15
306 | Classroom | 284 | 18 |  | 720 | 16 | 16
307 | Classroom | 297 | 19 |  | 768 | 17 | 17
308 | Classroom | 317 | 21 |  | 696 | 15 | 15
309 | Classroom | 272 | 18 |  | 696 | 15 | 15
310 | Classroom | 293 | 19 |  | 720 | 16 | 16
311 | Art Room | 0 | 0 | Yes | 928 | 21 | 21
314 | Office | 0 | 0 | Yes | 256 | 5 | 5
- | Boys Cafeteria | 0 | 0 | Yes | 851 | 19 | 19
- | Counselors Office | 0 | 0 | Yes | 160 | 3 | 3
- | Girls Cafeteria | 0 | 0 | Yes | 1728 | 39 | 39
- | Gym | 0 | 0 |  | 1760 | 40 | 0
- | IMC-A | 270 | 18 |  | 720 | 16 | 16
- | IMC-B | 292 | 19 |  | 720 | 16 | 16
- | IMC-C | 283 | 18 |  | 720 | 16 | 16
- | Main Office | 0 | 0 | Yes | 360 | 8 | 8
- | Nurses Office | 0 | 0 | Yes | 256 | 5 | 5
- | Teachers Lounge | 0 | 0 |  | 480 | 10 | 0

## Jenks, AS
Sheet Last Modified: | 2021-04-26
School: | Abraham S. Jenks Elementary School |  |  | House fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
14 | Classroom | 422 | 28 |  | 638 | 14 | 14 | House Fan
15 | Cafeteria | 221 | 14 |  | 638 | 14 | 14 | House Fan
101 | Classroom | 459 | 30 |  | 660 | 15 | 15 | House Fan
102 | Classroom | 1235 | 82 |  | 660 | 15 | 15 | House Fan
103 | Classroom | 1253 | 83 |  | 660 | 15 | 15 | House Fan
104 | Classroom | 919 | 61 |  | 660 | 15 | 15 | House Fan
105 | Classroom | 632 | 42 |  | 660 | 15 | 15 | House Fan
106 | Classroom | 748 | 49 |  | 660 | 15 | 15 | House Fan
201 | Classroom | 1277 | 85 |  | 690 | 15 | 15 | House Fan
202 | Classroom | 522 | 34 |  | 690 | 15 | 15 | House Fan
203 | Classroom | 1094 | 72 |  | 690 | 15 | 15 | House Fan
204 | Classroom | 803 | 53 |  | 690 | 15 | 15 | House Fan
205 | Classroom | 749 | 49 |  | 690 | 15 | 15 | House Fan
206 | Classroom | 1198 | 79 |  | 690 | 15 | 15 | House Fan
207 | Classroom | 1279 | 85 |  | 744 | 16 | 16 | House Fan
- | Principals Office |  | 0 | Yes | 165 | 3 | 3
- | Main Office |  | 0 | Yes | 195 | 4 | 4
- | Teacher Lounge |  | 0 |  | 165 | 3 | 0
- | Nurses Office |  | 0 | Yes | 190 | 4 | 4
- | Library | 176 | 11 |  | 638 | 14 | 11 | House Fan
- | Auditorium | 217 | 14 |  | 1540 | 35 | 14 | UV
- | Cafeteria | 362 | 24 |  | 638 | 14 | 14 | House Fan
- | North Trailer Classroom | 227 | 15 |  | N/A | 0 | 0 | N/A used for storage
- | South Trailer Classroom | 261 | 17 |  | 638 | 14 | 14 | AHU
- | Gym |  | 0 | Yes | 1700 | 38 | 38 | N/A

## Jenks, J.S.
Sheet Last Modified: | 2021-04-28
School: | John S. Jenks Elementary-Middle School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
322 | Classroom |  | 0 | Yes | 658 | 14 | 14 | House Fan
321 | Classroom |  | 0 | Yes | 692 | 15 | 15 | House Fan
320 | Classroom |  | 0 | Yes | 684.9 | 15 | 15 | House Fan
319B | - |  | 0 | Yes | 658 | 14 | 14 | House Fan
319A | - |  | 0 | Yes | 304.5 | 6 | 6 | House Fan
318 | Classroom |  | 0 | Yes | 654.4 | 14 | 14 | House Fan
317 | Classroom |  | 0 | Yes | 674.3 | 15 | 15 | House Fan
316 | Classroom |  | 0 | Yes | 692.9 | 15 | 15 | House Fan
315 | Classroom |  | 0 | Yes | 653.7 | 14 | 14 | House Fan
214 | Classroom |  | 0 | Yes | 671.3 | 15 | 15 | House Fan
213 | Classroom |  | 0 | Yes | 689.2 | 15 | 15 | House Fan
212 | Classroom |  | 0 | Yes | 683.1 | 15 | 15 | House Fan
211 | Classroom |  | 0 | Yes | 672.6 | 15 | 15 | House Fan
210 | Classroom |  | 0 | Yes | 671.3 | 15 | 15 | House Fan
209 | Classroom |  | 0 | Yes | 680.34 | 15 | 15 | House Fan
208 | Classroom |  | 0 | Yes | 695.4 | 15 | 15 | House Fan
207 | Classroom |  | 0 | Yes | 636 | 14 | 14 | House Fan
110 | - |  | 0 | Yes | 336 | 7 | 7 | House Fan
109 | - |  | 0 | Yes | 156 | 3 | 3 | house Fan
106 | IMC |  | 0 | Yes | 671 | 15 | 15 | House Fan
105 | Classroom |  | 0 | Yes | 640.4 | 14 | 14 | House Fan
104 | Classroom |  | 0 | Yes | 627 | 14 | 14 | House Fan
103 | Classroom |  | 0 | Yes | 665.9 | 15 | 15 | House Fan
102 | Classroom |  | 0 | Yes | 667.59 | 15 | 15 | House Fan
101 | Classroom |  | 0 | Yes | 602 | 13 | 13 | House Fan
100 | Classroom |  | 0 | Yes | 1053 | 23 | 23 | House Fan
- | Kindergarten Classroom |  | 0 | Yes | 1512 | 34 | 34 | House Fan
- | Gym |  | 0 | Yes | 4500 | 102 | 102
- | Main Office |  | 0 | Yes | 385 | 8 | 8
- | Principal Office |  | 0 | Yes | 112 | 2 | 2
- | Library |  | 0 | Yes | 615.5 | 13 | 13
- | Teachers Lounge |  | 0 | Yes | 402 | 9 | 9
- | Spo |  | 0 | Yes | 179.5 | 4 | 4
- | Counselor Office |  | 0 | Yes | 165 | 3 | 3
- | Nurse Office |  | 0 | Yes | 262.5 | 5 | 5
- | Speech Room |  | 0 | Yes | 103 | 2 | 2
- | Auditorium |  | 0 |  | 3463 | 78 | 0
- | Copy Room |  | 0 |  | 165.5 | 3 | 0
- | Art Room |  | 0 | Yes | 1085 | 24 | 24
- | Lego Room |  | 0 | Yes | 165 | 3 | 3
- | Kitchen |  | 0 | Yes | 578 | 13 | 13
- | Gym Office |  | 0 |  | 588 | 13 | 0
- | Home & school |  | 0 |  | 364 | 8 | 0
- | Boys Room |  | 0 |  | 144 | 3 | 0
- | Girls Room |  | 0 |  | 144 | 3 | 0
- | Boys room by gym |  | 0 |  | 614 | 13 | 0
- | Girls room by gym |  | 0 |  | 614 | 13 | 0

## Juniata Park Academy
Sheet Last Modified: | 2021-04-06
School: | Juniata Park Academy Elementary-Middle School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 1020 | 68 |  | 1100 | 25 | 25 | RTU/UV
2 | Classroom | 897 | 59 |  | 1108 | 25 | 25 | RTU/UV
3 | Classroom | 1328 | 88 |  | 1108 | 25 | 25 | RTU/UV
4 | Classroom | 1321 | 88 |  | 1093 | 24 | 24 | RTU/UV
5 | Classroom | 975 | 65 |  | 1123 | 25 | 25 | RTU/UV
6 | Classroom | 874 | 58 |  | 1125 | 25 | 25 | RTU/UV
100 | Classroom | 750 | 50 |  | 660 | 15 | 15 | RTU/UV
101 | Classroom | 969 | 64 |  | 660 | 15 | 15 | RTU/UV
102 | Classroom | 836 | 55 |  | 952 | 21 | 21 | RTU/UV
103 | Classroom | 1212 | 80 |  | 792 | 18 | 18 | RTU/UV
104 | Classroom | 1119 | 74 |  | 792 | 18 | 18 | RTU/UV
105 | Classroom | 2327 | 155 |  | 794 | 18 | 18 | RTU/UV
106 | Classroom | 1053 | 70 |  | 794 | 18 | 18 | RTU/UV
107 | Classroom | 789 | 52 |  | 794 | 18 | 18 | RTU/UV
108 | Classroom | 952 | 63 |  | 794 | 18 | 18 | RTU/UV
109 | Classroom | 910 | 60 |  | 794 | 18 | 18 | RTU/UV
110 | Classroom | 817 | 54 |  | 794 | 18 | 18 | RTU/UV
111 | Classroom | 1240 | 82 |  | 794 | 18 | 18 | RTU/UV
112 | Classroom | 1129 | 75 |  | 794 | 18 | 18 | RTU/UV
113 | Classroom | 967 | 64 |  | 794 | 18 | 18 | RTU/UV
114 | Classroom | 906 | 60 |  | 794 | 18 | 18 | RTU/UV
115 | Classroom | 1064 | 70 |  | 792 | 18 | 18 | RTU/UV
117 | Girls' Toilet Room | 115 | 7 |  | 140 | 3 | 3 | RTU/UV
116 | Classroom | 853 | 56 |  | 792 | 18 | 18 | RTU/UV
117 | Classroom | 636 | 42 |  | 672 | 15 | 15 | RTU/UV
120 | Boys' Toilet Room | 120 | 8 |  | 200 | 4 | 4 | RTU/UV
200 | Classroom | 661 | 44 |  | 609 | 13 | 13 | RTU/UV
201 | Classroom | 638 | 42 |  | 772 | 17 | 17 | RTU/UV
202 | Classroom | 449 | 29 |  | 721 | 16 | 16 | RTU/UV
203 | Classroom | 691 | 46 |  | 673 | 15 | 15 | RTU/UV
204 | Classroom | 534 | 35 |  | 794 | 18 | 18 | RTU/UV
205 | Classroom | 627 | 41 |  | 794 | 18 | 18 | RTU/UV
205 | Girls' Toilet Room | 22 | 1 |  | 182 | 4 | 1 | RTU/UV
206 | Classroom | 530 | 35 |  | 794 | 18 | 18 | RTU/UV
207 | Classroom | 539 | 35 |  | 794 | 18 | 18 | RTU/UV
208 | Classroom | 665 | 44 |  | 794 | 18 | 18 | RTU/UV
208 | Boys' Toilet Room | 24 | 1 |  | 195 | 4 | 1 | RTU/UV
209 | Classroom | 509 | 33 |  | 794 | 18 | 18 | RTU/UV
210 | Classroom | 310 | 20 |  | 794 | 18 | 18 | RTU/UV
211 | Classroom | 418 | 27 |  | 794 | 18 | 18 | RTU/UV
212 | Classroom | 487 | 32 |  | 794 | 18 | 18 | RTU/UV
213 | Classroom | 539 | 35 |  | 794 | 18 | 18 | RTU/UV
215 | Classroom | 538 | 35 |  | 794 | 18 | 18 | RTU/UV
217 | Classroom | 683 | 45 |  | 793 | 18 | 18 | RTU/UV
229 | Girls' Toilet Room | 330 | 22 |  | 195 | 4 | 4 | RTU/UV
235 | Boys' Toilet Room | 140 | 9 |  | 200 | 4 | 4 | RTU/UV
- | Main Office | 740 | 49 |  | 500 | 11 | 11 | RTU/UV
- | Confrence Room | 475 | 31 |  | 203 | 4 | 4 | RTU/UV
- | Main Office 4 | 255 | 17 |  | 153 | 3 | 3 | RTU/UV
- | Main Office 3 | 255 | 17 |  | 120 | 2 | 2 | RTU/UV
- | Main Office 2 | 260 | 17 |  | 120 | 2 | 2 | RTU/UV
- | Main Office 1 | 310 | 20 |  | 162 | 3 | 3 | RTU/UV
- | Main Office Work Room | 245 | 16 |  | 165 | 3 | 3 | RTU/UV
- | Principals Office | 365 | 24 |  | 201 | 4 | 4 | RTU/UV
- | Principal Bathroom | 52 | 3 |  | 77 | 1 | 1 | RTU/UV
- | IMC Workroom | 79 | 5 |  | 347 | 7 | 5 | RTU/UV
- | IMC Conference Rm | 128 | 8 |  | 360 | 8 | 8 | RTU/UV
- | IMC Reference | 62 | 4 |  | 260 | 5 | 4 | RTU/UV
- | IMC Main Area North | 320 | 21 |  | 1432 | 32 | 21 | RTU/UV
- | IMC Main Area South | 217 | 14 |  | 1432 | 32 | 14 | RTU/UV
- | Library | 710 | 47 |  | 2864 | 65 | 47 | RTU/UV
- | Art Room | 701 | 46 |  | 1202 | 27 | 27 | RTU/UV
- | Music Classroom | 738 | 49 |  | 1248 | 28 | 28 | RTU/UV
- | Cafeteria | 9535 | 635 |  | 4250 | 96 | 96 | RTU/UV
- | Food Service | 135 | 9 | Yes | 1600 | 36 | 36 | RTU/UV
- | Computer Lab | 1062 | 70 |  | 1000 | 22 | 22 | RTU/UV
- | Science Lab | 1041 | 69 |  | 1436 | 32 | 32 | RTU/UV
- | Tech Ed | 1222 | 81 |  | 1415 | 32 | 32 | RTU/UV
- | Health Suite | 575 | 38 |  | 250 | 5 | 5 | RTU/UV
- | Conference Rm | 37 | 2 |  | 99 | 2 | 2 | RTU/UV
- | Corridor | 405 | 27 |  |  | 0 | 0 | RTU/UV
- | Lounge | 220 | 14 |  | 418 | 9 | 9 | RTU/UV
- | Refrence Rm | 165 | 11 |  | 120 | 2 | 2 | RTU/UV
- | Boys' Toilet Room | 327 | 21 |  | 200 | 4 | 4 | RTU/UV
- | Girls' Toilet Room | 227 | 15 |  | 140 | 3 | 3 | RTU/UV
- | Storage | 190 | 12 |  | 156 | 3 | 3 | RTU/UV
- | Trash Rm | 160 | 10 |  | 213 | 4 | 4 | RTU/UV
- | Work Room | 160 | 10 |  | 152 | 3 | 3 | RTU/UV
- | Workshop | 210 | 14 |  | 153 | 3 | 3 | RTU/UV
- | Bldg Engineer | 160 | 10 |  | 150 | 3 | 3 | RTU/UV
- | Gym |  | 0 |  | 6809 | 154 | 0 | AHU

## Kearny
Sheet Last Modified: | 2021-04-13
School: | General Philip Kearny Elementary School
Vendor: | Chadwick | Exhaust Report | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 0 | 0 |  | 780 | 17 | 0 | UV
2 | classroom | 900 | 60 |  | 780 | 17 | 17 | UV
3 | classroom | 1129 | 75 |  | 780 | 17 | 17 | UV
4 | classroom | 1177 | 78 |  | 780 | 17 | 17 | UV
100 | classroom | 1118 | 74 |  | 750 | 17 | 17 | House Fan
101 | classroom | 1353 | 90 |  | 700 | 15 | 15 | House Fan
103 | classroom | 1342 | 89 |  | 945 | 21 | 21 | House Fan
105 | classroom | 1642 | 109 |  | 696 | 15 | 15 | House Fan
107 | classroom | 314 | 20 |  | 744 | 16 | 16 | House Fan
200 | classroom | 1129 | 75 |  | 696 | 15 | 15 | House Fan
201 | classroom | 1048 | 69 |  | 696 | 15 | 15 | House Fan
202 | classroom | 1034 | 68 |  | 783 | 17 | 17 | House Fan
203 | classroom | 1345 | 89 |  | 810 | 18 | 18 | House Fan
204 | classroom | 1224 | 81 |  | 324 | 7 | 7 | House Fan
207 | classroom | 1653 | 110 |  | 768 | 17 | 17 | House Fan
300 | classroom | 1129 | 75 |  | 672 | 15 | 15 | House Fan
301 | classroom | 990 | 66 |  | 725 | 16 | 16 | House Fan
302 | classroom | 623 | 41 |  | 783 | 17 | 17 | House Fan
303 | classroom | 986 | 65 |  | 810 | 18 | 18 | House Fan
305 | classroom | 1268 | 84 |  | 720 | 16 | 16 | House Fan
306 | classroom | 1338 | 89 |  | 414 | 9 | 9 | House Fan
307 | classroom | 1067 | 71 |  | 768 | 17 | 17 | House Fan
308 | classroom | 931 | 62 |  | 675 | 15 | 15 | House Fan
309 | classroom | 1059 | 70 |  | 675 | 15 | 15 | House Fan
310 | classroom | 1114 | 74 |  | 675 | 15 | 15 | House Fan
311 | classroom | 1191 | 79 |  | 675 | 15 | 15 | House Fan
312 | classroom | 924 | 61 |  | 414 | 9 | 9 | House Fan
312 | classroom | 1529 | 101 |  | 414 | 9 | 9 | House Fan
315 | classroom | 1386 | 92 |  | 702 | 15 | 15 | House Fan
- | Gym | 9069 | 604 |  | 6100 | 138 | 138 | RTU
- | Main office |  | 0 | Yes | 340 | 7 | 7 | House Fan
- | Principal office |  | 0 | Yes | 320 | 7 | 7 | House Fan
| Cafeteria |  | 0 | Yes | 3240 | 73 | 73
- | Auditorium |  | 0 |  | 3240 | 73 | 0 | House Fan
- | Faculty |  | 0 |  | 336 | 7 | 0
- | Kitchen |  | 0 |  | 700 | 15 | 0 | House Fan
- | Nurse |  | 0 | Yes | 171 | 3 | 3 | House Fan
- | Lunchroom |  | 0 | Yes | 3078 | 69 | 69 | House Fan

## Kelley, WD
Sheet Last Modified: | 2021-04-22
School: | William D. Kelley Elementary School
Vendor: | Devine Brothers | Devine Part 2
| Devine Part 3 | Devine Part 4
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 315 | 21 |  | 1053 | 23 | 21 | UV
102 | Classroom | 322 | 21 |  | 880 | 20 | 20 | UV
103 | Classroom | 319 | 21 |  | 735 | 16 | 16 | UV
104 | Classroom | 318 | 21 |  | 805 | 18 | 18 | UV
104B | Classroom | 301 | 20 |  | 870 | 19 | 19 | UV
105 | Classroom | 357 | 23 |  | 735 | 16 | 16 | UV
106 | Classroom | 395 | 26 |  | 735 | 16 | 16 | UV
108 | Classroom | 376 | 25 |  | 735 | 16 | 16 | UV
109 | Classroom | 302 | 20 |  | 735 | 16 | 16 | UV
110 | Classroom | 321 | 21 |  | 442 | 10 | 10 | UV
111 | Classroom | 339 | 22 |  | 735 | 16 | 16 | UV
200 | Classroom | 357 | 23 |  | 700 | 15 | 15 | UV
201 | Classroom | 302 | 20 |  | 720 | 16 | 16 | UV
202 | Classroom | 330 | 22 |  | 770 | 17 | 17 | UV
203 | Classroom | 314 | 20 |  | 735 | 16 | 16 | UV
204 | Classroom | 355 | 23 |  | 735 | 16 | 16 | UV
205 | Classroom | 344 | 22 |  | 735 | 16 | 16 | UV
206 | Classroom | 284 | 18 |  | 406 | 9 | 9 | UV
207 | Classroom | 332 | 22 |  | 735 | 16 | 16 | UV
208 | IMC | 302 | 20 |  | 1540 | 35 | 20 | UV
209 | Classroom | 341 | 22 |  | 770 | 17 | 17 | UV
210 | IMC | 323 | 21 |  | 1540 | 35 | 21 | UV
211 | Classroom | 307 | 20 |  | 735 | 16 | 16 | UV
212 | Classroom | 305 | 20 |  | 510 | 11 | 11 | UV
214 | Classroom | 339 | 22 |  | 735 | 16 | 16 | UV
216 | Classroom | 330 | 22 |  | 735 | 16 | 16 | UV
218 | Classroom | 180 | 12 |  | 143 | 3 | 3 | UV
300 | Classroom | 311 | 20 |  | 700 | 15 | 15 | UV
301 | Classroom | 320 | 21 |  | 720 | 16 | 16 | UV
302 | Classroom | 416 | 27 |  | 770 | 17 | 17 | UV
303 | Classroom | 380 | 25 |  | 735 | 16 | 16 | UV
304 | Classroom | 305 | 20 |  | 735 | 16 | 16 | UV
306 | Classroom | 281 | 18 |  | 406 | 9 | 9 | UV
307 | Classroom | 292 | 19 |  | 735 | 16 | 16 | UV
308 | Classroom | 385 | 25 |  | 735 | 16 | 16 | UV
309 | Classroom | 318 | 21 |  | 735 | 16 | 16 | UV
310 | Classroom | 163 | 10 | Yes | 735 | 16 | 16 | UV
311 | Classroom | 334 | 22 |  | 735 | 16 | 16 | UV
312 | Classroom | 275 | 18 |  | 510 | 11 | 11 | UV
314 | Classroom | 325 | 21 |  | 735 | 16 | 16 | UV
316 | Classroom | 302 | 20 |  | 735 | 16 | 16 | UV
318 | Classroom | 181 | 12 |  | 143 | 3 | 3 | UV
- | Auditorium | 1841 | 122 |  | 4278 | 97 | 97 | AHU
- | Gymnasium | 899 | 59 |  | 3588 | 81 | 59 | AHU
- | Library | 625 | 41 |  | 1540 | 35 | 35 | UV
- | Main Office | 101 | 6 | Yes | 483 | 10 | 10 | AHU
- | Nurse Office | 84 | 5 | Yes | 368 | 8 | 8
- | Admin Asst. Office | 38 | 2 |  | 99 | 2 | 2
- | Principal's Office | 41 | 2 |  | 315 | 7 | 2
- | Conference/Office | 90 | 6 |  | 384 | 8 | 6
- | Counselor's Office | 0 | 0 |  | 442 | 10 | 0

## Kelly, JB
Sheet Last Modified: | 2021-04-30
School: | John B. Kelly Elementary School
Vendor: | Capital
Vendor: | Devine Brothers | Retest | 2nd Retest
| Devine 3rd Retest | Devine 4th Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Teachers Dining | 340 | 22 |  | 868 | 19 | 19 | UV
102 | Classroom | 497 | 33 |  | 850 | 19 | 19 | UV
102A | Classroom | 155 | 10 |  | 550 | 12 | 10 | UV
103 | Classroom | 673 | 44 |  | 850 | 19 | 19 | UV
103A | Classroom | 216 | 14 |  | 550 | 12 | 12 | UV
104 | Classroom | 607 | 40 |  | 850 | 19 | 19 | UV
105 | Classroom | 592 | 39 |  | 850 | 19 | 19 | UV
106 | Classroom | 576 | 38 |  | 850 | 19 | 19 | UV
107 | Classroom | 572 | 38 |  | 850 | 19 | 19 | UV
108 | Classroom | 576 | 38 |  | 850 | 19 | 19 | UV
109 | Classroom | 539 | 35 |  | 850 | 19 | 19 | UV
110 | Classroom | 434 | 28 |  | 850 | 19 | 19 | UV
111 | Classroom | 336 | 22 |  | 850 | 19 | 19 | UV
112 | Classroom | 627 | 41 |  | 850 | 19 | 19 | UV
113 | Classroom | 320 | 21 |  | 850 | 19 | 19 | UV
114 | Classroom | 534 | 35 |  | 850 | 19 | 19 | UV
160 | Classroom | 305 | 20 |  | 942 | 21 | 20 | UV
160 | Main Office | 182 | 12 |  | 232 | 5 | 5 | UV
201 | Classroom | 370 | 24 |  | 850 | 19 | 19 | UV
202 | Classroom | 494 | 32 |  | 850 | 19 | 19 | UV
202A | Office | 33 | 2 |  | 140 | 3 | 2 | UV
203 | Classroom | 744 | 49 |  | 1088 | 24 | 24 | UV
204 | Classroom | 609 | 40 |  | 850 | 19 | 19 | UV
204A | Classroom | 282 | 18 |  | 550 | 12 | 12 | UV
205 | Classroom | 327 | 21 |  | 850 | 19 | 19 | UV
205A | Classroom | 293 | 19 |  | 550 | 12 | 12 | UV
206 | Classroom | 284 | 18 |  | 1088 | 24 | 18 | UV
207 | Classroom | 468 | 31 |  | 850 | 19 | 19 | UV
208 | Classroom | 586 | 39 |  | 850 | 19 | 19 | UV
209 | Classroom | 381 | 25 |  | 850 | 19 | 19 | UV
210 | Classroom | 341 | 22 |  | 1088 | 24 | 22 | UV
210A | Office | 188 | 12 |  | 136 | 3 | 3 | UV
211 | Classroom | 530 | 35 |  | 850 | 19 | 19 | UV
212 | Classroom | 729 | 48 |  | 850 | 19 | 19 | UV
212A | Classroom | 289 | 19 |  | 550 | 12 | 12 | UV
213 | Classroom | 661 | 44 |  | 850 | 19 | 19 | UV
213A | Classroom | 233 | 15 |  | 550 | 12 | 12 | UV
214 | Classroom | 588 | 39 |  | 1088 | 24 | 24 | UV
215 | Classroom | 341 | 22 |  | 676 | 15 | 15 | UV
216 | Classroom | 425 | 28 |  | 850 | 19 | 19 | UV
217 East | Classroom | 294 | 19 |  | 1006 | 22 | 19 | UV
217 North | Classroom | 227 | 15 |  | 1093 | 24 | 15 | UV
217 South Center | Classroom | 382 | 25 |  | 1069 | 24 | 24 | UV
217 West Center | Classroom | 285 | 19 |  | 1093 | 24 | 19 | UV
- | Admin/Asst. Office | 66 | 4 |  | 179 | 4 | 4 | UV
- | Administration Offices | 1305 | 87 |  | 535 | 12 | 12 | UV
ART | Art Classroom | 731 | 48 |  | 1350 | 30 | 30 | UV
ART -A | Art Classroom | 401 | 26 |  |  | 0 | 0 | UV
ART -B | Art Classroom | 557 | 37 |  |  | 0 | 0 | UV
ART -C | Art Classroom | 111 | 7 |  |  | 0 | 0 | UV
ART -D | Art Classroom | 318 | 21 |  |  | 0 | 0 | UV
- | Auditorium | 1721 | 114 |  | 6080 | 138 | 114 | UV
- | 1st Flr A-Wing Left Boys Bathroom | 53 | 3 |  | 88 | 2 | 2 | AHU
- | 2nd Flr A-Wing Left Boys Bathroom | 101 | 6 |  | 96 | 2 | 2 | AHU
- | 2nd Flr A-Wing Right Boys Bathroom | 43 | 2 |  | 103 | 2 | 2 | AHU
- | Conference Room | 139 | 9 |  | 211 | 4 | 4 | AHU
- | Copy/Storage Room | 110 | 7 |  | 165 | 3 | 3 | AHU
- | Corridor | 41 | 2 |  |  | 0 | 0 | AHU
- | Counselor Office | 58 | 3 |  | 123 | 2 | 2 | AHU
- | Dressing - A Backstage | 307 | 20 |  | 232 | 5 | 5 | UV
- | Dressing - B Backstage | 461 | 30 |  | 196 | 4 | 4 | UV
- | Dressing - C Backstage | 493 | 32 |  | 190 | 4 | 4 | UV
- | Dressing - D Backstage | 275 | 18 |  | 199 | 4 | 4 | UV
- | 1st Flr A-Wing Left Girls Bathroom | 41 | 2 |  | 109 | 2 | 2 | AHU
- | 2nd Flr A-Wing Left Girls Bathroom | 78 | 5 |  | 106 | 2 | 2 | AHU
- | 2nd Flr A-Wing Right Girls Bathroom | 54 | 3 |  | 103 | 2 | 2 | AHU
- | IMC | 0 | 0 |  | 8471 | 192 | 0 | AHU
- | IMC North Side | 947 | 63 |  | 480 | 10 | 10 | AHU
- | IMC South Side | 822 | 54 |  | 480 | 10 | 10 | AHU
- | IMC Entry from Office | 0 | 0 |  |  | 0 | 0 | AHU
- | IMC Entry to Hall | 0 | 0 |  |  | 0 | 0 | AHU
- | IMC-1 Office | 80 | 5 |  | 293 | 6 | 5 | AHU
- | IMC-2 Storage | 151 | 10 |  | 330 | 7 | 7 | AHU
- | IMC-4 Storage | 175 | 11 |  | 372 | 8 | 8 | AHU
- | IMC-5 Data/Storage | 68 | 4 |  | 277 | 6 | 4 | AHU
- | Cafeteria | 0 | 0 |  | 1195 | 27 | 0 | AHU
- | Cafeteria | 1928 | 128 |  | 4807 | 109 | 109 | AHU
- | Gym | 2934 | 195 |  | 387 | 8 | 8 | AHU
- | Music Classroom A | 326 | 21 |  |  | 0 | 0 | UV
- | Music Classroom B | 555 | 37 |  |  | 0 | 0 | UV
- | Music Classroom C | 152 | 10 |  |  | 0 | 0 | UV
- | Music Classroom D | 106 | 7 |  |  | 0 | 0 | UV
- | Main Music Classroom | 463 | 30 |  | 380 | 8 | 8 | UV
- | Music Office | 136 | 9 |  | 355 | 8 | 8 | AHU
- | Nurse Exam Room | 0 | 0 |  | 209 | 4 | 0 | AHU
- | Nurse Exam Room | 43 | 2 |  |  | 0 | 0 | AHU
- | Nurses Office | 0 | 0 |  |  | 0 | 0 | AHU
- | Nurses Rest | 68 | 4 |  |  | 0 | 0 | AHU
- | Nurses Suite | 411 | 27 |  |  | 0 | 0 | UV
- | Aud & Dental | 31 | 2 |  | 270 | 6 | 2 | AHU
- | Principals Office | 98 | 6 |  | 270 | 6 | 6 | AHU
- | Speech/Com | 388 | 25 |  | 736 | 16 | 16 | UV
- | Server Room | 55 | 3 |  | 121 | 2 | 2 | Split System
- | Storage | 247 | 16 |  | 809 | 18 | 16 | AHU
- | Office / Waiting Room | 277 | 18 |  |  | 0 | 0 | AHU
K - 1 | Kindergarten | 452 | 30 |  | 1488 | 33 | 30 | UV
K - 2 | Kindergarten | 490 | 32 |  | 1488 | 33 | 32 | UV
K - 3 | Kindergarten | 498 | 33 |  | 1488 | 33 | 33 | UV
K - 4 | Kindergarten | 635 | 42 |  | 1488 | 33 | 33 | UV
K - 5 | Kindergarten | 280 | 18 |  | 1488 | 33 | 18 | UV
K - 6 | Kindergarten | 300 | 20 |  | 1488 | 33 | 20 | UV

## Kenderton
Sheet Last Modified: | 2021-04-23
School: | Kenderton Elementary School
Vendor: | Chadwick | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 229 | 15 |  | 1012 | 23 | 15 | UV
101 | Classroom | 451 | 30 |  | 1680 | 38 | 30 | UV
102 | Classroom | 458 | 30 |  | 1652 | 37 | 30 | UV
103 | Classroom | 331 | 22 | Yes | 1344 | 30 | 30 | UV
104 | Nurse |  | 0 | Yes | 275 | 6 | 6
200A | Classroom | 198 | 13 |  | 442 | 10 | 10 | UV
200 | Classroom | 0 | 0 |  | 891 | 20 | 0 | UV
201 | Classroom | 278 | 18 | Yes | 891 | 20 | 20 | UV
202 | Classroom | 331 | 22 |  | 918 | 20 | 20 | UV
203 | Classroom | 297 | 19 |  | 980 | 22 | 19 | UV
204 | Classroom | 302 | 20 |  | 918 | 20 | 20 | UV
205 | Classroom | 198 | 13 |  | 918 | 20 | 13 | UV
206 | Classroom | 273 | 18 |  | 616 | 14 | 14 | UV
207 | Classroom | 273 | 18 |  | 918 | 20 | 18 | UV
208 | Classroom | 191 | 12 | Yes | 120 | 2 | 2 | UV
209 | Classroom | 283 | 18 |  | 918 | 20 | 18 | UV
211 | Classroom | 276 | 18 |  | 286 | 6 | 6 | UV
213 | Classroom | 271 | 18 |  | 918 | 20 | 18 | UV
300 | Classroom | 278 | 18 | Yes | 918 | 20 | 20 | UV
301 | Classroom | 271 | 18 |  | 918 | 20 | 18 | UV
302 | Classroom | 272 | 18 | Yes | 918 | 20 | 20 | UV
303 | Classroom | 296 | 19 |  | 980 | 22 | 19 | UV
304 | Classroom | 276 | 18 |  | 864 | 19 | 18 | UV
306 | Classroom | 316 | 21 |  | 918 | 20 | 20 | UV
307 | Classroom | 281 | 18 | Yes | 924 | 21 | 21 | UV
308 | Classroom | 0 | 0 | Yes | 924 | 21 | 21 | UV
309 | Classroom | 0 | 0 |  | 980 | 22 | 0 | UV
310 | Classroom | 0 | 0 | Yes | 616 | 14 | 14 | UV
311 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV
312 | Computer Room |  | 0 | Yes | 860 | 19 | 19
313 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV
314 | Classroom | 0 | 0 |  | 280 | 6 | 0 | UV
315 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV
316 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | UV
319 | Classroom | 0 | 0 |  | 918 | 20 | 0 | UV
400 | Classroom | 286 | 19 |  | 2660 | 60 | 19 | UV
401 | Classroom | 279 | 18 |  | 918 | 20 | 18 | UV
402 | Classroom | 313 | 20 |  | 918 | 20 | 20 | UV
403 | Classroom | 340 | 22 |  | 918 | 20 | 20 | UV
404 | Classroom | 0 | 0 |  | 868 | 19 | 0 | UV
406 | Classroom | 291 | 19 |  | 918 | 20 | 19 | UV
407 | Classroom | 0 | 0 | Yes | 924 | 21 | 21 | UV
408 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV
409 | Classroom | 0 | 0 | Yes | 980 | 22 | 22 | UV
410 | Classroom | 335 | 22 | Yes | 644 | 14 | 14 | UV
411 | Classroom | 0 | 0 |  | 918 | 20 | 0 | UV
412 | Classroom | 276 | 18 |  | 308 | 7 | 7 | UV
413 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | UV
414 | Classroom | 0 | 0 | Yes | 270 | 6 | 6 | UV
415 | Classroom | 0 | 0 |  | 918 | 20 | 0 | UV
- | Parent Resource | 0 | 0 |  | 2 | 0 | 0 | UV
- | Main Office | 42 | 2 |  | 406 | 9 | 2 | UV
- | Principal's Office |  | 0 |  | 320 | 7 | 0
- | Asist Prince | 172 | 11 |  | 11 | 0 | 0 | UV

## Kensington BusinessEd
Sheet Last Modified: | 2021-04-19
School: | Kensington High School |  |  | House fan Abated
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | - |  | 0 |  | 675 | 15 | 0
2 | - |  | 0 |  | 1014 | 23 | 0
3 | - |  | 0 |  | 728 | 16 | 0
4 | - |  | 0 |  | 364 | 8 | 0
5 | - |  | 0 |  | 850 | 19 | 0
100 | Main Office |  | 0 |  | 1014 | 23 | 0
102 | - |  | 0 | Yes | 800 | 18 | 18
103 | IMC |  | 0 |  | 1690 | 38 | 0
104 | - |  | 0 |  | 728 | 16 | 0
105 | - |  | 0 |  | 728 | 16 | 0
107 | - |  | 0 |  | 728 | 16 | 0
108 | - |  | 0 |  | 962 | 21 | 0
109 | - |  | 0 |  | 728 | 16 | 0
111 | - |  | 0 |  | 910 | 20 | 0
114 | - |  | 0 | Yes | 728 | 16 | 16
115 | - |  | 0 |  | 728 | 16 | 0
116 | - |  | 0 |  | 702 | 15 | 0
117 | - |  | 0 |  | 728 | 16 | 0
118 | - |  | 0 | Yes | 728 | 16 | 16
120 | - |  | 0 |  | 845 | 19 | 0
125 | - |  | 0 |  | 1020 | 23 | 0
200 | - |  | 0 |  | 728 | 16 | 0
201 | - |  | 0 |  | 962 | 21 | 0
202 | - |  | 0 |  | 910 | 20 | 0
203 | - |  | 0 |  | 728 | 16 | 0
204 | - |  | 0 |  | 702 | 15 | 0
205 | - |  | 0 |  | 728 | 16 | 0
207 | - |  | 0 |  | 728 | 16 | 0
208 | - |  | 0 |  | 884 | 20 | 0
209 | - |  | 0 |  | 546 | 12 | 0
210 | - |  | 0 |  | 546 | 12 | 0
211 | - |  | 0 |  | 884 | 20 | 0
214 | - |  | 0 |  | 728 | 16 | 0
215 | - |  | 0 |  | 728 | 16 | 0
217 | - |  | 0 |  | 728 | 16 | 0
218 | - |  | 0 |  | 728 | 16 | 0
221 | - |  | 0 |  | 1037 | 23 | 0
300 | - |  | 0 |  | 728 | 16 | 0
301 | - |  | 0 |  | 910 | 20 | 0
302 | - |  | 0 |  | 910 | 20 | 0
303 | - |  | 0 |  | 702 | 15 | 0
304 | - |  | 0 |  | 728 | 16 | 0
305 | - |  | 0 |  | 702 | 15 | 0
307 | - |  | 0 |  | 728 | 16 | 0
308 | - |  | 0 |  | 910 | 20 | 0
309 | - |  | 0 |  | 546 | 12 | 0
310 | - |  | 0 |  | 546 | 12 | 0
311 | - |  | 0 |  | 884 | 20 | 0
314 | - |  | 0 |  | 728 | 16 | 0
315 | - |  | 0 |  | 728 | 16 | 0
316 | - |  | 0 |  | 728 | 16 | 0
317 | - |  | 0 |  | 728 | 16 | 0
318 | - |  | 0 |  | 728 | 16 | 0
322 | Gym |  | 0 |  | 6360 | 144 | 0

## Kensington CAPA
Sheet Last Modified: | 2021-04-22
School: | Kensington Creative and Performing Arts (CAPA) High School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium |  | 0 |  | 5100 | 115 | 0
- | Gymnasium |  | 0 |  | 8400 | 190 | 0
101b | - |  | 0 |  | 450 | 10 | 0
101 | - |  | 0 |  | 400 | 9 | 0
103 | - |  | 0 |  | 1200 | 27 | 0
106 | - |  | 0 |  | 1200 | 27 | 0
118 | - |  | 0 |  | 900 | 20 | 0
119 | - |  | 0 |  | 900 | 20 | 0
121 | - |  | 0 |  | 900 | 20 | 0
122 | - |  | 0 |  | 900 | 20 | 0
123 | - |  | 0 |  | 900 | 20 | 0
131 | - |  | 0 |  | 1150 | 26 | 0
134 | - |  | 0 | Yes | 700 | 15 | 15
135 | - |  | 0 |  | 750 | 17 | 0
201 | - |  | 0 |  | 1200 | 27 | 0
209 | - |  | 0 |  | 900 | 20 | 0
210 | - |  | 0 |  | 900 | 20 | 0
212 | - |  | 0 |  | 900 | 20 | 0
213 | - |  | 0 |  | 900 | 20 | 0
214 | - |  | 0 |  | 900 | 20 | 0
216 | - |  | 0 | Yes | 1400 | 31 | 31
217 | - |  | 0 |  | 1400 | 31 | 0
218 | - |  | 0 |  | 1200 | 27 | 0
220 | - |  | 0 |  | 1200 | 27 | 0
221 | - |  | 0 |  | 1200 | 27 | 0
224 | - |  | 0 |  | 900 | 20 | 0
225 | - |  | 0 |  | 900 | 20 | 0
- | Cafe |  | 0 |  | 2400 | 54 | 0

## Kensington Health
Sheet Last Modified: | 2021-04-23
School: | Kensington Health Sciences Academy High School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Room | 247 | 16 |  | 857 | 19 | 16
102 | Room | 338 | 22 |  | 792 | 18 | 18
103 | Room | 206 | 13 |  | 854 | 19 | 13
104 | Room | 248 | 16 |  | 834 | 18 | 16
105 | Room | 212 | 14 |  | 854 | 19 | 14
106 | Room | 548 | 36 |  | 834 | 18 | 18
107 & 107A | Room | 613 | 40 |  | 783 | 17 | 17
110 | Room | 184 | 12 |  | 793 | 18 | 12
114 | Nurse |  | 0 |  | 114 | 2 | 0
115 | Room | 191 | 12 |  | 337 | 7 | 7
116 | Room | 171 | 11 |  | 848 | 19 | 11
201 | Room | 506 | 33 |  | 919 | 20 | 20
203 | Room | 0 | 0 |  | 795 | 18 | 0
208 | 2nd Floor Bed and Dental Area | 1803 | 120 |  | 943 | 21 | 21
211 | Room | 273 | 18 |  | 860 | 19 | 18
212 | Room | 77 | 5 |  | 456 | 10 | 5
213 | Room | 250 | 16 |  | 681 | 15 | 15
214 | Dental Classroom | 171 | 11 |  | 794 | 18 | 11
215 | Room | 204 | 13 |  | 689 | 15 | 13
216 | Room | 191 | 12 |  | 756 | 17 | 12
217 | Room | 222 | 14 |  | 681 | 15 | 14
218 | Room | 276 | 18 |  | 599 | 13 | 13
- | Cafeteria | 586 | 39 |  | 1697 | 38 | 38

## Key
Sheet Last Modified: | 2021-03-30
School: | Francis Scott Key Elementary School
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Gym |  | 0 | Yes | 704 | 16 | 16 | House Fan
102 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan
103 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan
104 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
105 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
106 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
107 | Classroom |  | 0 |  | 437 | 9 | 0 | House Fan
108 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan
109 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan
110 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
111 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
212 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan
213 | Classroom |  | 0 | Yes | 837 | 19 | 19 | House Fan
215 | IMC |  | 0 | Yes | 1536 | 34 | 34 | House Fan
216 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
217 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
218 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan
219 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan
220 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan
221 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan
222 | Computer Lab |  | 0 |  | 720 | 16 | 0 | House Fan
323 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan
324 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan
325 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan
326 | Classroom |  | 0 |  | 736 | 16 | 0 | House Fan
327 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan
328 | Classroom |  | 0 |  | 768 | 17 | 0 | House Fan
329 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan
330 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan
331 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan
332 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan
333 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan
- | Boy's Gang Bathrrom |  | 0 |  | 620 | 14 | 0 | N/A
- | Caferteria |  | 0 | Yes | 2240 | 50 | 50 | House Fan
- | Counselor's Office |  | 0 |  | 180 | 4 | 0 | House Fan
- | Girls Gang Bathrrom |  | 0 |  | 620 | 14 | 0 | N/A
- | Main Office |  | 0 | Yes | 361 | 8 | 8 | House Fan
- | Nurse |  | 0 | Yes | 391 | 8 | 8 | House Fan
- | Principle's Office |  | 0 |  | 276 | 6 | 0 | House Fan
- | Teachers' Lounge |  | 0 |  | 391 | 8 | 0 | House Fan

## Kirkbride
Sheet Last Modified: | 2021-03-24
School: | Eliza B. Kirkbride Elementary-Middle
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | - |  | 0 | Yes | 805 | 18 | 18 | House Fan
102 | - |  | 0 |  | 690 | 15 | 0 | House Fan
103 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan
104 | - |  | 0 | Yes | 690 | 15 | 15 | House Fan
106 | - |  | 0 | Yes | 690 | 15 | 15 | House Fan
107 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan
108 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan
109 | - |  | 0 | Yes | 690 | 15 | 15 | House Fan
110 | - |  | 0 | Yes | 841 | 19 | 19 | House Fan
201 | - |  | 0 | Yes | 814 | 18 | 18 | House Fan
202 | - |  | 0 |  | 660 | 15 | 0 | House Fan
203 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan
204 | - |  | 0 |  | 660 | 15 | 0 | House Fan
205 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan
208 | - |  | 0 | Yes | 638 | 14 | 14 | House Fan
209 | - |  | 0 |  | 638 | 14 | 0 | House Fan
210 | - |  | 0 | Yes | 841 | 19 | 19 | House Fan
211 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan
212 | - |  | 0 |  | 638 | 14 | 0 | House Fan
301 | - |  | 0 |  | 851 | 19 | 0 | House Fan
302 | - |  | 0 |  | 660 | 15 | 0 | House Fan
303 | - |  | 0 |  | 704 | 16 | 0 | House Fan
304 | - |  | 0 |  | 690 | 15 | 0 | House Fan
305/306 | - |  | 0 |  | 1357 | 30 | 0 | House Fan
307 | - |  | 0 |  | 690 | 15 | 0 | House Fan
308 | - |  | 0 |  | 690 | 15 | 0 | House Fan
309 | - |  | 0 |  | 690 | 15 | 0 | House Fan
310 | - |  | 0 |  | 841 | 19 | 0 | House Fan
311 | - |  | 0 |  | 660 | 15 | 0 | House Fan
312 | - |  | 0 |  | 690 | 15 | 0 | House Fan
- | Art |  | 0 |  | 696 | 15 | 0 | House Fan
- | Counselor Suite |  | 0 | Yes | 660 | 15 | 15 | House Fan
- | Gym |  | 0 | Yes | 3680 | 83 | 83 | House Fan
- | Library |  | 0 | Yes | 1380 | 31 | 31 | House Fan
- | Lunchroom1 |  | 0 | Yes | 690 | 15 | 15 | House Fan
- | Lunchroom2 |  | 0 | Yes | 1100 | 25 | 25 | House Fan
- | Main Office |  | 0 | Yes | 322 | 7 | 7 | House Fan
- | Nurse Office |  | 0 | Yes | 96 | 2 | 2 | House Fan
- | Principal Office |  | 0 | Yes | 240 | 5 | 5 | House Fan
- | Teacher Lounge/BE office |  | 0 | Yes | 960 | 21 | 21 | House Fan

## LaBrum
Sheet Last Modified: | 2021-04-20
School: | John Hancock Demonstration Middle School @ General J Harry LaBrum Campus
| LaBrum Building | LaBrum Retest
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
102 | Classroom | 391 | 26 |  | 875 | 19 | 19 | UV
102A | Classroom | 230 | 15 |  | 578 | 13 | 13 | UV
103 | Classroom | 0 | 0 | Yes | 910 | 20 | 20 | UV
104 | Classroom | 622 | 41 |  | 612 | 13 | 13 | UV
105 | Classroom | 150 | 10 | Yes | 1152 | 26 | 26 | UV
106 | Classroom | 320 | 21 |  | 342 | 7 | 7 | UV
107 | Classroom | 221 | 14 | Yes | 1044 | 23 | 23 | UV
201 | Classroom | 362 | 24 |  | 864 | 19 | 19 | UV
202 | Classroom | 267 | 17 |  | 782 | 17 | 17 | UV
203 | Classroom | 245 | 16 | Yes | 884 | 20 | 20 | UV
204 | Classroom | 240 | 16 | Yes | 1116 | 25 | 25 | UV
205 | Classroom | 311 | 20 |  | 900 | 20 | 20 | UV
206 | Classroom | 583 | 38 |  | 858 | 19 | 19 | UV
207 | Classroom | 340 | 22 |  | 840 | 19 | 19 | UV
208 | Classroom | 462 | 30 |  | 816 | 18 | 18 | UV
209 | Classroom | 410 | 27 |  | 720 | 16 | 16 | UV
210 | Classroom | 327 | 21 |  | 888 | 20 | 20 | UV
212 | Classroom | 390 | 26 |  | 875 | 19 | 19 | UV
213 | Classroom | 336 | 22 |  | 864 | 19 | 19 | UV
214 | Classroom | 366 | 24 |  | 828 | 18 | 18 | UV
- | Admin | 0 | 0 | Yes | 286 | 6 | 6 | UV
- | Cafeteria | 450 | 30 |  | 2765 | 62 | 30 | UV
- | Gym | 0 | 0 |  | 5248 | 119 | 0
- | Library | 538 | 35 |  | 2016 | 45 | 35 | UV
- | Nurse's Room | 0 | 0 | Yes | 550 | 12 | 12 | UV

## Lamberton
Sheet Last Modified: | 2021-04-27
School: | Robert E. Lamberton Elementary School
School: | Robert E. Lamberton Elementary- Little School House
School: | Robert E. Lamberton Elementary- Little School House- Part 2
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
1A | Music Room | 261 | 17 |  | 506 | 11 | 11 | UV
1B | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | UV
2A | Classroom | 264 | 17 |  | 504 | 11 | 11 | UV
4 | Classroom | 159 | 10 | Yes | 2024 | 46 | 46 | UV
5A | Classroom | 0 | 0 | Yes | 600 | 13 | 13 | UV
6 | Classroom | 0 | 0 | Yes | 625 | 14 | 14 | UV
7 | Classroom |  | 0 | Yes | 1206 | 27 | 27 | UV
101 | Classroom | 457 | 30 |  | 506 | 11 | 11 | UV
102 | Classroom | 348 | 23 |  | 1012 | 23 | 23 | UV
103 | Classroom | 466 | 31 |  | 989 | 22 | 22 | UV
104 | Classroom | 335 | 22 | Yes | 1012 | 23 | 23 | UV
105 | Classroom | 277 | 18 | Yes | 989 | 22 | 22 | UV
106 | Classroom | 198 | 13 | Yes | 1012 | 23 | 23 | UV
107 | Classroom | 406 | 27 |  | 1012 | 23 | 23 | UV
108 | Classroom | 271 | 18 |  | 667 | 15 | 15 | UV
109 | Classroom | 351 | 23 |  | 1012 | 23 | 23 | UV
110 | Classroom | 420 | 28 |  | 989 | 22 | 22 | UV
111 | Classroom | 338 | 22 |  | 989 | 22 | 22 | UV
112 | Classroom | 0 | 0 | Yes | 989 | 22 | 22 | UV
113 | Classroom | 280 | 18 |  | 575 | 13 | 13 | UV
114 | Classroom | 271 | 18 | Yes | 874 | 19 | 19 | UV
115 | Classroom | 278 | 18 | Yes | 874 | 19 | 19 | UV
116 | Classroom | 387 | 25 |  | 874 | 19 | 19 | UV
117 | Classroom | 176 | 11 | Yes | 874 | 19 | 19 | UV
118 | Classroom | 243 | 16 | Yes | 1012 | 23 | 23 | UV
119 | Assitant Principal |  | 0 | Yes | 361 | 8 | 8
120A | Tescher's Lounge |  | 0 | Yes | 377 | 8 | 8
120 | Nurse |  | 0 |  | 501 | 11 | 0
121 | Special Education |  | 0 | Yes | 531 | 12 | 12
201 | Classroom | 320 | 21 | Yes | 989 | 22 | 22 | UV
202 | Classroom | 0 | 0 | Yes | 667 | 15 | 15 | UV
203 | Classroom | 418 | 27 |  | 989 | 22 | 22 | UV
204 | Classroom | 511 | 34 |  | 1012 | 23 | 23 | UV
205 | Classroom | 560 | 37 |  | 1012 | 23 | 23 | UV
206 | Classroom | 770 | 51 |  | 1012 | 23 | 23 | UV
207 | Classroom | 0 | 0 | Yes | 1012 | 23 | 23 | UV
208 | Classroom | 246 | 16 | Yes | 989 | 22 | 22 | UV
209 | Classroom | 446 | 29 |  | 1012 | 23 | 23 | UV
210A | Classroom | 233 | 15 |  | 504 | 11 | 11 | UV
210B | Classroom | 0 | 0 | Yes | 504 | 11 | 11 | UV
215 | Classroom | 0 | 0 | Yes | 874 | 19 | 19 | UV
216 | Classroom | 0 | 0 | Yes | 874 | 19 | 19 | UV
217 | Classroom | 220 | 14 | Yes | 874 | 19 | 19 | UV
218 | Classroom | 359 | 23 |  | 874 | 19 | 19 | UV
220 | Classroom | 232 | 15 | Yes | 1012 | 23 | 23 | UV
221 | Classroom | 441 | 29 |  | 1058 | 24 | 24 | UV
- | Principal |  | 0 | Yes | 387 | 8 | 8
- | Main Office |  | 0 | Yes | 784 | 17 | 17
- | Auditorium | 4864 | 324 |  | 5832 | 132 | 132 | AHU
Lamberton LSH
15 | Classroom | 313 | 20 | Yes | 928 | 21 | 21 | AHU
16 | Classroom | 299 | 19 | Yes | 928 | 21 | 21 | AHU
17 | Classroom | 317 | 21 |  | 928 | 21 | 21 | AHU
18 | Classroom | 329 | 21 |  | 928 | 21 | 21 | AHU
19 | Classroom | 291 | 19 | Yes | 928 | 21 | 21 | AHU
20 | Classroom | 295 | 19 | Yes | 928 | 21 | 21 | AHU
21 | Classroom | 316 | 21 |  | 928 | 21 | 21 | AHU
22 | Classroom | 324 | 21 |  | 928 | 21 | 21 | AHU
23 | Classroom | 314 | 20 | Yes | 928 | 21 | 21 | AHU
24 | Classroom | 327 | 21 |  | 928 | 21 | 21 | AHU
25 | Classroom | 287 | 19 | Yes | 928 | 21 | 21 | AHU
26 | Classroom | 303 | 20 | Yes | 928 | 21 | 21 | AHU
- | Main Office | 4 | 0 | Yes | 300 | 6 | 6 | AHU
- | Multi Purpose | 1539 | 102 |  | 1749 | 39 | 39 | AHU
- | Janitor | 0 | 0 |  | 80 | 1 | 0 | AHU

## Lankenau
Sheet Last Modified: | 2021-04-16
School: | Lankenau Environmental Science High School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
201 | Classroom | 407 | 27 |  | 585 | 13 | 13
205 | Classroom | 242 | 16 |  | 534 | 12 | 12
206 | Classroom | 183 | 12 |  | 529 | 12 | 12
207 | Classroom | 182 | 12 |  | 529 | 12 | 12
208 | Classroom | 178 | 11 |  | 522 | 11 | 11
210 | Classroom | 117 | 7 |  | 493 | 11 | 7
211 | Classroom | 120 | 8 |  | 475 | 10 | 8
212 | Classroom | 63 | 4 |  | 507 | 11 | 4
213 | Classroom | 63 | 4 |  | 531 | 12 | 4
214 | Classroom | 67 | 4 |  | 603 | 13 | 4
302 | Classroom | 84 | 5 |  | 586 | 13 | 5
303 | Classroom | 87 | 5 |  | 589 | 13 | 5
304 | Classroom | 85 | 5 |  | 573 | 13 | 5
305 | Classroom | 73 | 4 |  | 613 | 13 | 4
307 | Classroom | 516.5 | 34 |  | 1146 | 26 | 26
308 | 308 | 412 | 27 |  | 879 | 19 | 19
308B | 308B | 38 | 2 |  | 350 | 7 | 2
309 | Classroom | 611 | 40 |  | 1120 | 25 | 25
- | Auditorium storage 1 | 23 | 1 |  | 67 | 1 | 1
- | Auditorium storage 2 | 22 | 1 |  | 109 | 2 | 1
- | Botany / Storage area | 198 | 13 |  | 3264 | 74 | 13
- | Cafeteria | 706 | 47 |  | 1326 | 30 | 30
- | Cafeteria 2 (Small) | 158 | 10 |  | 518 | 11 | 10
- | Cafeteria 3 (Main) | 662 | 44 |  | 1536 | 34 | 34
- | Conference Room | 55 | 3 |  | 254 | 5 | 3
- | Counselors Office | 241 | 16 |  | 700 | 15 | 15
- | Dean's Office | 54 | 3 |  | 280 | 6 | 3
- | Gym | 606 | 40 |  | 2089 | 47 | 40
- | Lounge | 141 | 9 |  | 409 | 9 | 9
- | Main Office | 166 | 11 |  | 605 | 13 | 11
- | Music Assembly | 1020 | 68 |  | 2424 | 55 | 55
- | Nurse's Office | 44 | 2 |  | 247 | 5 | 2
- | Principal's office | 109 | 7 |  | 280 | 6 | 6
- | Science Storage | 60 | 4 |  | 355 | 8 | 4
202 | - |  | 0 |  | 585 | 13 | 13
203 | - |  | 0 |  | 527 | 11 | 11
204 | - |  | 0 |  | 535 | 12 | 13
209 | - |  | 0 |  | 535 | 12 | 13
- | Roster Chair |  | 0 |  | 156 | 3 | 3
306 | - |  | 0 |  | 900 | 20 | 20

## Lawton
Sheet Last Modified: | 2021-03-18
School: | Henry W. Lawton Elementary School
Vendor: | Devine Brothers | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 956 | 63 |  | 990 | 22 | 22 | UV
102 | Classroom | 407 | 27 |  | 990 | 22 | 22 | UV
103 | Classroom | 547 | 36 |  | 730 | 16 | 16 | UV
104 | Classroom | 327 | 21 |  | 796 | 18 | 18 | UV
105 | Classroom | 464 | 30 |  | 730 | 16 | 16 | UV
106 | Classroom | 432 | 28 |  | 796 | 18 | 18 | UV
107 | Classroom | 376 | 25 |  | 730 | 16 | 16 | UV
108 | Classroom | 641 | 42 |  | 676 | 15 | 15 | UV
109 | Classroom | 519 | 34 |  | 730 | 16 | 16 | UV
110 | Classroom | 699 | 46 |  | 676 | 15 | 15 | UV
111 | Classroom | 685 | 45 |  | 720 | 16 | 16 | UV
112 | Classroom | 929 | 61 |  | 930 | 21 | 21 | UV
113 | Classroom | 742 | 49 |  | 720 | 16 | 16 | UV
114 | Classroom | 705 | 47 |  | 930 | 21 | 21 | UV
115 | Classroom | 712 | 47 |  | 720 | 16 | 16 | UV
117 | Classroom | 671 | 44 |  | 720 | 16 | 16 | UV
119 | Classroom | 713 | 47 |  | 720 | 16 | 16 | UV
121 | Classroom | 571 | 38 |  | 720 | 16 | 16 | UV
123 | Classroom | 400 | 26 |  | 720 | 16 | 16 | UV
201 | Classroom | 411 | 27 |  | 816 | 18 | 18 | UV
202 | Classroom | 658 | 43 |  | 816 | 18 | 18 | UV
203 | Classroom | 455 | 30 |  | 816 | 18 | 18 | UV
204 | Classroom | 790 | 52 |  | 816 | 18 | 18 | UV
205 | Classroom | 802 | 53 |  | 816 | 18 | 18 | UV
206 | Classroom | 611 | 40 |  | 816 | 18 | 18 | UV
207 | Classroom | 814 | 54 |  | 720 | 16 | 16 | UV
208 | Classroom | 320 | 21 |  | 816 | 18 | 18 | UV
209 | Classroom | 653 | 43 |  | 720 | 16 | 16 | UV
211 | Classroom | 707 | 47 |  | 720 | 16 | 16 | UV
213 | Classroom | 649 | 43 |  | 720 | 16 | 16 | UV
214 | Classroom | 289 | 19 |  | 540 | 12 | 12 | UV
215 | Classroom | 730 | 48 |  | 720 | 16 | 16 | UV
216 | Classroom | 332 | 22 |  | 768 | 17 | 17 | UV
217 | Classroom | 364 | 24 |  | 720 | 16 | 16 | UV
218 | Classroom | 716 | 47 |  | 676 | 15 | 15 | UV
219 | Classroom | 672 | 44 |  | 720 | 16 | 16 | UV
220 | Classroom | 639 | 42 |  | 676 | 15 | 15 | UV
222 | Classroom | 683 | 45 |  | 540 | 12 | 12 | UV
224 | Classroom | 633 | 42 |  | 720 | 16 | 16 | UV
226 | Classroom | 1102 | 73 |  | 540 | 12 | 12 | UV
- | Art (Large) | 477 | 31 |  | 1258 | 28 | 28 | UV
- | Cafeteria | 632 | 42 |  | 2310 | 52 | 42 | AHU
- | Computer | 886 | 59 |  | 1440 | 32 | 32 | UV
- | IMC | 426 | 28 |  | 2620 | 59 | 28 | UV
- | Main Office | 232 | 15 |  | 275 | 6 | 6 | UV
- | Nurse's Office | 283 | 18 |  | 363 | 8 | 8 | UV
- | Science (Large) | 375 | 25 |  | 1088 | 24 | 24 | UV

## Lea
Sheet Last Modified: | 2021-04-26
School: | Henry C. Lea Elementary School
Vendor: | Devine | Chadwick | Devine Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
L1 | Classroom | 166 | 11 |  | 696 | 15 | 11 | UV
L3 | Classroom | 0 | 0 |  | 624 | 14 | 0 | UV
L4 | Classroom | 191 | 12 |  | 696 | 15 | 12 | UV
L5 | Classroom | 208 | 13 |  | 864 | 19 | 13 | UV
L7 | Classroom | 247 | 16 |  | 768 | 17 | 16 | UV
B2 | Classroom |  | 0 | Yes | 1457 | 33 | 33
101 | Classroom | 312 | 20 |  | 1225 | 27 | 20 | UV
102 | Classroom | 319 | 21 |  | 1295 | 29 | 21 | UV
103 | Classroom | 284 | 18 |  | 810 | 18 | 18 | AHU
105 | Classroom | 287 | 19 |  | 840 | 19 | 19 | AHU
106 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
107 | Classroom | 289 | 19 |  | 840 | 19 | 19 | AHU
108 | Classroom | 301 | 20 |  | 840 | 19 | 19 | AHU
109 | Classroom | 295 | 19 |  | 840 | 19 | 19 | AHU
110 | Classroom | 298 | 19 |  | 840 | 19 | 19 | AHU
111 | Classroom | 289 | 19 |  | 840 | 19 | 19 | AHU
125 | Counselor's Office |  | 0 | Yes | 126 | 2 | 2
127 | Classroom |  | 0 | Yes | 126 | 2 | 2
201 | Classroom | 0 | 0 | Yes | 1015 | 23 | 23 | UV
202 | Classroom | 0 | 0 | Yes | 980 | 22 | 22 | UV
203 | Classroom |  | 0 | Yes | 840 | 19 | 19 | AHU
204 | Classroom |  | 0 | Yes | 840 | 19 | 19
204a | Classroom | 0 | 0 | Yes | 252 | 5 | 5 | AHU
205 | Classroom | 0 | 0 | Yes | 810 | 18 | 18 | AHU
206 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | AHU
207 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
208 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
209 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
210 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
211 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
212 | Classroom | 0 | 0 | Yes | 212 | 4 | 4 | AHU
301/302 | Library | 380 | 25 | Yes | 5400 | 122 | 122 | UV
303 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
304 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | AHU
304A | Room |  | 0 | Yes | 266 | 6 | 6
306 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
307 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
308 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
309 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
310 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
311 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
312 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU
313 | Classroom | 0 | 0 |  | 840 | 19 | 0 | AHU
- | Auditorium | 0 | 0 |  | 2296 | 52 | 0 | AHU
- | Side Cafeteria | 490 | 32 | Yes | 1800 | 40 | 40 | AHU
- | Front Cafeteria | 352 | 23 | Yes | 1560 | 35 | 35 | AHU
- | Computer Lab | 276 | 18 |  | 1456 | 33 | 18 | AHU
- | Corridor | 156 | 10 |  | 650 | 14 | 10 | UV
- | Gym | 0 | 0 | Yes | 3950 | 89 | 89 | AHU
- | Main Office | 212 | 14 |  | 460 | 10 | 10 | AHU
- | Nurse's Bathroom | 0 | 0 |  | 28 | 0 | 0 | AHU
- | Nurse's Office |  | 0 | Yes | 168 | 3 | 3 | AHU
- | Nurse's Exam Room |  | 0 |  | 88 | 2 | 0 | AHU
- | Office Bathroom | 0 | 0 |  | 25 | 0 | 0 | AHU
- | Principal's Office | 0 | 0 | Yes | 160 | 3 | 3 | UV

## Levering (Amy Northwest)
Sheet Last Modified: | 2021-04-22
School: | Amy Northwest @ Levering Middle School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 |  | 749.66 | 17 | 0
103 | Classroom |  | 0 | Yes | 725.14 | 16 | 16
106 | Nurse Office |  | 0 | Yes | 668 | 15 | 15
107 | Classroom |  | 0 |  | 665.7 | 15 | 0
109 | IMC |  | 0 | Yes | 1457 | 33 | 33
203 | Classroom |  | 0 | Yes | 675.29 | 15 | 15
204 | Classroom |  | 0 | Yes | 683.29 | 15 | 15
205 | Classroom |  | 0 | Yes | 663.26 | 15 | 15
206 | Classroom |  | 0 |  | 691.01 | 15 | 0
207 | Classroom |  | 0 |  | 671.674 | 15 | 0
209 | Classroom |  | 0 | Yes | 685.4 | 15 | 15
210 | Classroom |  | 0 |  | 677.49 | 15 | 0
303/304 | Classroom |  | 0 | Yes | 1253.15 | 28 | 28
305 | Classroom |  | 0 | Yes | 674.85 | 15 | 15
306 | Classroom |  | 0 | Yes | 692.4 | 15 | 15
307 | Classroom |  | 0 | Yes | 670.32 | 15 | 15
310 | Classroom |  | 0 |  | 1065.17 | 24 | 0
Annex 1 | Classroom |  | 0 | Yes | 732.55 | 16 | 16
Annex 2 | Classroom |  | 0 | Yes | 709.22 | 16 | 16
Annex 3 | Classroom |  | 0 |  | 730.39 | 16 | 0
Annex 4 | Classroom |  | 0 | Yes | 707.12 | 16 | 16
Annex 5 | Classroom |  | 0 | Yes | 722.94 | 16 | 16

## Lincoln
Sheet Last Modified: | 2021-04-01
School: | Abraham Lincoln High School
Vendor: | Devine Brothers | EMCOR Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
2 | Room 2 Office | 93 | 6 |  | 576 | 13 | 6 | AHU #7
3 | Room 3 Storage | 99 | 6 |  | 576 | 13 | 6 | AHU #8
4 | Room 4 Electrical | 103 | 6 |  | 576 | 13 | 6 | AHU #9
5 | Room 5 Kitchen | 461 | 30 |  | 576 | 13 | 13 | AHU #10
6 | Child Care | 1116 | 74 |  | 576 | 13 | 13 | AHU #11
8 | Child Care | 2029 | 135 |  | 1665 | 37 | 37 | AHU #12
100 | Classroom | 760 | 50 |  | 363 | 8 | 8 | UV1+UV2+AHU-2
100A | Classroom | 615 | 41 |  |  | 0 | 0 | UV+AHU-2
101 | Classroom | 1715 | 114 |  | 1247 | 28 | 28 | UV1+UV2+AHU-2
102 | Classroom | 1244 | 82 |  | 130 | 2 | 2 | UV+AHU-2
102A | Office | 25 | 1 |  | 140 | 3 | 1 | AHU-2
102B | Office | 35 | 2 |  | 107 | 2 | 2 | AHU-2
103 | Classroom | 1636 | 109 |  | 1410 | 32 | 32 | UV1+UV2+AHU-2
104 | Classroom | 1067 | 71 |  | 806 | 18 | 18 | UV1+UV2+AHU-2
105 | Classroom | 1322 | 88 |  | 1140 | 25 | 25 | UV1+UV2+AHU-2
106 | Classroom | 1182 | 78 |  | 957 | 21 | 21 | UV1+UV2+AHU-2
107 | Classroom | 1894 | 126 |  | 1426 | 32 | 32 | UV1+UV2+AHU-2
107A | Storage Room | 300 | 20 |  |  | 0 | 0 | AHU-1
108 | Classroom | 1212 | 80 |  | 899 | 20 | 20 | UV1+UV2+AHU-2
109 | 109 OFFICE | 144 | 9 |  | 99 | 2 | 2 | AHU-2 / FC
110 | Classroom | 1159 | 77 |  | 868 | 19 | 19 | UV1+UV2+AHU-1
111 | Classroom | 1827 | 121 |  | 1426 | 32 | 32 | UV1+UV2+AHU-1
112 | Classroom | 990 | 66 |  | 868 | 19 | 19 | UV1+UV2+AHU-1
114 | Classroom | 1114 | 74 |  | 837 | 19 | 19 | UV1+UV2+AHU-1
116 | Classroom | 663 | 44 |  | 896 | 20 | 20 | UV1+UV2+AHU-1
118 | Classroom | 932 | 62 |  | 1748 | 39 | 39 | UV1+UV2+AHU-1
120 | Classroom | 1141 | 76 |  | 864 | 19 | 19 | UV1+UV2+AHU-1
121 | Classroom | 1025 | 68 |  | 945 | 21 | 21 | UV1+UV2+AHU-1
122 | Classroom | 941 | 62 |  | 837 | 19 | 19 | UV1+UV2+AHU-1
123 | Classroom | 1848 | 123 |  | 2208 | 50 | 50 | UV1+UV2+UV1+UV2+AHU-1
124 | Classroom | 865 | 57 |  | 837 | 19 | 19 | UV1+UV2+AHU-1
125 | Classroom | 984 | 65 |  | 888 | 20 | 20 | UV1+UV2+AHU-1
126 | Classroom | 843 | 56 |  | 837 | 19 | 19 | UV1+UV2+AHU-1
128 | Classroom | 598 | 39 |  | 837 | 19 | 19 | UV1+UV2+AHU-1
129 | Classroom | 740 | 49 |  | 890 | 20 | 20 | UV1+UV2+AHU-1
130 | Security | 0 | 0 |  | 108 | 2 | 0 | AHU-4
131 | Police | 0 | 0 |  | 180 | 4 | 0 | AHU-4
132 | Classroom | 728 | 48 |  |  | 0 | 0 | UV1+UV2+UV3+UV4
133a | book room | 0 | 0 |  |  | 0 | 0 | AHU-4
135 | Classroom | 0 | 0 |  | 840 | 19 | 0 | UV1+UV2
136 | office | 0 | 0 |  | 140 | 3 | 0 | AHU-4
136a | storage | 0 | 0 |  |  | 0 | 0 | AHU-4
137 | storage | 0 | 0 |  |  | 0 | 0 | AHU-4
137a | storage | 0 | 0 |  |  | 0 | 0 | AHU-4
139 | office | 0 | 0 |  | 74.75 | 1 | 0 | AHU-4
140 | Main Office and waiting | 0 | 0 |  | 338 | 7 | 0 | AHU-4
141 | Office | 0 | 0 |  |  | 0 | 0 | AHU-4
142 | Office | 0 | 0 |  |  | 0 | 0 | AHU-4
143 | Office | 0 | 0 |  | 99 | 2 | 0 | AHU-4
144 | Office | 0 | 0 |  | 105 | 2 | 0 | AHU-4
145 | Office | 0 | 0 |  | 110 | 2 | 0 | AHU-4
146 | Work Room | 0 | 0 |  | 636 | 14 | 0 | AHU-4
147 | Conference | 0 | 0 |  | 192 | 4 | 0 | AHU-4
147A | records | 0 | 0 |  | 300 | 6 | 0 | AHU-4
149 | Health Suite | 0 | 0 |  | 495 | 11 | 0 | AHU-4
149a | Exam | 0 | 0 |  | 188 | 4 | 0 | AHU-4
149b | Exam | 0 | 0 |  | 197 | 4 | 0 | AHU-4
149c | Office | 0 | 0 |  | 197 | 4 | 0 | AHU-4
149D | Office | 0 | 0 |  | 109 | 2 | 0 | AHU-4
149E | Meditation | 0 | 0 |  | 209 | 4 | 0 | AHU-4
150 | office | 0 | 0 |  | 117 | 2 | 0 | AHU-4
151 | copy center | 0 | 0 |  | 418 | 9 | 0 | AHU-4
154 | office | 0 | 0 |  | 117 | 2 | 0 | AHU-4
155 | office | 0 | 0 |  | 121 | 2 | 0 | AHU-4
156 | work room | 0 | 0 |  | 875 | 19 | 0 | AHU-4
157 | Records | 0 | 0 |  | 96 | 2 | 0 | AHU-4
158 | Roster Room | 0 | 0 |  | 143 | 3 | 0 | AHU-4
159 | Office | 0 | 0 |  | 96 | 2 | 0 | AHU-4
160 | Classroom | 1346 | 89 |  | 1428 | 32 | 32 | UV1+UV2+AHU-3
160's | Men's Staff Restroom | 740 | 49 |  |  | 0 | 0 | AHU-3
160's | Women's Staff Restroom | 685 | 45 |  |  | 0 | 0 | AHU-3
160A | Science Prep | 423 | 28 |  | 891 | 20 | 20 | AHU-3
161 | Classroom | 829 | 55 |  | 891 | 20 | 20 | UV1+UV2+AHU-3
162 | Classroom | 1327 | 88 |  | 688 | 15 | 15 | UV1+UV2+AHU-3
163 | Classroom | 895 | 59 |  | 868 | 19 | 19 | UV1+UV2+AHU-3
164 | Classroom | 1334 | 88 |  | 1419 | 32 | 32 | UV1+UV2+AHU-3
164a | Science Prep | 44 | 2 |  |  | 0 | 0 | AHU-3
165 | Classroom | 942 | 62 |  | 868 | 19 | 19 | UV1+UV2+AHU-3
166 | Classroom | 1071 | 71 |  | 1155 | 26 | 26 | UV1+UV2+AHU-3
167 | Classroom | 458 | 30 |  | 918 | 20 | 20 | UV1+UV2+AHU-3
168 | Classroom | 1150 | 76 |  | 868 | 19 | 19 | UV1+UV2+AHU-3
169 | Classroom | 684 | 45 |  | 952 | 21 | 21 | UV1+UV2+AHU-3
170 | Classroom | 787 | 52 |  | 891 | 20 | 20 | UV+UV+AHU-3
171 | Classroom | 1006 | 67 |  | 918 | 20 | 20 | UV1+UV2+AHU-3
172 | Classroom | 994 | 66 |  | 891 | 20 | 20 | UV1+UV2+AHU-3
173 | Classroom | 565 | 37 |  | 891 | 20 | 20 | AHU-3
174 | Classroom | 736 | 49 |  | 896 | 20 | 20 | UV1+UV2+AHU-3
175 | Classroom | 1415 | 94 |  | 891 | 20 | 20 | UV1+UV2+AHU-3
176 | Classroom | 903 | 60 |  | 800 | 18 | 18 | UV1+UV2+AHU-3
177 | Classroom | 867 | 57 |  | 918 | 20 | 20 | UV1+UV2+AHU-3
190 | Music Classroom | 1656 | 110 |  | 1395 | 31 | 31 | AHU-8
190 | Office | 82 | 5 |  | 225 | 5 | 5 | AHU-8
190 | Storage | 52 | 3 |  | 1716 | 39 | 3 | AHU-8
190A | Classroom | 315 | 21 |  | 90 | 2 | 2 | AHU-8
190D | Classroom | 166 | 11 |  | 623 | 14 | 11 | AHU-8
190E | Classroom | 191 | 12 |  | 336 | 7 | 7 | AHU-8
191 | Music Classroom | 1393 | 92 |  | 2100 | 47 | 47 | AHU-8
191A | Classroom | 68 | 4 |  | 56 | 1 | 1 | AHU-8
191B | Classroom | 72 | 4 |  | 90 | 2 | 2 | AHU-8
191C | Classroom | 83 | 5 |  | 90 | 2 | 2 | AHU-8
192 | Classroom | 998 | 66 |  | 1189 | 27 | 27 | AHU-8
200 | Classroom | 1117 | 74 |  | 1240 | 28 | 28 | UV1+UV2+AHU-2
201 | Classroom | 1325 | 88 |  | 1485 | 33 | 33 | UV1+UV2+AHU-2
201A | Science Prep | 255 | 17 |  | 1486 | 33 | 17 | AHU-2
202 | Classroom | 1325 | 88 |  | 2270 | 51 | 51 | UV1+UV2+UV3+AHU-2
202A | Office | 44 | 2 |  | 99 | 2 | 2 | AHU-2
203 | Classroom | 1339 | 89 |  | 1575 | 35 | 35 | UV1+UV2+AHU-2
204 | Classroom | 403 | 26 |  | 806 | 18 | 18 | UV1+UV2+AHU-2
205 | Classroom | 652 | 43 |  | 1395 | 31 | 31 | UV1+UV2+AHU-2
206 | Office Suite toilet |  | 0 |  | 1254 | 28 | 0 | AHU-2
207 | Classroom | 1006 | 67 |  | 891 | 20 | 20 | UV1+UV2+AHU-2
208 | Classroom | 759 | 50 |  | 1152 | 26 | 26 | UV1+UV2+AHU-2
209 | Classroom | 419 | 27 |  | 864 | 19 | 19 | UV1+UV2+AHU-2
210 | Classroom | 614 | 40 |  | 837 | 19 | 19 | UV1+UV2+AHU-2
211 | Classroom | 994 | 66 |  | 390 | 8 | 8 | UV1+UV2+AHU-1
212 | Classroom | 615 | 41 |  | 858 | 19 | 19 | UV1+UV2+AHU-2
213 | Classroom | 995 | 66 |  | 891 | 20 | 20 | UV1+UV2+AHU-1
214 | Classroom | 625 | 41 |  | 924 | 21 | 21 | UV1+UV2+AHU-1
216 | Classroom | 564 | 37 |  | 918 | 20 | 20 | UV1+UV2+AHU-1
218 | Classroom | 729 | 48 |  | 837 | 19 | 19 | UV1+UV2+AHU-1
220 | Classroom | 1242 | 82 |  | 1395 | 31 | 31 | UV1+UV2+AHU-1
221 | Classroom | 653 | 43 |  | 924 | 21 | 21 | UV1+UV2+AHU-1
222 | Classroom | 909 | 60 |  | 891 | 20 | 20 | UV1+UV2+AHU-1
223 | Classroom | 848 | 56 |  | 864 | 19 | 19 | UV1+UV2+AHU-1
224 | Classroom | 2035 | 135 |  | 1972 | 44 | 44 | UV1+UV2+UV3+UV4+AHU-1
224A | Office | 96 | 6 |  | 121 | 2 | 2 | AHU-1
225 | Classroom | 639 | 42 |  | 918 | 20 | 20 | UV1+UV2+AHU-1
226 | Classroom | 1282 | 85 |  | 1870 | 42 | 42 | UV1+UV2+UV3+UV4+AHU-1
226A | Office | 41 | 2 |  | 123 | 2 | 2 | AHU-1
227 | Classroom | 825 | 55 |  | 891 | 20 | 20 | UV1+UV2+AHU-1
228 | Classroom | 551 | 36 |  | 924 | 21 | 21 | UV1+UV2+AHU-1
229 | Classroom | 800 | 53 |  | 878 | 19 | 19 | UV1+UV2+AHU-1
- | 2nd floor Corridor | 1498 | 99 |  |  | 0 | 0 | AHU-1
- | Gym | 40145 | 2676 |  | 18327 | 416 | 416 | AHU-9+AHU-10
- | 2nd Floor B Corridor | 543 | 36 |  |  | 0 | 0 | AHU-2
- | 2nd Floor Staff toilet |  | 0 |  |  | 0 | 0 | AHU-2
- | Auditorium | 16961 | 1130 |  | 6745 | 153 | 153 | AHU-6
- | Small Gym | 0 | 0 |  | 6438 | 146 | 0 | AHU-11
- | Weight Room | 0 | 0 |  | 2450 | 55 | 0 | AHU-12
- | Counselor Center | 0 | 0 |  |  | 0 | 0 | AHU-4
- | Child Care- Hallway | 240 | 16 |  |  | 0 | 0 | AHU #13
- | Child Care- Kitchen | 47 | 3 |  | 330 | 7 | 3 | AHU-7
- | Child Care- Lending Library | 96 | 6 | Yes | 1184 | 26 | 26 | AHU-7
- | Library/IMC | 1522 | 101 |  | 8640 | 196 | 101 | AHU #14
- | Child Care Office | 9 | 0 |  | 99 | 2 | 0 | AHU-7
- | Admin 140's Area Corridor | 0 | 0 |  | 375 | 8 | 0 | AHU-4
- | Gym Office |  | 0 |  | 343 | 7 | 0
- | Gym office 2 |  | 0 |  | 280 | 6 | 0
- | Gym office 3 |  | 0 |  | 260 | 5 | 0

## Lingelbach
Sheet Last Modified: | 2021-04-12
School: | Lingelbach Elementary School
Vendor: | Devine Brothers | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 227 | 15 |  | 968 | 22 | 15 | UV
102 | Classroom | 477 | 31 |  | 968 | 22 | 22 | UV
103 | Classroom | 219 | 14 |  | 889 | 20 | 14 | UV
104 | Classroom | 0 | 0 |  | 963 | 21 | 0 | UV
105 | Classroom | 268 | 17 |  | 941 | 21 | 17 | UV
106 | Classroom | 293 | 19 |  | 971 | 22 | 19 | UV
200 | Classroom | 444 | 29 |  | 1394 | 31 | 29 | UV
200A | Classroom | 675 | 45 |  | 1235 | 28 | 28 | UV
201 | Classroom | 514 | 34 |  | 969 | 22 | 22 | UV
202 | Classroom | 280 | 18 |  | 969 | 22 | 18 | UV
203 | Classroom | 278 | 18 |  | 971 | 22 | 18 | UV
204 | Classroom | 290 | 19 |  | 971 | 22 | 19 | UV
205 | Classroom | 336 | 22 |  | 955 | 21 | 21 | UV
206 | Classroom | 278 | 18 |  | 969 | 22 | 18 | UV
301 | Classroom | 285 | 19 |  | 940 | 21 | 19 | UV
302 | Classroom | 795 | 53 |  | 937 | 21 | 21 | UV
303 | Classroom | 837 | 55 |  | 933 | 21 | 21 | UV
303A | Classroom | 357 | 23 |  | 463 | 10 | 10 | UV
304 | Classroom | 406 | 27 |  | 464 | 10 | 10 | UV
305 | Classroom | 395 | 26 |  | 967 | 21 | 21 | UV
306 | Classroom | 906 | 60 |  | 944 | 21 | 21 | UV
- | Main Office |  | 0 | Yes | 332 | 7 | 7
- | Principals Office |  | 0 | Yes | 262 | 5 | 5
- | Nurses Office |  | 0 | Yes | 269 | 6 | 6
- | Auditorium | 841 | 56 |  | 2847 | 64 | 56 | AHU
- | Gym/Cafeteria | 1451 | 96 |  | 2340 | 53 | 53 | AHU
- | North Stairwell | 0 | 0 |  | 168 | 3 | 0 | UV
- | South Stairwell | 0 | 0 |  | 168 | 3 | 0 | UV
- | Library | 855 | 57 |  | 2312 | 52 | 52 | UV

## Locke
Sheet Last Modified: | 2021-04-05
School: | Alain Locke Elementary School
Vendor: | Devine Brothers | Devine Brothers Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium | 2700 | 180 |  | 3658 | 83 | 83 | AHU
- | Gym/Cafeteria | 2014 | 134 |  | 4464 | 101 | 101 | AHU
- | Library | 585 | 39 |  | 1352 | 30 | 30 | UV
- | Main Office | 425 | 28 |  | 1213 | 27 | 27 | UV
- | Principals Office | 0 | 0 | Yes | 384 | 8 | 8 | UV
100 | Classroom | 421 | 28 |  | 840 | 19 | 19 | UV
101 | Classroom | 454 | 30 |  | 840 | 19 | 19 | UV
102 | Classroom | 425 | 28 |  | 864 | 19 | 19 | UV
103 | Classroom | 318 | 21 |  | 432 | 9 | 9 | UV
104 | Classroom | 405 | 27 |  | 744 | 16 | 16 | UV
105 | Classroom | 453 | 30 |  | 840 | 19 | 19 | UV
107 | Classroom | 435 | 29 |  | 1064 | 24 | 24 | UV
108A | Office A Library |  | 0 | Yes | 156 | 3 | 3
108B | Office B Library |  | 0 | Yes | 156 | 3 | 3
109 | Classroom | 428 | 28 |  | 864 | 19 | 19 | UV
111 | Classroom | 394 | 26 |  | 840 | 19 | 19 | UV
112 | Classroom | 330 | 22 |  | 840 | 19 | 19 | UV
113 | Classroom | 416 | 27 |  | 980 | 22 | 22 | UV
115 | Classroom | 393 | 26 |  | 1248 | 28 | 26 | UV
116A | Counselor Office |  | 0 | Yes | 132 | 3 | 3
116B | COVID Quarantine |  | 0 | Yes | 132 | 3 | 3
117 | Classroom | 321 | 21 |  | 1440 | 32 | 21 | UV
200 | Classroom | 592 | 39 |  | 875 | 19 | 19 | UV
201 | Classroom | 340 | 22 |  | 864 | 19 | 19 | UV
202 | Classroom | 341 | 22 |  | 875 | 19 | 19 | UV
203 | Classroom | 485 | 32 |  | 864 | 19 | 19 | UV
204 | Classroom | 279 | 18 |  | 875 | 19 | 18 | UV
205 | Classroom | 295 | 19 |  | 864 | 19 | 19 | UV
207A | Classroom | 0 | 0 | Yes | 168 | 3 | 3 | UV
207B | Classroom | 300 | 20 |  | 336 | 7 | 7 | UV
208 | Classroom | 349 | 23 |  | 1225 | 27 | 23 | UV
209 | Classroom | 348 | 23 |  | 864 | 19 | 19 | UV
210 | Classroom | 295 | 19 |  | 480 | 10 | 10 | UV
211 | Classroom | 360 | 24 |  | 864 | 19 | 19 | UV
212 | Classroom | 332 | 22 |  | 840 | 19 | 19 | UV
213 | Classroom | 297 | 19 |  | 875 | 19 | 19 | UV
300 | Classroom | 419 | 27 |  | 840 | 19 | 19 | UV
301 | Classroom | 416 | 27 |  | 840 | 19 | 19 | UV
302 | Classroom | 375 | 25 |  | 840 | 19 | 19 | UV
303 | Classroom | 395 | 26 |  | 840 | 19 | 19 | UV
304 | Classroom | 398 | 26 |  | 840 | 19 | 19 | UV
305 | Classroom | 411 | 27 |  | 840 | 19 | 19 | UV
307A | Office | 205 | 13 |  | 336 | 7 | 7 | UV
307B | Office | 0 | 0 | Yes | 168 | 3 | 3 | UV
308 | Classroom | 383 | 25 |  | 864 | 19 | 19 | UV
309 | Classroom | 365 | 24 |  | 840 | 19 | 19 | UV
310 | Classroom | 325 | 21 |  | 875 | 19 | 19 | UV
311 | Classroom | 309 | 20 |  | 840 | 19 | 19 | UV
312 | Classroom | 419 | 27 |  | 840 | 19 | 19 | UV
313 | Classroom | 346 | 23 |  | 840 | 19 | 19 | UV
- | Nurses office |  | 0 | Yes | 352 | 8 | 8 | UV

## Loesche
Sheet Last Modified: | 2021-04-08
School: | William Loesche Elementary School
Vendor: | Devine Brothers | Devine Brothers Retest
Devine Brothers 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 286 | 19 |  | 840 | 19 | 19 | UV
101 | Classroom | 282 | 18 |  | 840 | 19 | 18 | UV
102 | Classroom | 82 | 5 | Yes | 784 | 17 | 17 | UV
103 | Classroom | 288 | 19 |  | 840 | 19 | 19 | UV
104 | Classroom | 0 | 0 |  | 840 | 19 | 0 | UV
105 | Classroom | 300 | 20 |  | 840 | 19 | 19 | UV
107 | Classroom | 288 | 19 |  | 840 | 19 | 19 | UV
108 | Classroom | 213 | 14 | Yes | 1122 | 25 | 25 | UV
109 | Classroom | 185 | 12 |  | 840 | 19 | 12 | UV
110 | Classroom | 156 | 10 | Yes | 840 | 19 | 19 | UV
111 | Classroom | 190 | 12 | Yes | 882 | 20 | 20 | UV
112 | Classroom | 285 | 19 |  | 729.24 | 16 | 16 | UV
200 | Classroom | 258 | 17 |  | 840 | 19 | 17 | UV
201 | Classroom | 292 | 19 |  | 840 | 19 | 19 | UV
202 | Classroom | 283 | 18 |  | 840 | 19 | 18 | UV
203 | Classroom | 158 | 10 | Yes | 840 | 19 | 19 | UV
204 | Classroom | 262 | 17 |  | 840 | 19 | 17 | UV
205 | Classroom | 205 | 13 | Yes | 840 | 19 | 19 | UV
206 | Classroom | 153 | 10 |  | 476 | 10 | 10 | UV
207 | Classroom | 297 | 19 |  | 840 | 19 | 19 | UV
208 | Classroom | 210 | 14 |  | 840 | 19 | 14 | UV
208A | Classroom | 150 | 10 |  | 252 | 5 | 5 | UV
209 | Classroom | 184 | 12 | Yes | 840 | 19 | 19 | UV
210 | Classroom | 193 | 12 |  | 780 | 17 | 12 | UV
211 | Classroom | 142 | 9 | Yes | 783 | 17 | 17 | UV
212 | Classroom | 267 | 17 |  | 840 | 19 | 17 | UV
214 | Classroom | 280 | 18 |  | 1212 | 27 | 18 | UV
215 | Classroom | 268 | 17 |  | 1232 | 28 | 17 | UV
216 | Classroom | 415 | 27 |  | 756 | 17 | 17 | UV
217 | Classroom | 276 | 18 |  | 841 | 19 | 18 | UV
218 | Classroom | 144 | 9 | Yes | 840 | 19 | 19 | UV
219 | Classroom | 106 | 7 | Yes | 840 | 19 | 19 | UV
220 | Classroom | 246 | 16 |  | 870 | 19 | 16 | UV
221 | Classroom | 140 | 9 |  | 870 | 19 | 9 | UV
222 | Classroom | 106 | 7 |  | 840 | 19 | 7 | UV
223 | Classroom | 175 | 11 |  | 840 | 19 | 11 | UV
224 | Classroom | 94 | 6 |  | 840 | 19 | 6 | UV
A-1 | Classroom | 242 | 16 |  | 884 | 20 | 16 | UV
A-2 | Classroom | 254 | 16 |  | 884 | 20 | 16 | UV
A-3 | Classroom | 298 | 19 |  | 884 | 20 | 19 | UV
A-4 | Classroom | 281 | 18 |  | 884 | 20 | 18 | UV
- | A-wing Mech. Rm | 0 | 0 |  | 357.96 | 8 | 0 | UV
- | Auditorium | 0 | 0 |  | 3600 | 81 | 0 | AHU
B-1 | Classroom | 314 | 20 |  | 806 | 18 | 18 | UV
B-2 | Classroom | 311 | 20 |  | 806 | 18 | 18 | UV
B-3 | Classroom | 300 | 20 |  | 806 | 18 | 18 | UV
B-4 | Classroom | 313 | 20 |  | 806 | 18 | 18 | UV
B-5 | Classroom | 287 | 19 |  | 806 | 18 | 18 | UV
B-6 | Classroom | 297 | 19 |  | 905 | 20 | 19 | UV
B-7 | Classroom | 285 | 19 |  | 905 | 20 | 19 | UV
B-8 | Classroom | 304 | 20 |  | 905 | 20 | 20 | UV
B-9 | Classroom | 282 | 18 |  | 905 | 20 | 18 | UV
- | Backstage | 0 | 0 |  | 180 | 4 | 0 | UV
- | Backstage Dressing Rm. | 172 | 11 |  | 252 | 5 | 5 | UV
- | Cafeteria | 0 | 0 | Yes | 5540 | 125 | 125 | AHU
- | GYM | 0 | 0 |  | 4495.5 | 102 | 0 | AHU
- | Library | 0 | 0 |  | 1131 | 25 | 0 | UV
- | Main Office | 292 | 19 |  | 992 | 22 | 19 | UV
- | Nurse's Office | 94 | 6 |  | 706.42 | 16 | 6 | UV
- | Principal's Office | 148 | 9 |  | 308 | 7 | 7 | UV

## Logan
Sheet Last Modified: | 2021-03-24
School: | James Logan Elementary-Middle School |  |  | House Fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B-1 | Classroom | 1228 | 81 |  | 889 | 20 | 20 | House Fan
B-2 | Classroom | 975 | 65 |  | 737 | 16 | 16 | House Fan
B-3 | Classroom | 1131 | 75 |  | 1017 | 23 | 23 | House Fan
101 | Classroom | 539 | 35 |  | 729 | 16 | 16 | House Fan
102 | Classroom | 578 | 38 |  | 732 | 16 | 16 | House Fan
103 | Classroom | 593 | 39 |  | 724 | 16 | 16 | House Fan
104 | Classroom | 674 | 44 |  | 676 | 15 | 15 | House Fan
104A | Office | 0 | 0 |  | 177 | 4 | 0 | House Fan
105 | Teacher's Lounge | 617 | 41 |  | 650 | 14 | 14 | House Fan
106 | Classroom | 621 | 41 |  | 726 | 16 | 16 | House Fan
107 | Classroom | 376 | 25 |  | 722 | 16 | 16 | House Fan
108 | Classroom | 849 | 56 |  | 717 | 16 | 16 | House Fan
201 | IMC | 509 | 33 |  | 639 | 14 | 14 | House Fan
202 | IMC | 632 | 42 |  | 639 | 14 | 14 | House Fan
203 | Classroom | 551 | 36 |  | 720 | 16 | 16 | House Fan
204 | Office Storage | 0 | 0 |  | 201 | 4 | 0 | House Fan
205 | Classroom | 519 | 34 |  | 718 | 16 | 16 | House Fan
205A | Office | 0 | 0 |  | 164 | 3 | 0 | House Fan
206 | Classroom | 715 | 47 |  | 735 | 16 | 16 | House Fan
206A | Counselor | 0 | 0 |  | 231 | 5 | 0 | House Fan
207 | Classroom | 394 | 26 |  | 723 | 16 | 16 | House Fan
208 | Classroom | 423 | 28 |  | 724 | 16 | 16 | House Fan
209 | Classroom | 575 | 38 |  | 725 | 16 | 16 | House Fan
209A | Classroom | 0 | 0 |  | 260 | 5 | 0 | House Fan
301 | Classroom | 522 | 34 |  | 679 | 15 | 15 | House Fan
302 | Classroom | 549 | 36 |  | 679 | 15 | 15 | House Fan
303 | Classroom | 458 | 30 |  | 724 | 16 | 16 | House Fan
304 | Classroom | 481 | 32 |  | 714 | 16 | 16 | House Fan
305 | Classroom | 347 | 23 |  | 890 | 20 | 20 | House Fan
306 | Classroom | 381 | 25 |  | 750 | 17 | 17 | House Fan
307 | Classroom | 312 | 20 |  | 992 | 22 | 20 | House Fan
308 | Classroom | 466 | 31 |  | 751 | 17 | 17 | House Fan
309 | Classroom | 508 | 33 |  | 992 | 22 | 22 | House Fan
310 | Classroom | 477 | 31 |  | 720 | 16 | 16 | House Fan
311 | Classroom | 409 | 27 |  | 703 | 15 | 15 | House Fan
312 | Classroom | 491 | 32 |  | 730 | 16 | 16 | House Fan
313 | Classroom | 570 | 38 |  | 721 | 16 | 16 | House Fan
- | Auditorium | 2427 | 161 |  | 3685 | 83 | 83 | House Fan
- | Boys' Bathroom | 125 | 8 |  | 561 | 12 | 8 | N/A
- | Girls' Bathroom | 73 | 4 |  | 547 | 12 | 4 | N/A
- | Cafeteria | 1258 | 83 |  | 1726 | 39 | 39 | House Fan
- | Speech Classroom | 0 | 0 | Yes | 192 | 4 | 4 | House Fan
- | Gym | 0 | 0 | Yes | 3970 | 90 | 90 | N/A
- | Nurse's Office | 0 | 0 | Yes | 220 | 5 | 5 | House Fan
- | IMC Office | 0 | 0 |  | 158 | 3 | 0 | House Fan
- | Main Office | 0 | 0 | Yes | 333 | 7 | 7 | House Fan
- | Principal's Office | 0 | 0 | Yes | 342 | 7 | 7 | House Fan

## Longstreth
Sheet Last Modified: | 2021-03-26
School: | W.C. Longstreth Elementary School
Vendor: | EMCOR Fluidics | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100D | Faculty Dining | 96 | 6 |  | 625 | 14 | 6 | AHU-6
102 | Main Office | 110 | 7 |  | 646 | 14 | 7 | AHU-6
102C | Principal Office | 77 | 5 |  | 225 | 5 | 5 | AHU-6
102D | Comference Room | 72 | 4 |  | 198 | 4 | 4 | AHU-6
103 | Classroom | 141 | 9 |  | 704 | 16 | 9 | AHU-1
105 | Classroom | 206 | 13 |  | 609 | 13 | 13 | AHU-1
106 | Art Room | 610 | 40 |  | 1333 | 30 | 30 | AHU-2
107 | Classroom | 468 | 31 |  | 1320 | 30 | 30 | AHU-1
109 | Classroom | 469 | 31 |  | 1276 | 29 | 29 | AHU-1
110 | Nurses Suite | 45 | 3 |  | 180 | 4 | 3 | AHU-6
110C | Nurses Office | 102 | 6 |  | 132 | 3 | 3 | AHU-6
110D | Audio Rm | 101 | 6 |  | 132 | 3 | 3 | AHU-6
110E | Audio Rm | 78 | 5 |  | 48 | 1 | 1 | AHU-6
111 | Classroom | 487 | 32 |  | 1232 | 28 | 28 | AHU-1
112A | Building Engineers Office | 90 | 6 |  | 88 | 2 | 2 | AHU-6
113 | Classroom | 361 | 24 |  | 1364 | 31 | 24 | AHU-1
200 | Library | 715 | 47 |  | 2859 | 64 | 47 | AHU-5
200A | Computer Lab | 119 | 7 |  | 704 | 16 | 7 | AHU-5
200B | Consortium | 67 | 4 |  | 552 | 12 | 4 | AHU-5
201 | Classroom | 403 | 26 |  | 818 | 18 | 18 | AHU-1
202 | Classroom | 360 | 24 |  | 510 | 11 | 11 | AHU-2
203 | Classroom | 321 | 21 |  | 544 | 12 | 12 | AHU-1
204 | Classroom | 206 | 13 | Yes | 510 | 11 | 11 | AHU-2
205 | Classroom | 273 | 18 |  | 544 | 12 | 12 | AHU-1
206 | Classroom | 364 | 24 |  | 510 | 11 | 11 | AHU-2
207 | Classroom | 419 | 27 |  | 544 | 12 | 12 | AHU-1
208 | Classroom | 309 | 20 |  | 510 | 11 | 11 | AHU-2
209 | Classroom | 417 | 27 |  | 544 | 12 | 12 | AHU-1
210 | Classroom | 276 | 18 |  | 510 | 11 | 11 | AHU-2
211 | Classroom | 88 | 5 |  | 576 | 13 | 5 | AHU-1
212 | Classroom | 304 | 20 |  | 765 | 17 | 17 | AHU-2
213 | Classroom | 303 | 20 |  | 810 | 18 | 18 | AHU-1
214 | Classroom - WEIGHT ROOM | 669 | 44 |  | 1204 | 27 | 27 | AHU-2
215 | Classroom | 141 | 9 |  | 285 | 6 | 6 | AHU-1
219 | Classroom | 175 | 11 |  | 220 | 5 | 5 | AHU-1
220 | Classroom | 61 | 4 |  | 612 | 13 | 4 | AHU-2
301 | Classroom | 311 | 20 |  | 595 | 13 | 13 | AHU-1
303 | Classroom | 323 | 21 |  | 561 | 12 | 12 | AHU-1
304 | Classroom | 220 | 14 |  | 570 | 12 | 12 | AHU-2
305 | Classroom | 316 | 21 |  | 577 | 13 | 13 | AHU-1
306 | Classroom | 462 | 30 |  | 510 | 11 | 11 | AHU-2
307 | Classroom | 331 | 22 |  | 577 | 13 | 13 | AHU-1
308 | Classroom | 327 | 21 |  | 510 | 11 | 11 | AHU-2
309 | Classroom | 356 | 23 |  | 594 | 13 | 13 | AHU-1
310 | Classroom | 320 | 21 |  | 527 | 11 | 11 | AHU-2
311 | Classroom | 340 | 22 |  | 576 | 13 | 13 | AHU-1
312 | Classroom | 332 | 22 |  | 544 | 12 | 12 | AHU-2
313 | Classroom | 422 | 28 |  | 840 | 19 | 19 | AHU-1
314 | Classroom | 577 | 38 |  | 1290 | 29 | 29 | AHU-2
315 | Classroom | 145 | 9 |  | 280 | 6 | 6 | AHU-1
319 | Classroom | 129 | 8 |  | 220 | 5 | 5 | AHU-1
320 | Classroom | 171 | 11 |  | 210 | 4 | 4 | AHU-2
- | Auditorium | 1337 | 89 |  | 3540 | 80 | 80 | AHU-3
- | Cafeteria | 2211 | 147 |  | 3658 | 83 | 83 | AHU-4
- | Diagnostic Center | 213 | 14 |  | 306 | 6 | 6 | AHU-6
- | Main Office Admin | 82 | 5 |  | 110 | 2 | 2 | AHU-6
- | Main Storage Room | 27 | 1 |  | 192 | 4 | 1 | AHU-6
- | Nurses Suite Laundry | 115 | 7 |  | 372 | 8 | 7 | AHU-6
- | Gym | 0 | 0 |  | 4720 | 107 | 0 | AHU 1 and 2

## Lowell
Sheet Last Modified: | 2021-03-26
School: | James R. Lowell Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B010A | Boys Bathroom | 725 | 48 |  | 667 | 15 | 15 | N/A
B10 | Music | 0 | 0 |  | 925 | 21 | 0 | N/A
B11 | Classroom | 346 | 23 |  | 695 | 15 | 15 | House Fan
B12 | Girls Bathroom | 305 | 20 |  | 695 | 15 | 15 | House Fan
B8 | Classroom | 175 | 11 |  | 576 | 13 | 11 | House Fan
B9 | Classroom | 388 | 25 |  | 667 | 15 | 15 | House Fan
100 | Classroom | 0 | 0 |  | 240 | 5 | 0 | House Fan
101 | Classroom | 285 | 19 |  | 566 | 12 | 12 | House Fan
102 | Classroom | 327 | 21 |  | 559 | 12 | 12 | House Fan
103 | Classroom | 325 | 21 |  | 100 | 2 | 2 | House Fan
104 | Classroom | 102 | 6 |  | 640 | 14 | 6 | House Fan
105 | Classroom | 593 | 39 |  | 654 | 14 | 14 | House Fan
106 | Classroom | 399 | 26 |  | 566 | 12 | 12 | House Fan
107 | Classroom | 0 | 0 |  | 667 | 15 | 0 | House Fan
108 | Classroom | 154 | 10 |  | 650 | 14 | 10 | House Fan
109 | Classroom | 304 | 20 |  | 602 | 13 | 13 | House Fan
110 | Classroom | 0 | 0 |  | 207 | 4 | 0 | House Fan
111 | Counselor |  | 0 |  | 154 | 3 | 0
200 | Classroom | 0 | 0 |  | 240 | 5 | 0 | House Fan
201 | Classroom | 300 | 20 |  | 654 | 14 | 14 | House Fan
202 | Computer Room |  | 0 |  | 810 | 18 | 0
203 | Classroom | 647 | 43 |  | 654 | 14 | 14 | House Fan
204 | Classroom | 457 | 30 |  | 650 | 14 | 14 | House Fan
205 | Classroom | 531 | 35 |  | 650 | 14 | 14 | House Fan
206 | Classroom | 247 | 16 |  | 695 | 15 | 15 | House Fan
207 | Classroom | 102 | 6 |  | 694 | 15 | 6 | House Fan
207 | Faculty Room | 0 | 0 |  | 207 | 4 | 0 | N/A
208 | Classroom | 200 | 13 |  | 695 | 15 | 13 | House Fan
209 | Classroom | 139 | 9 |  | 650 | 14 | 9 | House Fan
210 | Classroom | 275 | 18 |  | 560 | 12 | 12 | House Fan
211 | Classroom | 0 | 0 |  | 420 | 9 | 0 | House Fan
300 | Classroom | 0 | 0 |  | 240 | 5 | 0 | House Fan
301A | Classroom | 132 | 8 |  | 566 | 12 | 8 | House Fan
301B | Classroom | 139 | 9 |  | 300 | 6 | 6 | House Fan
302 | Classroom | 145 | 9 |  | 240 | 5 | 5 | House Fan
303 | Classroom | 318 | 21 |  | 666 | 15 | 15 | House Fan
304 | Classroom | 387 | 25 |  | 610 | 13 | 13 | House Fan
305 | Classroom | 432 | 28 |  | 620 | 14 | 14 | House Fan
306 | Classroom | 249 | 16 |  | 650 | 14 | 14 | House Fan
307 | Classroom | 325 | 21 |  | 650 | 14 | 14 | House Fan
308 | Classroom | 322 | 21 |  | 650 | 14 | 14 | House Fan
309 | Classroom | 262 | 17 |  | 654 | 14 | 14 | House Fan
310 | Classroom | 203 | 13 |  | 636 | 14 | 13 | House Fan
311 | Classroom | 0 | 0 |  | 221 | 5 | 0 | House Fan
312 | Classroom | 0 | 0 |  | 273 | 6 | 0 | House Fan
- | Library | 213 | 14 |  | 1040 | 23 | 14 | AHU
- | Entrance Lobby | 290 | 19 |  | 325 | 7 | 7 | N/A
- | Gym | 0 | 0 |  | 4368 | 99 | 0 | AHU
- | Music Rm | 127 | 8 |  | 286 | 6 | 6 | Unit Ventilator
S-11 | Classroom | 419 | 27 |  | 810 | 18 | 18 | Unit Ventilator
S-12 | Classroom | 906 | 60 |  | 692 | 15 | 15 | Unit Ventilator
S-13 | Classroom | 635 | 42 |  | 692 | 15 | 15 | Unit Ventilator
S-14 | Classroom | 715 | 47 |  | 695 | 15 | 15 | Unit Ventilator
S-15 | Classroom | 411 | 27 |  | 692 | 15 | 15 | Unit Ventilator
S-16 | Classroom | 502 | 33 |  | 692 | 15 | 15 | Unit Ventilator
S-17 | Classroom | 371 | 24 |  | 828 | 18 | 18 | Unit Ventilator
S-18 | Classroom | 482 | 32 |  | 828 | 18 | 18 | Unit Ventilator
S-19 | Classroom | 742 | 49 |  | 828 | 18 | 18 | Unit Ventilator
S-21 | Classroom | 429 | 28 |  | 640 | 14 | 14 | Unit Ventilator
S-22 | Classroom | 663 | 44 |  | 640 | 14 | 14 | Unit Ventilator
S-23 | Classroom | 480 | 32 |  | 654 | 14 | 14 | Unit Ventilator
S-24 | Classroom | 333 | 22 |  | 636 | 14 | 14 | Unit Ventilator
S-25 | Classroom | 844 | 56 |  | 636 | 14 | 14 | Unit Ventilator
S-26 | Classroom | 490 | 32 |  | 654 | 14 | 14 | Unit Ventilator
S-27 | Storage | 393 | 26 |  | 610 | 13 | 13 | Unit Ventilator
S-27 | Classroom | 266 | 17 |  | 610 | 13 | 13 | Unit Ventilator
S-28 | Classroom | 450 | 30 |  | 610 | 13 | 13 | Unit Ventilator
S-29 | Classroom | 260 | 17 |  | 610 | 13 | 13 | Unit Ventilator
S-30 | Teacher's Lounge | 378 | 25 |  | 858 | 19 | 19 | Unit Ventilator
S-31 | Office | 508 | 33 |  | 140 | 3 | 3 | Unit Ventilator
- | Main Office |  | 0 |  | 338 | 7 | 0
- | Principals Office |  | 0 |  | 364 | 8 | 0
- | Nurses Office |  | 0 |  | 240 | 5 | 0

## Ludlow
Sheet Last Modified: | 2021-04-27
School: | James R. Ludlow Elementary-Middle School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
3 | Art |  | 0 |  | 667 | 15 | 0 | House Fan
100B | Home and School |  | 0 |  | 121 | 2 | 0 | House Fan
100C | Counselor |  | 0 |  | 195 | 4 | 0 | House Fan
101 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
103 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan
104 | Classroom |  | 0 | Yes | 638 | 14 | 14 | House Fan
105 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
106 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
107 | Classroom |  | 0 |  | 920 | 20 | 0 | House Fan
108 | Classroom |  | 0 | Yes | 638 | 14 | 14 | House Fan
109 | Classroom |  | 0 | Yes | 841 | 19 | 19 | House Fan
110 | Counselor |  | 0 |  | 128 | 2 | 0 | House Fan
200 | Classroom |  | 0 | Yes | 552 | 12 | 12 | House Fan
201 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
202 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
203 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
204 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan
207 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
208 | Classroom |  | 0 | Yes | 667 | 15 | 15
209 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
211 | Classroom |  | 0 | Yes | 841 | 19 | 19 | House Fan
300 | Ladies lounge |  | 0 |  | 276 | 6 | 0 | House Fan
300A | Ladies lounge |  | 0 |  | 276 | 6 | 0 | House Fan
301 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
302 | Classroom |  | 0 | Yes | 782 | 17 | 17 | House Fan
303 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan
304 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
305 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan
306 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
307 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
308 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
309 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan
310 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
311 | Classroom |  | 0 | Yes | 406 | 9 | 9 | House Fan
- | Library |  | 0 | Yes | 1298 | 29 | 29 | House Fan
- | Gym |  | 0 | Yes | 5208 | 118 | 118
- | Kitchen |  | 0 | Yes | 1288 | 29 | 29 | House Fan
- | Lunchroom/Cafetorium |  | 0 |  | 3157 | 71 | 0 | House Fan
- | Main office |  | 0 | Yes | 322 | 7 | 7 | House Fan
- | Nurses Office |  | 0 | Yes | 128 | 2 | 2 | House Fan
- | Principals office |  | 0 | Yes | 165 | 3 | 3 | House Fan

## Marshall, J
Sheet Last Modified: | 2021-03-08
School: | John Marshall Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
102 | Classroom | 723 | 48 |  | 832 | 18 | 18 | House Fan
103 | Classroom | 653 | 43 |  | 449 | 10 | 10 | House Fan
104 | Classroom | 684 | 45 |  | 781 | 17 | 17 | House Fan
105 | Classroom | 717 | 47 |  | 738 | 16 | 16 | House Fan
106 | Classroom | 624 | 41 |  | 893 | 20 | 20 | House Fan
107 | Classroom | 575 | 38 |  | 623 | 14 | 14 | House Fan
200 | Classroom | 640 | 42 |  | 790 | 17 | 17 | House Fan
201 | Classroom | 692 | 46 |  | 803 | 18 | 18 | House Fan
202 | Classroom | 691 | 46 |  | 746 | 16 | 16 | House Fan
203 | Classroom | 556 | 37 |  | 770 | 17 | 17 | House Fan
204 | Classroom | 678 | 45 |  | 715 | 16 | 16 | House Fan
205 | Classroom | 765 | 51 |  | 225 | 5 | 5 | House Fan
206 | Classroom | 535 | 35 |  | 548 | 12 | 12 | House Fan
300 | Classroom | 596 | 39 |  | 766 | 17 | 17 | House Fan
300A | Classroom |  | 0 | Yes | 510 | 11 | 11 | Wndow Fan
301 | Classroom | 531 | 35 |  | 884 | 20 | 20 | House Fan
302 | Classroom | 683 | 45 |  | 766 | 17 | 17 | House Fan
303 | Classroom | 785 | 52 |  | 748 | 17 | 17 | House Fan
304 | Classroom | 793 | 52 |  | 779 | 17 | 17 | House Fan
305 | Classroom | 668 | 44 |  | 757 | 17 | 17 | House Fan
306 | Classroom | 609 | 40 |  | 876 | 19 | 19 | House Fan
- | 1st Fl. Corridor | 1954 | 130 |  | 352 | 8 | 8 | N/A
- | Grnd. Fl. Boys Bathrm. | 402 | 26 |  | 234 | 5 | 5 | N/A
- | Grnd. Fl. Girls Bathrm. | 333 | 22 |  | 156 | 3 | 3 | N/A
- | Main Office | 343 | 22 |  | 298 | 6 | 6 | House Fan
- | Nurse / office | 340 | 22 |  | 420 | 9 | 9 | House Fan
- | Cafeteria |  | 0 | Yes | 3129 | 71 | 71 | Wndow Fan

## Marshall, T
Sheet Last Modified: | 2021-03-24
School: | Thurgood Marshall Elementary School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 99 | 6 | Yes | 875 | 19 | 19
101 | Classroom | 112 | 7 | Yes | 875 | 19 | 19
102 | Classroom | 53 | 3 | Yes | 875 | 19 | 19
103 | Classroom | 60 | 4 | Yes | 875 | 19 | 19
104 | Classroom | 310 | 20 |  | 589 | 13 | 13
105 | Classroom | 143 | 9 | Yes | 624 | 14 | 14
106 | Office | 154 | 10 |  | 143 | 3 | 3
106A | Office | 0 | 0 |  | 99 | 2 | 0
106B | Office | 0 | 0 |  | 99 | 2 | 0
106C | Office | 168 | 11 |  | 99 | 2 | 2
106D | Office | 180 | 12 |  | 126 | 2 | 2
106E | Office | 165 | 11 |  | 130 | 2 | 2
106G | Office | 191 | 12 |  | 130 | 2 | 2
106H | Hallway | 0 | 0 |  | 528 | 12 | 0
106 RR | Office | 513 | 34 |  | 52.5 | 1 | 1
107 | Classroom | 82 | 5 |  | 720 | 16 | 5
107-2 | Classroom | 0 | 0 |  | 215 | 4 | 0
107A | Classroom | 89 | 5 |  | 816 | 18 | 5
108 | Classroom | 38 | 2 |  | 506 | 11 | 2
108A | Classroom | 37 | 2 |  | 128 | 2 | 2
109 | Classroom | 71 | 4 |  | 1196 | 27 | 4
110 | Classroom | 382 | 25 |  | 682 | 15 | 15
111 | Classroom | 216 | 14 | Yes | 630 | 14 | 14
113A | Principals Office | 18 | 1 |  | 340 | 7 | 1
113D | Admin Office | 33 | 2 |  | 99 | 2 | 2
113E | Admin Office | 24 | 1 |  | 99 | 2 | 1
113F | Admin Office | 25 | 1 |  | 99 | 2 | 1
113G | Admin Office | 20 | 1 |  | 99 | 2 | 1
115 | Classroom | 142 | 9 |  | 782 | 17 | 9
200 | Classroom | 88 | 5 |  | 875 | 19 | 5
201 | Classroom | 157 | 10 | Yes | 875 | 19 | 19
202 | Classroom | 75 | 5 | Yes | 875 | 19 | 19
203 | Classroom | 73 | 4 | Yes | 875 | 19 | 19
204 | Classroom | 90 | 6 | Yes | 993 | 22 | 22
205 | Classroom | 53 | 3 |  | 327.75 | 7 | 3
206A | Classroom | 42 | 2 |  | 154 | 3 | 2
206B | Classroom | 31 | 2 |  | 270 | 6 | 2
206C | Classroom | 49 | 3 |  | 127 | 2 | 2
207 | Library | 519 | 34 |  | 2108 | 47 | 34
208 | Computer Lab | 73 | 4 | Yes | 1024 | 23 | 23
209 | Music Room | 0 | 0 |  | 1171 | 26 | 0
215 | Faculty Lounge | 279 | 18 |  | 400 | 9 | 9
300 | Classroom | 140 | 9 | Yes | 875 | 19 | 19
301 | Classroom | 125 | 8 | Yes | 875 | 19 | 19
302 | Classroom | 200 | 13 | Yes | 875 | 19 | 19
303 | Classroom | 37 | 2 |  | 875 | 19 | 2
304 | Classroom | 86 | 5 | Yes | 960 | 21 | 21
305 | Classroom | 111 | 7 |  | 782 | 17 | 7
306 | Classroom | 200 | 13 |  | 782 | 17 | 13
307 | Classroom | 132 | 8 |  | 782 | 17 | 8
308 | Classroom | 33 | 2 |  | 782 | 17 | 2
310 | Classroom | 65 | 4 |  | 782 | 17 | 4
311 | Classroom | 632 | 42 |  | 782 | 17 | 17
312 | Classroom | 99 | 6 |  | 782 | 17 | 6
313 | Classroom | 76 | 5 |  | 782 | 17 | 5
314 | Classroom | 87 | 5 |  | 782 | 17 | 5
315 | Classroom | 112 | 7 |  | 782 | 17 | 7
404 | Classroom | 90 | 6 |  | 1156 | 26 | 6
405 | Classroom | 129 | 8 |  | 782 | 17 | 8
405A | Office | 0 | 0 |  | 112 | 2 | 0
406 | Classroom | 93 | 6 |  | 782 | 17 | 6
407 | Classroom | 147 | 9 |  | 782 | 17 | 9
408 | Classroom | 40 | 2 |  | 782 | 17 | 2
409A | Office | 23 | 1 |  | 140 | 3 | 1
410 | Classroom | 0 | 0 |  | 782 | 17 | 0
411 | Classroom | 86 | 5 |  | 782 | 17 | 5
412 | Classroom | 94 | 6 |  | 782 | 17 | 6
413 | Classroom | 76 | 5 |  | 782 | 17 | 5
414 | Classroom | 84 | 5 |  | 782 | 17 | 5
415 | Classroom | 100 | 6 |  | 782 | 17 | 6
- | Auditorium | 369 | 24 |  | 2162 | 49 | 24
- | Stage | 0 | 0 |  | 630 | 14 | 0
- | Building Engineer Office | 0 | 0 |  | 120 | 2 | 0
- | Cafeteria | 3225 | 215 |  | 4400 | 100 | 100
- | East Kitchen | 0 | 0 |  | 360 | 8 | 0
- | West Kitchen | 0 | 0 |  | 1040 | 23 | 0
- | Kitchen Office | 75 | 5 |  | 120 | 2 | 2
- | Gym | 4507 | 300 |  | 5005 | 113 | 113
- | Nurses Office | 154 | 10 |  | 143 | 3 | 3

## Mastbaum
Sheet Last Modified: |  | 2021-04-19
School: |  | Jules E. Mastbaum High School
Vendor: |  | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
SDP Building Name | Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Old Building | 101 | Classroom | 0 | 0 |  | 958.5 | 21 | 0
Old Building | 102 | Classroom | 0 | 0 |  | 966.966 | 21 | 0
Old Building | 103 | Classroom | 304 | 20 |  | 1130 | 25 | 20
Old Building | 104 | Classroom | 455 | 30 |  | 801 | 18 | 18
Old Building | 105 | Carpentry Shop |  | 0 | Yes | 2502 | 56 | 56
Old Building | 201 | Classroom | 0 | 0 |  | 585 | 13 | 0
Old Building | 202 | Classroom | 237 | 15 |  | 190 | 4 | 4
Old Building | 206 | Classroom | 569 | 37 |  | 1044.66 | 23 | 23
Old Building | 207 | Classroom | 0 | 0 |  | 906 | 20 | 0
Old Building | 209 | Classroom | 738 | 49 |  | 603 | 13 | 13
Old Building | 301 | Classroom | 680 | 45 |  | 582.742 | 13 | 13
Old Building | 302 | Classroom | 271 | 18 |  | 915.087 | 20 | 18
Old Building | 304 | Classroom | 256 | 17 |  | 942.933 | 21 | 17
Old Building | 306 | Classroom | 1285 | 85 |  | 1099.2 | 24 | 24
Old Building | 308 | Classroom | 292 | 19 |  | 971 | 22 | 19
Old Building | 310A | Classroom | 279 | 18 |  | 1014.53 | 23 | 18
Old Building | 311 | Classroom | 0 | 0 |  | 939.768 | 21 | 0
Old Building | 313 | Classroom | 572 | 38 |  | 939.134 | 21 | 21
Old Building | 315 | Classroom | 404 | 26 |  | 611.278 | 13 | 13
Old Building | 401 | Classroom | 194 | 12 |  | 561.645 | 12 | 12
Old Building | 402 | Classroom | 588 | 39 |  | 923.769 | 20 | 20
Old Building | 404 | Classroom | 337 | 22 |  | 936.079 | 21 | 21
Old Building | 406 | Classroom | 590 | 39 |  | 658.138 | 14 | 14
Old Building | 407 | Classroom | 0 | 0 |  | 749.51 | 17 | 0
Old Building | 408 | Classroom | 0 | 0 |  | 676.807 | 15 | 0
Old Building | 409 | Classroom | 0 | 0 |  | 659.406 | 14 | 0
Old Building | 410 | Classroom | 737 | 49 |  | 539.452 | 12 | 12
Old Building | 412 | Classroom | 956 | 63 |  | 934.951 | 21 | 21
Old Building | 413 | Classroom | 349 | 23 |  | 460.279 | 10 | 10
Old Building | 414 | Classroom | 446 | 29 |  | 462.262 | 10 | 10
Old Building | 415 | Classroom | 600 | 40 |  | 600.802 | 13 | 13
Old Building | 501 | Classroom | 0 | 0 |  | 583 | 13 | 0
Old Building | 505 | Classroom | 1040 | 69 |  | 700.54 | 15 | 15
Old Building | 506 | Classroom | 0 | 0 |  | 110 | 2 | 0
Old Building | 510 | Classroom | 595 | 39 |  | 652.168 | 14 | 14
Old Building | 511 | Classroom |  | 0 | Yes | 917 | 20
Old Building | 512 | Classroom | 0 | 0 |  | 734.362 | 16 | 0
Old Building | 513 | Classroom | 708 | 47 |  | 744.936 | 16 | 16
Old Building | 601 | Classroom | 352 | 23 |  | 562.177 | 12 | 12
Old Building | 602 | Classroom | 838 | 55 |  | 935.45 | 21 | 21
Old Building | 603 | Classroom | 1066 | 71 |  | 929.278 | 21 | 21
Old Building | 604 | Classroom | 604 | 40 |  | 883.594 | 20 | 20
Old Building | 605 | Classroom | 555 | 37 |  | 964.184 | 21 | 21
Old Building | 607 | Classroom | 733 | 48 |  | 929.6 | 21 | 21
Old Building | 609 | Classroom | 350 | 23 |  | 498.173 | 11 | 11
Old Building | 610 | Classroom | 1042 | 69 |  | 939.121 | 21 | 21
Old Building | 611 | Classroom | 944 | 62 |  | 942.573 | 21 | 21
Old Building | 612 | Classroom | 357 | 23 |  | 598.13 | 13 | 13
Old Building | 613 | Classroom | 312 | 20 |  | 696.196 | 15 | 15
Old Building | 614 | Classroom | 0 | 0 |  | 823.353 | 18 | 0
Old Building | 615 | Classroom | 411 | 27 |  | 1008.3 | 22 | 22
Old Building | 616 | Classroom | 1153 | 76 |  | 900.761 | 20 | 20
Old Building | 617 | Classroom | 0 | 0 |  | 899.388 | 20 | 0
Old Building | B1 A | Wood Shop | 475 | 31 |  | 2780 | 63 | 31
Old Building | B2 A | Classroom | 499 | 33 |  | 967 | 21 | 21
Old Building | - | Auditorium | 1222 | 81 |  | 4005 | 91 | 81
Old Building | - | 3rd Flr. Gym | 2212 | 147 |  | 3294.84 | 74 | 74
Old Building | - | 3rd Flr.Gym Locker Room | 3013 | 200 |  | 1903 | 43 | 43
Old Building | - | Stage | 532 | 35 |  | 993 | 22 | 22
Old Building | - | 1st Floor N Corridor | 301 | 20 |  | 160 | 3 | 3
Old Building | - | 1st Floor E Corridor | 536 | 35 |  | 160 | 3 | 3
Old Building | - | 1st Floor S Corridor | 427 | 28 |  | 2120 | 48 | 28
Old Building | - | 1st Floor W Corridor | 382 | 25 |  | 160 | 3 | 3
Old Building | - | 2nd Floor S Corridor | 438 | 29 |  | 2120 | 48 | 29
Old Building | - | 2nd Floor W Corridor | 465 | 31 |  | 160 | 3 | 3
Old Building | - | 2nd Floor N Corridor | 711 | 47 |  | 2120 | 48 | 47
Old Building | - | 2nd Floor E Corridor | 720 | 48 |  | 160 | 3 | 3
Old Building | - | 3rd Floor E Corridor | 504 | 33 |  |  | 0 | 0
Old Building | - | 3rd Floor N Corridor | 619 | 41 |  | 2120 | 48 | 41
Old Building | - | 3rd Floor W Corridor | 761 | 50 |  |  | 0 | 0
Old Building | - | 3rd Floor S Corridor | 569 | 37 |  | 2120 | 48 | 37
Old Building | - | 4th Floor N Corridor | 502 | 33 |  | 2120 | 48 | 33
Old Building | - | 4th Floor E Corridor | 633 | 42 |  |  | 0 | 0
Old Building | - | 4th Floor S Corridor | 0 | 0 |  | 2120 | 48 | 0
Old Building | - | 4th Floor W Corridor | 0 | 0 |  |  | 0 | 0
Old Building | - | 5th Floor N Corridor | 593 | 39 |  | 2120 | 48 | 39
Old Building | - | 5th Floor Library | 1677 | 111 |  | 2114.91 | 48 | 48
Old Building | - | 6th Floor S Corridor | 683 | 45 |  | 2120 | 48 | 45
Old Building | - | 6th Floor W Corridor | 918 | 61 |  |  | 0 | 0
Old Building | - | 6th Floor N Corridor | 530 | 35 |  | 2120 | 48 | 35
Old Building | - | 6th Floor E Corridor | 0 | 0 |  |  | 0 | 0
Old Building | - | Café | 1559 | 103 |  | 734.362 | 16 | 16
New Building | 120 | Auto Shop | 1016 | 67 |  | 2981 | 67 | 67
New Building | 124 | Auto Shop | 8220 | 548 |  | 4344 | 98 | 98
New Building | 220-221 | Electrical Shop | 0 | 0 |  | 1973.1 | 44 | 0
New Building | 224-223 | Shop | 2067 | 137 |  | 1149.75 | 26 | 26
New Building | 225-226 | Shop | 2858 | 190 |  | 3742.64 | 85 | 85
New Building | 324-323 | 324-323 | 877 | 58 |  | 2781 | 63 | 58
New Building | 326-325 | 326-325 | 1135 | 75 |  | 2395 | 54 | 54
New Building | 420 | 420 | 0 | 0 |  | 1250 | 28 | 0
New Building | 421 | 421 | 0 | 0 |  | 1873 | 42 | 0
New Building | 423 | 423 | 487 | 32 |  | 1693.03 | 38 | 32
New Building | 426 | 426 Plumbing Shop | 1678 | 111 |  | 1265.49 | 28 | 28
New Building | 427-426 | 427-426 | 0 | 0 |  | 1583 | 35 | 0
New Building | - | Gym | 958 | 63 |  | 7555.89 | 171 | 63
New Building | - | Gym Locker Rm. | 0 | 0 |  | 5738 | 130 | 0
New Building | 321 | Nursing | 614 | 40 |  | 1898 | 43 | 40
New Building | - | Weld Shop | 2329 | 155 |  | 624.854 | 14 | 14

## Masterman
Sheet Last Modified: | 2021-04-07
School: | Julia R. Masterman Laboratory and Demonstration High School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
8 | Music Room |  | 0 |  | 630 | 14 | 0
9 | Classroom | 0 | 0 |  | 874 | 19 | 0
11 | Classroom | 0 | 0 |  | 825 | 18 | 0 | AHU Inoperable
11A | Classroom | 0 | 0 |  | 368 | 8 | 0 | AHU Inoperable
12 | Classroom | 0 | 0 |  | 832 | 18 | 0 | AHU Inoperable
14 | Art Room |  | 0 |  | 1023 | 23 | 0 | AHU Inoperable
15 | Classroom | 0 | 0 |  | 1148 | 26 | 0
101 | Classroom | 0 | 0 | Yes | 704 | 16 | 16 | AHU Inoperable
102 | Music Room | 0 | 0 |  | 836 | 19 | 0 | AHU Inoperable
103 | Classroom | 0 | 0 |  | 638 | 14 | 0 | AHU Inoperable
104 | Classroom | 0 | 0 |  | 660 | 15 | 0 | AHU Inoperable
201 | Classroom | 0 | 0 | Yes | 704 | 16 | 16 | AHU Inoperable
202 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable
203 | Classroom | 0 | 0 | Yes | 644 | 14 | 14 | AHU Inoperable
204 | Library | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable
205 | Fitness Storage | 0 | 0 | Yes | 690 | 15 | 15 | AHU Inoperable
206 | Fitness Storage | 0 | 0 |  | 704 | 16 | 0 | AHU Inoperable
207 | Classroom | 0 | 0 | Yes | 660 | 15 | 15 | AHU Inoperable
208 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable
209 | Classroom | 0 | 0 |  | 187 | 4 | 0 | AHU Inoperable
210 | Classroom | 0 | 0 |  | 187 | 4 | 0 | AHU Inoperable
211 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | AHU Inoperable
212 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable
213 | Classroom | 0 | 0 |  | 374 | 8 | 0 | AHU Inoperable
214 | Classroom | 0 | 0 |  | 374 | 8 | 0 | AHU Inoperable
218 | Main Office |  | 0 | Yes | 210 | 4 | 4 | AHU Inoperable
301 | Classroom | 0 | 0 | Yes | 682 | 15 | 15
302 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable
303 | Classroom | 0 | 0 |  | 660 | 15 | 0 | AHU Inoperable
304 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable
305 | Classroom | 0 | 0 | Yes | 638 | 14 | 14 | AHU Inoperable
306 | Classroom | 0 | 0 |  | 144 | 3 | 0 | AHU Inoperable
307 | Classroom |  | 0 |  | 726 | 16 | 0 | AHU Inoperable
307A | Office |  | 0 |  | 264 | 6 | 0
308 | Classroom | 0 | 0 |  | 1210 | 27 | 0
309 | Office | 0 | 0 |  | 300 | 6 | 0 | AHU Inoperable
310 | Classroom | 0 | 0 |  | 96 | 2 | 0 | AHU Inoperable
311 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable
312 | Classroom | 0 | 0 |  | 1078 | 24 | 0 | AHU Inoperable
313 | Room |  | 0 |  | 374 | 8 | 0 | AHU Inoperable
402 | Classroom | 0 | 0 |  | 880 | 20 | 0
404 | Classroom | 0 | 0 |  | 704 | 16 | 0 | AHU Inoperable
406 | Classroom | 0 | 0 |  | 504 | 11 | 0 | AHU Inoperable
408 | Classroom | 0 | 0 |  | 672 | 15 | 0 | AHU Inoperable
410 | Classroom | 0 | 0 |  | 1008 | 22 | 0 | AHU Inoperable
412 | Office | 0 | 0 |  | 205 | 4 | 0 | AHU Inoperable
502 | Classroom | 0 | 0 |  | 880 | 20 | 0 | AHU Inoperable
506 | Classroom | 0 | 0 |  | 690 | 15 | 0 | AHU Inoperable
- | Game Room |  | 0 |  | 790 | 17 | 0 | AHU Inoperable
- | Auditorium | 0 | 0 |  | 5850 | 132 | 0
- | Cafeteria | 0 | 0 |  | 3600 | 81 | 0 | AHU Inoperable
- | Counselor's Office |  | 0 |  | 110 | 2 | 0 | AHU Inoperable
- | Counselor's Office |  | 0 |  | 110 | 2 | 0
- | Faculty Cafeteria | 0 | 0 |  | 726 | 16 | 0
- | Gym | 0 | 0 | Yes | 6208 | 141 | 141 | AHU Inoperable
- | Boy's Locker Room |  | 0 |  | 580 | 13 | 0
- | Girl's Locker Room |  | 0 |  | 209 | 4 | 0
- | Health room |  | 0 |  | 100 | 2 | 0
- | Kitchen | 0 | 0 |  | 828 | 18 | 0 | AHU Inoperable
- | LIbrary Room |  | 0 |  | 620 | 14 | 0
- | Library Office |  | 0 |  | 231 | 5 | 0
- | Library A |  | 0 |  | 506 | 11 | 0
- | Library B |  | 0 |  | 651 | 14 | 0
- | Library C |  | 0 |  | 230 | 5 | 0
- | Nurse Office | 0 | 0 | Yes | 170 | 3 | 3 | AHU Inoperable
| Nurse Examining |  | 0 | Yes | 100 | 2 | 2
| Nurse Roster Room |  | 0 | Yes | 288 | 6 | 6
- | Robotics | 0 | 0 |  | 420 | 9 | 0 | AHU Inoperable
- | Science Office |  | 0 |  | 187 | 4 | 0
- | Principal 's Office |  | 0 |  | 210 | 4 | 0
- | Assant Principal's Office |  | 0 |  | 140 | 3 | 0
- | Operations Office |  | 0 |  | 56 | 1 | 0
- | Office Waiting Area |  | 0 |  | 275 | 6 | 0
- | Roster Office |  | 0 |  | 136 | 3 | 0

## Mayfair
Sheet Last Modified: | 2021-04-23
School: | Mayfair Elementary School
Vendor: | Devine Brothers | Devine Part 2 | Devine Part 3
Vendor: | Capital | Capital Update | Capital Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 207 | 13 |  | 696 | 15 | 13 | Unit Ventilator
101 | Classroom | 201 | 13 |  | 696 | 15 | 13 | Unit Ventilator
102 | Classroom | 197 | 13 |  | 598 | 13 | 13 | Unit Ventilator
103 | Classroom | 189 | 12 |  | 720 | 16 | 12 | Unit Ventilator
104 | Classroom | 355 | 23 |  | 690 | 15 | 15 | Unit Ventilator
105 | Classroom | 231 | 15 |  | 624 | 14 | 14 | Unit Ventilator
106 | Classroom | 237 | 15 |  | 720 | 16 | 15 | Unit Ventilator
107 | Classroom | 458 | 30 |  | 720 | 16 | 16 | Unit Ventilator
108 | Classroom | 115 | 7 |  | 600 | 13 | 7 | Unit Ventilator
109 | Classroom | 186 | 12 |  | 744 | 16 | 12 | Unit Ventilator
110 | Classroom | 418 | 27 |  | 696 | 15 | 15 | Unit Ventilator
111 | Classroom | 202 | 13 |  | 624 | 14 | 13 | Unit Ventilator
112 | Classroom | 461 | 30 |  | 1032 | 23 | 23 | Unit Ventilator
113 | Classroom | 211 | 14 |  | 720 | 16 | 14 | Unit Ventilator
114 | Classroom | 377 | 25 |  | 644 | 14 | 14 | Unit Ventilator
115 | Classroom | 271 | 18 |  | 620 | 14 | 14 | Unit Ventilator
116 | Classroom | 395 | 26 |  | 989 | 22 | 22 | Unit Ventilator
118 | Classroom | 384 | 25 |  | 690 | 15 | 15 | Unit Ventilator
119 | Classroom | 320 | 21 |  | 624 | 14 | 14 | Unit Ventilator
120 | Classroom | 311 | 20 |  | 1610 | 36 | 20 | Unit Ventilator
200 | Classroom |  | 0 | Yes | 205 | 4 | 4
201 | Classroom | 286 | 19 |  | 696 | 15 | 15 | Unit Ventilator
202 | Classroom | 560 | 37 |  | 696 | 15 | 15 | Unit Ventilator
203 | Classroom | 381 | 25 |  | 725 | 16 | 16 | Unit Ventilator
204 | Classroom | 323 | 21 |  | 884 | 20 | 20 | Unit Ventilator
205 | Classroom | 271 | 18 |  | 780 | 17 | 17 | Unit Ventilator
206 | Classroom | 316 | 21 |  | 806 | 18 | 18 | Unit Ventilator
207 | Classroom | 295 | 19 |  | 806 | 18 | 18 | Unit Ventilator
207A | Asst. Principal Office | 0 | 0 | Yes | 293 | 6 | 6 | Unit Ventilator
208 | Classroom | 305 | 20 |  | 528 | 12 | 12 | Unit Ventilator
209 | Classroom | 560 | 37 |  | 884 | 20 | 20 | Unit Ventilator
210 | Classroom | 290 | 19 |  | 1118 | 25 | 19 | Unit Ventilator
211 | Classroom | 307 | 20 |  | 648 | 14 | 14 | Unit Ventilator
212 | Classroom | 483 | 32 |  | 665 | 15 | 15 | Unit Ventilator
213 | Classroom | 590 | 39 |  | 806 | 18 | 18 | Unit Ventilator
214 | Classroom | 300 | 20 |  | 806 | 18 | 18 | Unit Ventilator
215 | Classroom | 294 | 19 |  | 728 | 16 | 16 | Unit Ventilator
216 | Classroom | 317 | 21 |  | 648 | 14 | 14 | Unit Ventilator
217 | Classroom | 350 | 23 |  | 782 | 17 | 17 | Unit Ventilator
218 | Classroom | 271 | 18 |  | 621 | 14 | 14 | Unit Ventilator
219 | Classroom | 137 | 9 |  | 648 | 14 | 9 | Unit Ventilator
220 | Classroom | 235 | 15 |  | 648 | 14 | 14 | Unit Ventilator
221 | Classroom | 325 | 21 |  | 744 | 16 | 16 | Unit Ventilator
222 | Classroom | 180 | 12 |  | 648 | 14 | 12 | Unit Ventilator
301 | Classroom | 325 | 21 |  | 720 | 16 | 16 | ERU
302 | Classroom | 304 | 20 |  | 720 | 16 | 16 | ERU
303 | Classroom | 270 | 18 |  | 720 | 16 | 16 | ERU
304 | Classroom | 435 | 29 |  | 720 | 16 | 16 | ERU
305 | Classroom | 453 | 30 |  | 720 | 16 | 16 | ERU
306 | Classroom | 480 | 32 |  | 720 | 16 | 16 | ERU
401 | Classroom | 320 | 21 |  | 720 | 16 | 16 | ERU
402 | Classroom | 282 | 18 |  | 720 | 16 | 16 | ERU
403 | Classroom | 551 | 36 |  | 720 | 16 | 16 | ERU
404 | Classroom | 412 | 27 |  | 720 | 16 | 16 | ERU
405 | Classroom | 412 | 27 |  | 720 | 16 | 16 | ERU
406 | Classroom | 406 | 27 |  | 720 | 16 | 16 | ERU
510 | Classroom | 282 | 18 |  | 754 | 17 | 17 | ERU
511 | Classroom | 430 | 28 |  | 754 | 17 | 17 | ERU
512 | Classroom | 447 | 29 |  | 754 | 17 | 17 | ERU
513 | Classroom | 543 | 36 |  | 754 | 17 | 17 | ERU
515 | Classroom | 652 | 43 |  | 754 | 17 | 17 | ERU
516 | Classroom | 519 | 34 |  | 754 | 17 | 17 | ERU
517 | Classroom | 605 | 40 |  | 754 | 17 | 17 | ERU
520 | Classroom | 500 | 33 |  | 754 | 17 | 17 | ERU
521 | Classroom | 548 | 36 |  | 754 | 17 | 17 | ERU
522 | Classroom | 530 | 35 |  | 754 | 17 | 17 | ERU
523 | Classroom | 509 | 33 |  | 754 | 17 | 17 | ERU
525 | Classroom | 676 | 45 |  | 754 | 17 | 17 | ERU
526 | Classroom | 646 | 43 |  | 754 | 17 | 17 | ERU
527 | Classroom | 568 | 37 |  | 774.3 | 17 | 17 | ERU
- | Main Office |  | 0 | Yes | 493 | 11 | 11
- | Counselor Office |  | 0 | Yes | 126 | 2 | 2
- | Counselor Office |  | 0 | Yes | 231 | 5 | 5
- | Principal Office |  | 0 | Yes | 196 | 4 | 4
- | Special Education |  | 0 | Yes | 275 | 6 | 6
- | Conference Room |  | 0 | Yes | 135 | 3 | 3
- | Faculty Room |  | 0 | Yes | 171 | 3 | 3
- | Nurse Office |  | 0 | Yes | 372 | 8 | 8
- | Asst. Principal 1 |  | 0 | Yes | 86 | 1 | 1
- | Asst. Principal 2 |  | 0 | Yes | 97 | 2 | 2
- | Auditorium |  | 0 |  | 4920 | 111 | 0 | AHU
| Auditorium Room 1 |  | 0 | Yes | 263 | 5 | 5
| Auditorium Room 2 |  | 0 | Yes | 254 | 5 | 5
Music 1 | Room |  | 0 | Yes | 354 | 8 | 8
Music 2 | Room |  | 0 | Yes | 711 | 16 | 16
- | Cafeteria | 998 | 66 |  | 3257.25 | 74 | 66 | RTU
- | Gym |  | 0 | Yes | 3982 | 90 | 90 | AHU
School Police | Office |  | 0 | Yes | 54 | 1 | 1
- | Nurse Office | 292 | 19 |  | 372 | 8 | 8 | Unit Ventilator
1 | Mobile Classroom | 326 | 21 |  | 594 | 13 | 13 | AHU
2 | Mobile Classroom | 328 | 21 |  | 594 | 13 | 13 | AHU
3 | Mobile Classroom | 644 | 42 |  | 594 | 13 | 13 | AHU
4 | Mobile Classroom | 451 | 30 |  | 594 | 13 | 13 | AHU
5 | Mobile Classroom | 580 | 38 |  | 594 | 13 | 13 | AHU
6 | Mobile Classroom | 438 | 29 |  | 594 | 13 | 13 | AHU
7 | Mobile Classroom | 414 | 27 |  | 594 | 13 | 13 | AHU
8 | Mobile Classroom | 574 | 38 |  | 594 | 13 | 13 | AHU

## McCall
Sheet Last Modified: | 2021-04-06
School: | General George A. McCall Elementary School
Vendor: | Devine | 2nd Retest | 3rd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
0 | Classroom | 0 | 0 | Yes | 572 | 13 | 13 | N/A
1 | Classroom | 370 | 24 |  | 924 | 21 | 21 | Unit Ventilator
2 | Music Room | 453 | 30 |  | 836 | 19 | 19 | Unit Ventilator
4 | Classroom | 1630.65 | 108 |  | 660 | 15 | 15 | AHU
5 | Classroom | 477.639 | 31 |  | 1012 | 23 | 23 | AHU
6 | Classroom | 534.798 | 35 |  | 1100 | 25 | 25 | AHU
101 | Office | 0 | 0 | Yes | 276 | 6 | 6 | N/A
101A | Office | 182 | 12 | Yes | 440 | 10 | 10 | Unit Ventilator
102 | Classroom | 332 | 22 |  | 836 | 19 | 19 | Unit Ventilator
103 | Classroom | 283 | 18 | Yes | 880 | 20 | 20 | Unit Ventilator
105 | Classroom | 278 | 18 | Yes | 880 | 20 | 20 | Unit Ventilator
106 | Classroom | 340 | 22 |  | 924 | 21 | 21 | Unit Ventilator
107 | Classroom | 292 | 19 | Yes | 968 | 22 | 22 | Unit Ventilator
108 | Classroom | 303 | 20 |  | 836 | 19 | 19 | Unit Ventilator
109 | Classroom | 375 | 25 |  | 880 | 20 | 20 | Unit Ventilator
110 | Classroom | 0 | 0 | Yes | 220 | 5 | 5 | N/A
110A | Office | 336 | 22 |  | 440 | 10 | 10 | Unit Ventilator
209 | Classroom | 0 | 0 | Yes | 440 | 10 | 10 | Unit Ventilator
210 | Classroom | 273 | 18 | Yes | 880 | 20 | 20 | Unit Ventilator
211 | Classroom | 293 | 19 | Yes | 924 | 21 | 21 | Unit Ventilator
212 | Classroom | 294 | 19 |  | 880 | 20 | 19 | Unit Ventilator
213 | Classroom | 320 | 21 |  | 924 | 21 | 21 | Unit Ventilator
214 | Classroom | 376 | 25 |  | 880 | 20 | 20 | Unit Ventilator
216A | Office | 0 | 0 | Yes | 480 | 10 | 10 | N/A
217 | Classroom | 297 | 19 |  | 792 | 18 | 18 | Unit Ventilator
218 | Classroom | 309 | 20 |  | 924 | 21 | 20 | Unit Ventilator
219 | Classroom | 313 | 20 |  | 792 | 18 | 18 | Unit Ventilator
318 | Classroom | 172 | 11 | Yes | 748 | 17 | 17 | Unit Ventilator
319 | Classroom | 368 | 24 |  | 924 | 21 | 21 | Unit Ventilator
320 | Classroom | 401 | 26 |  | 836 | 19 | 19 | Unit Ventilator
321 | Classroom | 329 | 21 |  | 880 | 20 | 20 | Unit Ventilator
322 | Classroom | 292 | 19 |  | 924 | 21 | 19 | Unit Ventilator
323 | Classroom | 351 | 23 |  | 924 | 21 | 21 | Unit Ventilator
324 | Classroom | 284 | 18 |  | 880 | 20 | 18 | Unit Ventilator
325 | Classroom | 396 | 26 |  | 924 | 21 | 21 | Unit Ventilator
326 | Classroom | 309 | 20 |  | 836 | 19 | 19 | Unit Ventilator
327 | Classroom | 345 | 23 |  | 792 | 18 | 18 | Unit Ventilator
327A | Classroom | 261 | 17 |  | 484 | 11 | 11 | Unit Ventilator
- | Auditorium | 1451 | 96 |  | 4224 | 96 | 96 | AHU
- | Gym/Cafeteria | 1279 | 85 |  | 3740 | 85 | 85 | AHU
- | Main Office | 311 | 20 |  | 792 | 18 | 18 | Unit Ventilator
- | Library | 492 | 32 |  | 1584 | 36 | 32 | Unit Ventilator
- | Engineer Office | 0 | 0 |  | 432 | 9 | 0 | N/A
- | Gym Office | 0 | 0 |  | 110 | 2 | 0 | AHU
- | Kitchen | 9 | 0 | Yes | 384 | 8 | 8 | AHU
- | Principals Office | 0 | 0 | Yes | 493 | 11 | 11 | AHU

## McCloskey
Sheet Last Modified: | 2021-04-13
School: | John F. McCloskey Elementary School
Vendor: | Chadwick | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
2 | IMC |  | 0 | Yes | 1044 | 23 | 23 | Unit Ventilator
7 | Recovery. room |  | 0 | Yes | 180 | 4 | 4 | Convector
101 | Classroom | 229 | 15 |  | 936 | 21 | 15 | Unit Ventilator
102 | Classroom | 192 | 12 |  | 936 | 21 | 12 | Unit Ventilator
103 | Classroom | 394 | 26 |  | 936 | 21 | 21 | Unit Ventilator
104 | Classroom | 155 | 10 | Yes | 1056 | 24 | 24 | Unit Ventilator
105 | Classroom | 342 | 22 |  | 897 | 20 | 20 | Unit Ventilator
106 | Classroom | 203 | 13 |  | 936 | 21 | 13 | Unit Ventilator
107 | Classroom | 206 | 13 |  | 936 | 21 | 13 | Unit Ventilator
108 | Classroom | 390 | 26 |  | 936 | 21 | 21 | Unit Ventilator
109 | Classroom | 282 | 18 |  | 736 | 16 | 16 | Unit Ventilator
111 | Classroom | 356 | 23 |  | 736 | 16 | 16 | Unit Ventilator
113 | Classroom | 320 | 21 |  | 736 | 16 | 16 | Unit Ventilator
114 | Classroom | 319 | 21 |  | 736 | 16 | 16 | Unit Ventilator
201 | Classroom |  | 0 |  | 916 | 20 | 0 | Unit Ventilator
202 | Classroom | 200 | 13 |  | 936 | 21 | 13 | Unit Ventilator
203 | Classroom | 194 | 12 |  | 936 | 21 | 12 | Unit Ventilator
204 | Classroom | 378 | 25 |  | 936 | 21 | 21 | Unit Ventilator
205 | Classroom | 342 | 22 |  | 936 | 21 | 21 | Unit Ventilator
206 | Classroom | 487 | 32 |  | 936 | 21 | 21 | Unit Ventilator
208 | Classroom | 346 | 23 |  | 936 | 21 | 21 | Unit Ventilator
209 | Classroom | 514 | 34 |  | 936 | 21 | 21 | Unit Ventilator
210 | Classroom | 247 | 16 |  | 936 | 21 | 16 | Unit Ventilator
211 | Classroom | 374 | 24 |  | 936 | 21 | 21 | Unit Ventilator
- | Auditorium |  | 0 |  | 2700 | 61 | 0 | AHU
- | Computer Room | 40 | 2 |  | 1080 | 24 | 2 | Unit Ventilator
- | Gym |  | 0 | Yes | 3744 | 85 | 85 | AHU
- | Main Office |  | 0 | Yes | 338 | 7 | 7 | Convector
- | Prin. Office |  | 0 | Yes | 312 | 7 | 7 | Convector
- | Nurse. Office |  | 0 | Yes | 225 | 5 | 5 | Convector

## McClure
Sheet Last Modified: | 2021-03-18
School: | Alexander K. McClure Elementary School
Vendor: | Devine Brothers | Retest | 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
0 | Building Engineer | 0 | 0 |  |  | 0 | 0 | N/A
1 | Gym | 650 | 43 |  | 2486 | 56 | 43 | House Fan
6 | Art | 302 | 20 |  | 894 | 20 | 20 | House Fan
7 | Classroom | 559 | 37 |  | 839 | 19 | 19 | House Fan
11 | Classroom | 523 | 34 |  | 821 | 18 | 18 | House Fan
101 | Classroom | 603 | 40 |  | 887 | 20 | 20 | House Fan
106 | Classroom | 419 | 27 |  | 927 | 21 | 21 | House Fan
106A | Asst. Principal | 0 | 0 | Yes | 104 | 2 | 2 | House Fan
107 | Classroom | 505 | 33 |  | 753 | 17 | 17 | House Fan
108 | Classroom | 329 | 21 |  | 849 | 19 | 19 | House Fan
109 | Classroom | 454 | 30 |  | 791 | 17 | 17 | House Fan
110 | Classroom | 603 | 40 |  | 725 | 16 | 16 | House Fan
111 | Classroom | 537 | 35 |  | 699 | 15 | 15 | House Fan
201 | Classroom | 585 | 39 |  | 847 | 19 | 19 | House Fan
202 | Classroom | 597 | 39 |  | 883 | 20 | 20 | House Fan
203 | Classroom | 423 | 28 |  | 903 | 20 | 20 | House Fan
204 | Classroom | 461 | 30 |  | 887 | 20 | 20 | House Fan
205 | Classroom | 482 | 32 |  | 945 | 21 | 21 | House Fan
206 | Library | 431 | 28 |  | 890 | 20 | 20 | House Fan
206A | Nurse Office | 0 | 0 |  | 194 | 4 | 0 | N/A
206B | Nurse Exam | 0 | 0 | Yes | 362 | 8 | 8 | House Fan
207 | Classroom | 442 | 29 |  | 869 | 19 | 19 | House Fan
208 | Classroom | 309 | 20 |  | 812 | 18 | 18 | House Fan
209 | Classroom | 412 | 27 |  | 823 | 18 | 18 | House Fan
210 | Classroom | 602 | 40 |  | 714 | 16 | 16 | House Fan
211 | Classroom | 595 | 39 |  | 740 | 16 | 16 | House Fan
301 | Classroom | 559 | 37 |  | 882 | 20 | 20 | House Fan
302 | Classroom | 501 | 33 |  | 902 | 20 | 20 | House Fan
303 | Classroom | 377 | 25 |  | 900 | 20 | 20 | House Fan
304 | Classroom | 483 | 32 |  | 875 | 19 | 19 | House Fan
305 | Classroom | 469 | 31 |  | 910 | 20 | 20 | House Fan
306 | Classroom | 402 | 26 |  | 894 | 20 | 20 | House Fan
306A | Office | 0 | 0 | Yes | 185 | 4 | 4 | House Fan
307 | Classroom | 470 | 31 |  | 932 | 21 | 21 | House Fan
308 | Classroom | 301 | 20 |  | 815 | 18 | 18 | House Fan
309 | Classroom | 313 | 20 |  | 851 | 19 | 19 | House Fan
310 | Classroom | 396 | 26 |  | 726 | 16 | 16 | House Fan
311 | Classroom | 406 | 27 |  | 732 | 16 | 16 | House Fan
312 | Classroom | 0 | 0 | Yes | 435 | 9 | 9 | N/A
- | 4th Floor Office N | 0 | 0 |  |  | 0 | 0 | N/A
- | 4th Floor Office S | 0 | 0 |  |  | 0 | 0 | N/A
- | Cafeteria | 1876 | 125 |  | 2974 | 67 | 67 | House Fan
- | Main Office | 0 | 0 | Yes | 262 | 5 | 5 | N/A
- | Principal Office | 0 | 0 | Yes | 194 | 4 | 4 | N/A
- | Portable Classroom | 289 | 19 |  | 1290 | 29 | 19 | Unit Ventilators

## McDaniel
Sheet Last Modified: | 2021-04-29
School: | Delaplaine McDaniel Elementary-Middle School
McDaniel Annex (St. Edmunds)
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
McDaniel Main
102 | Classroom | 865 | 57 |  | 660 | 15 | 15 | Unit Ventilator
103 | Classroom | 250 | 16 |  | 660 | 15 | 15 | Unit Ventilator
104 | Classroom | 340 | 22 |  | 836 | 19 | 19 | Unit Ventilator
105 | Classroom | 275 | 18 |  | 660 | 15 | 15 | Unit Ventilator
107 | Classroom | 1025 | 68 |  | 660 | 15 | 15 | Unit Ventilator
108 | Classroom |  | 0 | Yes | 464 | 10 | 10
109 | Classroom | 550 | 36 |  | 1260 | 28 | 28 | Unit Ventilator
200 | Classroom | 430 | 28 |  | 1260 | 28 | 28 | Unit Ventilator
201 | Classroom | 0 | 0 |  | 396 | 9 | 0 | Unit Ventilator
203 | Classroom | 635 | 42 |  | 630 | 14 | 14 | Unit Ventilator
204 | Computer Lab | 949 | 63 |  | 924 | 21 | 21 | Unit Ventilator
205 | Classroom | 635 | 42 |  | 660 | 15 | 15 | Unit Ventilator
206 | Classroom | 475 | 31 |  | 858 | 19 | 19 | Unit Ventilator
207 | Classroom | 0 | 0 |  | 783 | 17 | 0 | Unit Ventilator
209 | Classroom | 0 | 0 |  | 777 | 17 | 0 | Unit Ventilator
300 | Classroom | 0 | 0 | Yes | 819 | 18 | 18 | Unit Ventilator
301 | Classroom | 0 | 0 |  | 691 | 15 | 0 | Unit Ventilator
303 | Classroom | 428 | 28 |  | 945 | 21 | 21 | Unit Ventilator
304 | Classroom | 134 | 8 |  | 704 | 16 | 8 | Unit Ventilator
305 | Classroom | 374 | 24 |  | 638 | 14 | 14 | Unit Ventilator
306 | Classroom | 185 | 12 |  | 638 | 14 | 12 | Unit Ventilator
307 | Classroom | 570 | 38 |  | 638 | 14 | 14 | Unit Ventilator
308 | Classroom | 470 | 31 |  | 638 | 14 | 14 | Unit Ventilator
309 | Classroom | 400 | 26 |  | 638 | 14 | 14 | Unit Ventilator
310 | Classroom | 494 | 32 |  | 880 | 20 | 20 | Unit Ventilator
311 | Classroom | 430 | 28 |  | 638 | 14 | 14 | Unit Ventilator
313 | Classroom | 1099 | 73 |  | 814 | 18 | 18 | Unit Ventilator
- | Gym | 0 | 0 | Yes | 3300 | 75 | 75 | AHU
- | Gym Office |  | 0 | Yes | 77 | 1 | 1
- | Nurse Office |  | 0 | Yes | 280 | 6 | 6
- | Media Center | 700 | 46 |  | 1078 | 24 | 24 | Unit Ventilator
- | Kitchen |  | 0 | Yes | 294 | 6 | 6
- | School Police |  | 0 | Yes | 90 | 2 | 2
- | Counselor Office |  | 0 | Yes | 117 | 2 | 2
- | Principals Office |  | 0 | Yes | 196 | 4 | 4
- | Vice Principal |  | 0 | Yes | 187 | 4 | 4
- | Office | 0 | 0 | Yes | 392 | 8 | 8 | AHU
McDaniel Annex (St. Edmunds)
K-1 | Classroom | 269 | 17 |  | 516 | 11 | 11 | Unit Ventilator
K-2 | Classroom | 449 | 29 |  | 616 | 14 | 14 | Unit Ventilator
K-3 | Classroom | 407 | 27 |  | 616 | 14 | 14 | Unit Ventilator
K-4 | Classroom | 348 | 23 |  | 516 | 11 | 11 | Unit Ventilator
206 | Classroom | 350 | 23 |  | 616 | 14 | 14 | Unit Ventilator
207 | Classroom | 530 | 35 |  | 792 | 18 | 18 | Unit Ventilator
208 | Classroom | 632 | 42 |  | 660 | 15 | 15 | Unit Ventilator
209 | Classroom | 495 | 33 |  | 660 | 15 | 15 | Unit Ventilator
210 | Classroom | 375 | 25 |  | 440 | 10 | 10 | Unit Ventilator
213 | Classroom | 447 | 29 |  | 440 | 10 | 10 | Unit Ventilator
215 | Classroom | 640 | 42 |  | 792 | 18 | 18 | Unit Ventilator
306 | Classroom | 525 | 35 |  | 616 | 14 | 14 | Unit Ventilator
307 | Classroom | 653 | 43 |  | 792 | 18 | 18 | Unit Ventilator
308 | Classroom | 425 | 28 |  | 660 | 15 | 15 | Unit Ventilator
309 | Classroom | 630 | 42 |  | 660 | 15 | 15 | Unit Ventilator
310 | Classroom | 471 | 31 |  | 660 | 15 | 15 | Unit Ventilator
312 | Classroom | 481 | 32 |  | 704 | 16 | 16 | Unit Ventilator
313 | Classroom | 611 | 40 |  | 704 | 16 | 16 | Unit Ventilator
- | Cafeteria / Gym | 14007 | 933 |  | 3960 | 90 | 90 | AHU
- | Classroom | 15010 | 1000 |  | 1431 | 32 | 32 | AHU

## McKinley
Sheet Last Modified: | 2021-04-06
School: | William McKinley Elementary School
Vendor: | Devine Brothers | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | A1/11 | 529 | 35 |  | 858 | 19 | 19 | Unit Ventilator
- | A2/12 | 627 | 41 |  | 832 | 18 | 18 | Unit Ventilator
- | A3/13 | 298 | 19 |  | 858 | 19 | 19 | Unit Ventilator
- | A4/14 | 512 | 34 |  | 858 | 19 | 19 | Unit Ventilator
- | Autistic Support 8 | 231 | 15 |  | 726 | 16 | 15 | Unit Ventilator
- | B1/21 | 711 | 47 |  | 792 | 18 | 18 | Unit Ventilator
- | B2/22 | 630 | 42 |  | 754 | 17 | 17 | Unit Ventilator
- | B3/23 | 660 | 44 |  | 754 | 17 | 17 | Unit Ventilator
- | B4/24 | 538 | 35 |  | 744 | 16 | 16 | Unit Ventilator
- | C1/31 | 604 | 40 |  | 726 | 16 | 16 | Unit Ventilator
- | C2/32 | 271 | 18 |  | 675 | 15 | 15 | Unit Ventilator
- | C3/33 | 605 | 40 |  | 700 | 15 | 15 | Unit Ventilator
- | C4/34 | 669 | 44 |  | 720 | 16 | 16 | Unit Ventilator
- | CCTC 11 | 1062 | 70 |  | 1215 | 27 | 27 | Unit Ventilator
- | D1 | 426 | 28 |  | 858 | 19 | 19 | Unit Ventilator
- | D2 | 553 | 36 |  | 780 | 17 | 17 | Unit Ventilator
- | D3 | 290 | 19 |  | 780 | 17 | 17 | Unit Ventilator
- | D4 | 310 | 20 |  | 780 | 17 | 17 | Unit Ventilator
- | Gymnasium | 1525 | 101 |  | 2860 | 65 | 65 | AHU
- | Kindergarten 1 | 355 | 23 |  | 924 | 21 | 21 | Unit Ventilator
- | Kindergarten 2 | 290 | 19 | Yes | 924 | 21 | 21 | Unit Ventilator
- | Kindergarten 3 | 282 | 18 | Yes | 924 | 21 | 21 | Unit Ventilator
- | Pre K 4 | 739 | 49 |  | 924 | 21 | 21 | Unit Ventilator
- | Room 5 | 611 | 40 |  | 726 | 16 | 16 | Unit Ventilator
-- | Room 6 | 467 | 31 |  | 726 | 16 | 16 | Unit Ventilator
- | Room 9 / Visual Arts | 748 | 49 |  | 726 | 16 | 16 | AHU
- | Room 12 | 587 | 39 |  | 809 | 18 | 18 | AHU
A-0 | Small Classroom | 37 | 2 |  | 150 | 3 | 2 | AHU
7 | Teachers Lounge | 59 | 3 | Yes | 351 | 7 | 7 | AHU
- | Nurse Exam Large | 69 | 4 | Yes | 252 | 5 | 5 | AHU
- | Nurse Office | 38 | 2 |  | 119 | 2 | 2 | AHU
- | Nurse Exam | 59 | 3 |  | 153 | 3 | 3 | AHU
- | Storage Large | 61 | 4 |  | 216 | 4 | 4 | AHU
- | Storage | 24 | 1 |  |  | 0 | 0 | AHU
- | Auditorium | 1667 | 111 |  | 2453 | 55 | 55 | AHU
- | Music Room | 319 | 21 |  | 727 | 16 | 16 | AHU
- | Library | 1047 | 69 |  | 3888 | 88 | 69 | AHU
- | Cafeteria | 894 | 59 |  | 2331 | 52 | 52 | AHU
D-0 | Small Classroom | 36 | 2 |  | 150 | 3 | 2 | AHU
C-0 | Small Classroom | 21 | 1 |  | 150 | 3 | 1 | AHU
B-0 | Small Classroom | 53 | 3 |  | 150 | 3 | 3 | AHU
10 | Small Classroom | 26 | 1 | Yes | 364 | 8 | 8 | AHU
- | Main Office | 50 | 3 | Yes | 817 | 18 | 18 | AHU
- | Admin Office 1 | 52 | 3 |  | 128 | 2 | 2 | AHU
- | Admin Office 2 | 73 | 4 |  | 128 | 2 | 2 | AHU
- | Admin Office 3 | 43 | 2 |  | 128 | 2 | 2 | AHU
- | Admin Office 5 | 50 | 3 |  | 160 | 3 | 3 | AHU
- | Admin Office 6 | 49 | 3 |  | 285 | 6 | 3 | AHU
- | Admin Office 7 | 22 | 1 | Yes | 120 | 2 | 2 | AHU
- | Equip Storage | 0 | 0 |  | 120 | 2 | 0 | AHU
- | Corridor | 35 | 2 |  | 440 | 10 | 2 | AHU
- | Principals Office | 35 | 2 | Yes | 180 | 4 | 4 | AHU

## McMichael
Sheet Last Modified: | 2021-04-29
School: | Morton McMichael Elementary School
Vendor: | Chadwick | Part 2 | Part 3
Part 4
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Staff Lounge | 125 | 8 |  | 468 | 10 | 8 | Unit Ventilator
101 | Admin | 281 | 18 |  | 1056 | 24 | 18 | Unit Ventilator
102 | Superintendants | 284 | 18 |  | 600 | 13 | 13 | Unit Ventilator
- | IT Office |  | 0 |  | 459 | 10 | 0
104 | Small Conf/Assis. Super | 110 | 7 |  | 252 | 5 | 5 | Unit Ventilator
105 | Large Conference | 319 | 21 |  | 1188 | 27 | 21 | Unit Ventilator
108 | Classroom | 375 | 25 |  | 864 | 19 | 19 | Unit Ventilator
110 | Classroom | 279 | 18 |  | 840 | 19 | 18 | Unit Ventilator
114 | Classroom | 284 | 18 |  | 576 | 13 | 13 | Unit Ventilator
200 | Classroom | 340 | 22 |  | 840 | 19 | 19 | Unit Ventilator
201 | Classroom | 328 | 21 |  | 840 | 19 | 19 | Unit Ventilator
201A | Classroom | 320 | 21 |  | 336 | 7 | 7 | Unit Ventilator
202 | Classroom | 292 | 19 |  | 840 | 19 | 19 | Unit Ventilator
204 | Classroom | 272 | 18 |  | 2592 | 58 | 18 | Unit Ventilator
205 | Classroom | 326 | 21 |  | 840 | 19 | 19 | Unit Ventilator
206 | Classroom | 275 | 18 |  | 2592 | 58 | 18 | Unit Ventilator
207 | Classroom | 318 | 21 |  | 840 | 19 | 19 | Unit Ventilator
208 | Classroom | 249 | 16 |  | 2592 | 58 | 16 | Unit Ventilator
210 | Classroom | 351 | 23 |  | 840 | 19 | 19 | Unit Ventilator
212 | Classroom | 363 | 24 |  | 840 | 19 | 19 | Unit Ventilator
214 | Classroom | 282 | 18 |  | 840 | 19 | 18 | Unit Ventilator
216 | Classroom | 262 | 17 |  | 864 | 19 | 17 | Unit Ventilator
217 | Classroom | 368 | 24 |  | 1944 | 44 | 24 | Unit Ventilator
218 | Classroom | 320 | 21 |  | 840 | 19 | 19 | Unit Ventilator
219 | Classroom | 351 | 23 |  | 1944 | 44 | 23 | Unit Ventilator
220 | Classroom | 403 | 26 |  | 840 | 19 | 19 | Unit Ventilator
222 | Classroom | 280 | 18 |  | 504 | 11 | 11 | Unit Ventilator
224 | Classroom |  | 0 |  | 840 | 19 | 0 | Unit Ventilator
226 | Classroom | 240 | 16 |  | 840 | 19 | 16 | Unit Ventilator
300 | Classroom | 239 | 15 |  | 840 | 19 | 15 | Unit Ventilator
301 | Classroom | 291 | 19 |  | 840 | 19 | 19 | Unit Ventilator
302 | Classroom | 302 | 20 |  | 840 | 19 | 19 | Unit Ventilator
303 | Classroom | 288 | 19 |  | 840 | 19 | 19 | Unit Ventilator
305 | Classroom | 317 | 21 |  | 840 | 19 | 19 | Unit Ventilator
306 | Classroom | 546 | 36 |  | 1248 | 28 | 28 | Unit Ventilator
307 | Classroom | 274 | 18 |  | 840 | 19 | 18 | Unit Ventilator
308 | Classroom | 273 | 18 |  | 864 | 19 | 18 | Unit Ventilator
310 | Classroom | 272 | 18 |  | 840 | 19 | 18 | Unit Ventilator
312 | Classroom | 281 | 18 |  | 840 | 19 | 18 | Unit Ventilator
314 | Classroom | 306 | 20 |  | 840 | 19 | 19 | Unit Ventilator
316 | Classroom | 315 | 21 |  | 864 | 19 | 19 | Unit Ventilator
317 | Classroom | 392 | 26 |  | 840 | 19 | 19 | Unit Ventilator
318 | Classroom | 274 | 18 |  | 840 | 19 | 18 | Unit Ventilator
319 | Classroom | 276 | 18 |  | 840 | 19 | 18 | Unit Ventilator
320 | Classroom | 281 | 18 |  | 840 | 19 | 18 | Unit Ventilator
322 | Classroom | 270 | 18 |  | 576 | 13 | 13 | Unit Ventilator
323 | Classroom | 279 | 18 |  | 864 | 19 | 18 | Unit Ventilator
324 | Classroom | 326 | 21 |  | 840 | 19 | 19 | Unit Ventilator
325 | Classroom | 285 | 19 |  | 888 | 20 | 19 | Unit Ventilator
326 | Classroom | 262 | 17 |  | 864 | 19 | 17 | Unit Ventilator
- | Auditorium | 520 | 34 |  | 4914 | 111 | 34 | AHU
- | Cafe | 590 | 39 |  | 2485 | 56 | 39 | AHU
- | Gym | 690 | 46 |  | 3621 | 82 | 46 | AHU
- | Main Office |  | 0 | Yes | 1401 | 31 | 31
- | Nurse Office |  | 0 | Yes | 616 | 14 | 14

## Meade
Sheet Last Modified: | 2021-04-06
School: | General George G. Meade Elementary-Middle School
Vendor: | EMCOR | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
15 | Classroom | 378 | 25 | Yes | 644 | 14 | 14 | Unit Ventilator
16 | Classroom | 336 | 22 |  | 833 | 18 | 18 | Unit Ventilator
17 | Classroom | 184 | 12 |  | 330 | 7 | 7 | Unit Ventilator
18 | Classroom | 686 | 45 | Yes | 1101 | 25 | 25 | Unit Ventilator
101 | Classroom | 294 | 19 |  | 892 | 20 | 19 | Unit Ventilator
102 | Classroom | 299 | 19 | Yes | 765 | 17 | 17 | Unit Ventilator
103 | Classroom | 360 | 24 | Yes | 823 | 18 | 18 | Unit Ventilator
104 | Classroom | 281 | 18 |  | 705 | 16 | 16 | Unit Ventilator
105 | Classroom | 445 | 29 |  | 674 | 15 | 15 | Unit Ventilator
106 | Classroom | 405 | 27 |  | 846 | 19 | 19 | Unit Ventilator
107 | Classroom | 332 | 22 |  | 526 | 11 | 11 | Unit Ventilator
108 | Classroom | 294 | 19 |  | 670 | 15 | 15 | Unit Ventilator
109 | Classroom | 279 | 18 |  | 705 | 16 | 16 | Unit Ventilator
115 | Classroom | 640 | 42 | Yes | 865 | 19 | 19 | Unit Ventilator
116 | Classroom | 325 | 21 | Yes | 413 | 9 | 9 | Unit Ventilator
117 | Classroom | 433 | 28 | Yes | 837 | 19 | 19 | Unit Ventilator
118 | Classroom | 664 | 44 | Yes | 849 | 19 | 19 | Unit Ventilator
200 | Classroom | 193 | 12 |  | 349 | 7 | 7 | Unit Ventilator
201 | Classroom | 414 | 27 |  | 667 | 15 | 15 | Unit Ventilator
202 | Classroom | 53 | 3 |  | 673 | 15 | 3 | Unit Ventilator
203 | Classroom | 275 | 18 |  | 666 | 15 | 15 | Unit Ventilator
204 | Classroom | 360 | 24 |  | 669 | 15 | 15 | Unit Ventilator
205 | Classroom | 343 | 22 |  | 701 | 15 | 15 | Unit Ventilator
206 | Classroom | 280 | 18 |  | 705 | 16 | 16 | Unit Ventilator
207 | Classroom | 303 | 20 |  | 671 | 15 | 15 | Unit Ventilator
208 | Classroom | 259 | 17 |  | 576 | 13 | 13 | Unit Ventilator
209 | Classroom | 0 | 0 |  | 540 | 12 | 0 | Unit Ventilator
210 | Classroom | 311 | 20 |  | 511 | 11 | 11 | Unit Ventilator
211 | Classroom | 222 | 14 |  | 720 | 16 | 14 | Unit Ventilator
215 | Classroom | 550 | 36 |  | 843 | 19 | 19 | Unit Ventilator
216 | Classroom | 306 | 20 |  | 855 | 19 | 19 | Unit Ventilator
217 | Classroom | 169 | 11 |  | 842 | 19 | 11 | Unit Ventilator
218 | Classroom | 631 | 42 |  | 852 | 19 | 19 | Unit Ventilator
285 | Classroom | 273 | 18 |  | 0 | 0 | 0 | Unit Ventilator
301 | Classroom | 883 | 58 |  | 2031 | 46 | 46 | Unit Ventilator
304 | Classroom | 276 | 18 |  | 670 | 15 | 15 | Unit Ventilator
305 | Classroom | 346 | 23 |  | 702 | 15 | 15 | Unit Ventilator
306 | Classroom | 319 | 21 |  | 706 | 16 | 16 | Unit Ventilator
307 | Classroom | 347 | 23 |  | 670 | 15 | 15 | Unit Ventilator
308 | Classroom | 112 | 7 |  | 852 | 19 | 7 | Unit Ventilator
309 | Classroom | 333 | 22 |  | 309 | 7 | 7 | Unit Ventilator
310 | Classroom | 247 | 16 |  | 510 | 11 | 11 | Unit Ventilator
311 | Classroom | 351 | 23 |  | 706 | 16 | 16 | Unit Ventilator
312 | Classroom | 305 | 20 |  | 514 | 11 | 11 | Unit Ventilator
315 | Classroom | 289 | 19 |  | 838 | 19 | 19 | Unit Ventilator
316 | Classroom | 285 | 19 |  | 855 | 19 | 19 | Unit Ventilator
317 | Classroom | 548 | 36 |  | 847 | 19 | 19 | Unit Ventilator
318 | Classroom | 647 | 43 |  | 852 | 19 | 19 | Unit Ventilator
- | Main Office |  | 0 | Yes | 305.08 | 6 | 6
- | Nurse Office |  | 0 | Yes | 242.55 | 5 | 5
- | 1st Floor Hall | 310 | 20 |  | 2688 | 61 | 20 | Unit Ventilator
- | 1st Floor Nurse RR | 0 | 0 |  | 244 | 5 | 0 | N/A
- | 1st Floor Staff Womens RR | 0 | 0 |  | 393 | 8 | 0 | N/A
- | 2nd Floor Hall | 0 | 0 |  | 2066 | 46 | 0 | Unit Ventilator
- | 2nd Floor Mens RR | 99 | 6 |  | 355 | 8 | 6 | N/A
- | 2nd Floor Womens RR | 236 | 15 |  | 328 | 7 | 7 | N/A
- | 3rd Floor Hall | 289 | 19 |  | 2661 | 60 | 19 | Unit Ventilator
- | 3rd Floor Mens RR | 95 | 6 |  | 259 | 5 | 5 | N/A
- | 3rd Floor Womens RR | 219 | 14 |  | 328 | 7 | 7 | N/A
- | Cafeteria | 754 | 50 |  | 5223 | 118 | 50 | Unit Ventilator
- | Bsmt: Boys RR | 0 | 0 |  | 765 | 17 | 0 | N/A
- | Bsmt: Grils RR | 0 | 0 |  | 697 | 15 | 0 | N/A
- | Staff Restroom: 1st Floor | 0 | 0 |  | 168 | 3 | 0 | N/A
- | Library | 0 | 0 |  | 2062.2 | 46 | 0 | Unit Ventilator
- | Staff Restroom: 2nd Floor | 0 | 0 |  | 305 | 6 | 0 | N/A
- | Staff Restroom: 3rd Floor | 0 | 0 |  | 308 | 7 | 0 | N/A

## Meehan
Sheet Last Modified: | 2021-04-08
School: | Austin Meehan Middle School
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
3 | Classroom | 280 | 18 |  | 1537 | 34 | 18 | Unit Ventilator
111 | Classroom | 323 | 21 |  | 917 | 20 | 20 | Unit Ventilator
112 | Classroom | 309 | 20 |  | 1490 | 33 | 20 | Unit Ventilator
113 | Classroom | 287 | 19 |  | 208 | 4 | 4 | Unit Ventilator
114 | Classroom | 307 | 20 |  | 1193 | 27 | 20 | Unit Ventilator
115 | Classroom | 274 | 18 |  | 1192 | 27 | 18 | Unit Ventilator
121 | Classroom | 0 | 0 |  | 944 | 21 | 0 | Unit Ventilator
122 | Classroom | 503 | 33 |  | 1085 | 24 | 24 | Unit Ventilator
123 | Classroom | 350 | 23 |  | 1175 | 26 | 23 | Unit Ventilator
124 | Classroom | 283 | 18 |  | 1123 | 25 | 18 | Unit Ventilator
125 | Classroom | 413 | 27 |  | 1156 | 26 | 26 | Unit Ventilator
126 | Classroom | 400 | 26 |  | 1064 | 24 | 24 | Unit Ventilator
127 | Classroom | 333 | 22 |  | 1198 | 27 | 22 | Unit Ventilator
128 | Classroom | 343 | 22 |  | 933 | 21 | 21 | Unit Ventilator
211 | Classroom | 327 | 21 |  | 867 | 19 | 19 | Unit Ventilator
212 | Classroom | 382 | 25 |  | 1630 | 37 | 25 | Unit Ventilator
213 | Classroom | 281 | 18 |  | 269 | 6 | 6 | Unit Ventilator
214 | Classroom | 372 | 24 |  | 1317 | 29 | 24 | Unit Ventilator
215 | Classroom | 396 | 26 |  | 1199 | 27 | 26 | Unit Ventilator
221 | Classroom | 0 | 0 |  | 1054 | 23 | 0 | Unit Ventilator
222 | Classroom | 337 | 22 |  | 1286 | 29 | 22 | Unit Ventilator
223 | Classroom | 343 | 22 |  | 1230 | 27 | 22 | Unit Ventilator
224 | Classroom | 0 | 0 |  | 1091 | 24 | 0 | Unit Ventilator
225 | Classroom | 420 | 28 |  | 1151 | 26 | 26 | Unit Ventilator
226 | Classroom | 397 | 26 |  | 1175 | 26 | 26 | Unit Ventilator
227 | Classroom | 327 | 21 |  | 1292 | 29 | 21 | Unit Ventilator
228 | Classroom | 0 | 0 |  | 931 | 21 | 0 | Unit Ventilator
311 | Classroom | 310 | 20 |  | 1041 | 23 | 20 | Unit Ventilator
312 | Classroom | 309 | 20 |  | 1602 | 36 | 20 | Unit Ventilator
313 | Classroom | 0 | 0 |  | 756 | 17 | 0 | Unit Ventilator
314 | Classroom | 0 | 0 |  | 1279 | 29 | 0 | Unit Ventilator
315 | Classroom | 0 | 0 |  | 1219 | 27 | 0 | Unit Ventilator
321 | Classroom | 0 | 0 |  | 1064 | 24 | 0 | Unit Ventilator
322 | Classroom | 460 | 30 |  | 1199 | 27 | 27 | Unit Ventilator
323 | Classroom | 0 | 0 |  | 1365 | 31 | 0 | Unit Ventilator
324 | Classroom | 377 | 25 |  | 1039 | 23 | 23 | Unit Ventilator
325 | Classroom | 270 | 18 |  | 1247 | 28 | 18 | Unit Ventilator
326 | Classroom | 493 | 32 |  | 1322 | 30 | 30 | Unit Ventilator
327 | Classroom | 417 | 27 |  | 1184 | 26 | 26 | Unit Ventilator
328 | Classroom | 397 | 26 |  | 955 | 21 | 21 | Unit Ventilator
411 | Classroom | 576 | 38 |  | 947 | 21 | 21 | Unit Ventilator
412 | Classroom | 352 | 23 |  | 1474 | 33 | 23 | Unit Ventilator
413 | Classroom | 307 | 20 |  | 208 | 4 | 4 | Unit Ventilator
414 | Classroom | 313 | 20 |  | 1255 | 28 | 20 | Unit Ventilator
415 | Classroom | 347 | 23 |  | 1215 | 27 | 23 | Unit Ventilator
421 | Classroom |  | 0 | Yes | 1058 | 24 | 24 | N/A
422 | Classroom | 463 | 30 |  | 1199 | 27 | 27 | Unit Ventilator
423 | Classroom | 363 | 24 |  | 1327 | 30 | 24 | Unit Ventilator
424 | Classroom | 300 | 20 |  | 1365 | 31 | 20 | Unit Ventilator
425 | Classroom | 383 | 25 |  | 1350 | 30 | 25 | Unit Ventilator
426 | Classroom | 450 | 30 |  | 1201 | 27 | 27 | Unit Ventilator
427 | Classroom | 357 | 23 |  | 1242 | 28 | 23 | Unit Ventilator
428 | Classroom | 390 | 26 |  | 1054 | 23 | 23 | Unit Ventilator
A-01 A | Art | 599 | 39 |  | 1692 | 38 | 38 | Unit Ventilator
A-02 | Art | 288 | 19 |  |  | 0 | 0 | Unit Ventilator
A-03 A | Art | 648 | 43 |  | 1692 | 38 | 38 | Unit Ventilator
- | Boys Locker Room | 1404 | 93 |  | 700 | 15 | 15 | AHU
- | Girls Locker Room | 1531 | 102 |  | 700 | 15 | 15 | AHU
Ground Level Pod #1 | Auditorium Control room | 0 | 0 |  | 102 | 2 | 0 | AHU
Ground Level Pod #1 | Center Core | 163 | 10 |  | 528 | 12 | 10 | AHU
Ground Level Pod #1 | Center Core | 297 | 19 |  | 1012 | 23 | 19 | AHU
Ground Level Pod #1 | Conference | 38 | 2 |  | 150 | 3 | 2 | AHU
Ground Level Pod #1 | Counselor | 0 | 0 |  | 80 | 1 | 0 | AHU
Ground Level Pod #1 | Entryway | 0 | 0 |  | 238 | 5 | 0 | AHU
Ground Level Pod #1 | Entryway | 32 | 2 |  | 238 | 5 | 2 | AHU
Ground Level Pod #1 | Lobby | 113 | 7 |  | 1625 | 36 | 7 | AHU
Ground Level Pod #1 | Lobby Entryway | 55 | 3 |  | 238 | 5 | 3 | AHU
Ground Level Pod #1 | Main Office - Waiting | 143 | 9 |  | 1550 | 35 | 9 | AHU
Ground Level Pod #1 | Main Office 1 | 63 | 4 |  | 130 | 2 | 2 | AHU
Ground Level Pod #1 | Main Office 2 | 74 | 4 |  | 231 | 5 | 4 | AHU
Ground Level Pod #1 | Main Office 3 | 41 | 2 |  | 110 | 2 | 2 | AHU
Ground Level Pod #1 | Main Office 4 | 135 | 9 |  | 156 | 3 | 3 | AHU
Ground Level Pod #1 | Office | 28 | 1 |  | 143 | 3 | 1 | AHU
Ground Level Pod #1 | Office Floor | 0 | 0 |  | 500 | 11 | 0 | AHU
Ground Level Pod #1 | Ticket Booth | 0 | 0 |  |  | 0 | 0 | AHU
Ground level Pod #2 | Cafeteria | 374 | 24 |  | 2900 | 65 | 24 | AHU
Ground level Pod #2 | Center Core | 68 | 4 |  | 400 | 9 | 4 | AHU
Ground level Pod #2 | Entryway | 32 | 2 |  | 300 | 6 | 2 | AHU
Ground level Pod #2 | Office | 8 | 0 |  |  | 0 | 0 | AHU
Ground level Pod #2 | Pod Center Core | 116 | 7 |  | 925 | 21 | 7 | AHU
Ground Level Pod #3 | Cafeteria | 59 | 3 |  | 2900 | 65 | 3 | AHU
Ground Level Pod #3 | Center Core | 272 | 18 |  | 425 | 9 | 9 | AHU
Ground Level Pod #3 | Entryway | 68 | 4 |  | 460 | 10 | 4 | AHU
Ground Level Pod #3 | Pod Center Core | 174 | 11 |  | 900 | 20 | 11 | AHU
Ground Level Pod #3 | Pod Center Prep | 30 | 2 |  | 945 | 21 | 2 | AHU
Ground level Pod #4 | Center Ring - Counselor | 34 | 2 |  | 110 | 2 | 2 | AHU
Ground level Pod #4 | Center Ring - Police | 0 | 0 |  | 187 | 4 | 0 | AHU
Ground level Pod #4 | Center Ring - Social Work | 36 | 2 |  | 110 | 2 | 2 | AHU
Ground Level Pod #4 | Mayfair Center Core | 63 | 4 |  | 425 | 9 | 4 | AHU
Ground Level Pod #4 | Mayfair Conference | 27 | 1 |  | 156 | 3 | 1 | AHU
Ground Level Pod #4 | Mayfair Entry way | 0 | 0 |  | 204 | 4 | 0 | AHU
Ground Level Pod #4 | Mayfair Nurse Office | 0 | 0 |  | 216 | 4 | 0 | AHU
Ground Level Pod #4 | Mayfair Office | 0 | 0 |  | 144 | 3 | 0 | AHU
Ground Level Pod #4 | Mayfair Pod Center Core | 21 | 1 |  | 969 | 22 | 1 | AHU
Ground Level Pod #4 | Mayfair Pod Center Prep | 0 | 0 |  | 646 | 14 | 0 | AHU
Ground Level Pod #4 | Mayfair Principal Office | 0 | 0 |  | 190 | 4 | 0 | AHU
Ground Level Pod #4 | Nurse Exam | 62 | 4 |  | 54 | 1 | 1 | AHU
Ground Level Pod #4 | Nurse Office | 93 | 6 |  | 420 | 9 | 6 | AHU
Ground Level Pod #4 | Roster Area Entry | 134 | 8 |  | 150 | 3 | 3 | AHU
Ground Level Pod #4 | Roster Room | 64 | 4 |  | 80 | 1 | 1 | AHU
- | Gym | 3715 | 247 |  | 3700 | 84 | 84 | AHU
Lower Level Pod #2 | M-1 Band - Ensemble | 60 | 4 |  | 459 | 10 | 4 | AHU
Lower Level Pod #2 | M-1 Band - Office | 30 | 2 |  | 600 | 13 | 2 | AHU
Lower Level Pod #2 | M-1 Band - Practice 1 | 59 | 3 |  | 450 | 10 | 3 | AHU
Lower Level Pod #2 | Math Rm - Office | 30 | 2 |  | 104 | 2 | 2 | AHU
Lower Level Pod #2 | Math Rm - Storage | 0 | 0 |  | 50 | 1 | 0 | AHU
Lower Level Pod #2 | Storage | 0 | 0 |  |  | 0 | 0 | AHU
Lower Level Pod #2 | Visual Com. Lab - Darkroom | 58 | 3 |  | 380 | 8 | 3 | AHU
Lower Level Pod #4 | Center Core Art-01,02,03 | 60 | 4 |  | 1692 | 38 | 4 | AHU
Lower Level Pod #4 | Center Core Storage | 21 | 1 |  |  | 0 | 0 | AHU
Lower Level Pod #4 | Classroom #3 Office | 25 | 1 |  | 144 | 3 | 1 | AHU
Lower Level Pod #4 | Classroom #3 Prep | 27 | 1 |  | 50 | 1 | 1 | AHU
Lower Level Pod #4 | Classroom #3 Storage | 24 | 1 |  | 126 | 2 | 1 | AHU
Lower Level Pod #4 | M-5 Band Rm Ensemble | 46 | 3 |  | 1734 | 39 | 3 | AHU
Lower Level Pod #4 | M-5 Band Rm Office | 0 | 0 |  | 100 | 2 | 0 | AHU
Lower Level Pod #4 | M-5 Band Rm Practice 1 | 0 | 0 |  | 40 | 0 | 0 | AHU
Lower Level Pod #4 | M-5 Band Rm Practice 2 | 0 | 0 |  | 40 | 0 | 0 | AHU
M-1 B | Band Room | 323 | 21 |  | 1178 | 26 | 21 | Unit Ventilator
M-5 | Band Room | 0 | 0 |  | 1734 | 39 | 0 | Unit Ventilator
Math Lab | Classroom | 338 | 22 |  | 1337 | 30 | 22 | Unit Ventilator
S-01 A | Power Tech Lab | 312 | 20 |  | 1472 | 33 | 20 | Unit Ventilator
S-02 A | Engineering Lab | 797 | 53 |  | 1985 | 45 | 45 | Unit Ventilator
S-03 | Visual Comm. Lab | 321 | 21 |  | 1379 | 31 | 21 | Unit Ventilator
Technology Lab | Classroom | 326 | 21 |  | 1025 | 23 | 21 | Unit Ventilator
- | Auditorium | 4818 | 321 |  | 4485 | 101 | 101 | AHU
Upper Level | Mayfair Multi-Purpose Room | 835 | 55 |  | 5781 | 131 | 55 | AHU
129A | Upper Level Pod #1 Classroom | 264 | 17 |  | 731 | 16 | 16 | AHU
Upper Level Pod #1 | Core | 309 | 20 |  | 540 | 12 | 12 | AHU
Upper Level Pod #1 | Deans Office | 355 | 23 |  | 480 | 10 | 10 | AHU
Upper Level Pod #1 | Pod Center Core | 0 | 0 |  | 616 | 14 | 0 | AHU
430 | Upper Level Multi-Purpose Mayfair Classroom | 90 | 6 | Yes | 1249 | 28 | 28 | AHU
431 | Upper Level Multi-Purpose Mayfair Classroom | 136 | 9 | Yes | 789 | 17 | 17 | AHU
Upper Level Pod #2 | Core | 0 | 0 |  | 425 | 9 | 0 | AHU
432 | Upper Level Pod #2 Lab B/C (Mayfair Room) | 212 | 14 | Yes | 928 | 21 | 21 | AHU
433 | Upper Level Pod #2 Mayfair Kindergarten (Mayfair Room) | 184 | 12 | Yes | 1145 | 26 | 26 | AHU
Upper Level Pod #2 | Pod Center Core | 0 | 0 |  | 2968 | 67 | 0 | AHU
Upper Level Pod #3 | Center Core | 0 | 0 |  | 616 | 14 | 0 | AHU
Upper Level Pod #3 | Lab C Classroom | 187 | 12 |  | 806 | 18 | 12 | AHU
Upper Level Pod #3 | Lab Office | 28 | 1 |  | 120 | 2 | 1 | AHU
Upper Level Pod #3 | Pod Center Core | 0 | 0 |  | 2968 | 67 | 0 | AHU
Upper Level Pod #4 | Mayfair Center Core | 174 | 11 |  | 4366 | 99 | 11 | AHU
429 | Upper Level Pod #4 Mayfair Classroom | 263 | 17 |  | 1008 | 22 | 17 | AHU
Upper Level Pod #4 | Mayfair Counselor Office | 79 | 5 |  | 132 | 3 | 3 | AHU
Upper Level Pod #4 | Mayfair Multi-Purpose Room | 424 | 28 |  | 4662 | 105 | 28 | AHU
Upper Level Pod #4 | Mayfair Principal Office | 83 | 5 |  | 180 | 4 | 4 | AHU
Weight Room | Classroom | 107 | 7 |  | 210 | 4 | 4 | AHU

## Meredith
Sheet Last Modified: | 2021-04-27
School: | William M. Meredith Elementary-Middle School
William M. Meredith Elementary-Middle School Modular Building
Vendor: | Capital
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
B5 | Classroom |  | 0 | Yes | 696 | 15 | 15
102 | Classroom |  | 0 | Yes | 690 | 15 | 15
103 | Classroom |  | 0 | Yes | 690 | 15 | 15
104 | Classroom |  | 0 | Yes | 690 | 15 | 15
105 | Classroom |  | 0 | Yes | 920 | 20 | 20
106 | Classroom |  | 0 | Yes | 816 | 18 | 18
107 | Classroom |  | 0 | Yes | 664 | 15 | 15
108 | Classroom |  | 0 | Yes | 664 | 15 | 15
201 | Classroom |  | 0 | Yes | 667 | 15 | 15
202 | Classroom |  | 0 | Yes | 690 | 15 | 15
204.5 | Classroom |  | 0 | Yes | 425 | 9 | 9
205 | Classroom |  | 0 | Yes | 782 | 17 | 17
206 | Classroom |  | 0 | Yes | 759 | 17 | 17
206A | Classroom |  | 0 | Yes | 368 | 8 | 8
207 | Classroom |  | 0 | Yes | 506 | 11 | 11
208 | Classroom |  | 0 | Yes | 664 | 15 | 15
301 | Classroom |  | 0 | Yes | 696 | 15 | 15
302 | Classroom |  | 0 | Yes | 682 | 15 | 15
303 | Classroom |  | 0 | Yes | 638 | 14 | 14
304 | Classroom |  | 0 | Yes | 667 | 15 | 15
305 | Classroom |  | 0 | Yes | 1210 | 27 | 27
306 | Classroom |  | 0 | Yes | 782 | 17 | 17
307 | Classroom |  | 0 | Yes | 667 | 15 | 15
308 | Classroom |  | 0 | Yes | 667 | 15 | 15
309 | Classroom |  | 0 | Yes | 648 | 14 | 14
309A | Classroom |  | 0 |  | 420 | 9 | 0
- | Auditorium |  | 0 |  | 3185 | 72 | 0
- | Counselors Office |  | 0 | Yes | 375 | 8 | 8
- | Gym |  | 0 |  | 3723 | 84 | 0
- | Library |  | 0 | Yes | 1298 | 29 | 29
- | Lunchroom |  | 0 |  | 2250 | 51 | 0
- | Main office |  | 0 | Yes | 368 | 8 | 8
- | Nurses Office |  | 0 | Yes | 168 | 3 | 3
- | Principals office |  | 0 | Yes | 256 | 5 | 5
- | Psych Office #1 |  | 0 |  | 138 | 3 | 0
- | Psych Office #2 |  | 0 |  | 88 | 2 | 0
- | Teachers Lounge |  | 0 |  | 322 | 7 | 0
Modular Building
1 | Classroom | 368 | 24 |  | 720 | 16 | 16 | AHU
2 | Classroom | 378 | 25 |  | 720 | 16 | 16 | AHU
3 | Classroom | 381 | 25 |  | 720 | 16 | 16 | AHU
4 | Classroom | 374 | 24 |  | 720 | 16 | 16 | AHU

## Mifflin
Sheet Last Modified: | 2021-04-26
School: | Thomas Mifflin Elementary School
Vendor: | EMCOR | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 253 | 16 | Yes | 794 | 18 | 18 | Unit Ventilator
102 | Classroom | 555 | 37 |  | 1040 | 23 | 23 | Unit Ventilator
103 | Classroom | 288 | 19 |  | 375 | 8 | 8 | Unit Ventilator
104 | Classroom | 270 | 18 |  | 537 | 12 | 12 | Unit Ventilator
105 | Classroom | 395 | 26 |  | 484 | 11 | 11 | Unit Ventilator
106 | Classroom | 422 | 28 |  | 682 | 15 | 15 | Unit Ventilator
107 | Classroom | 330 | 22 |  | 658 | 14 | 14 | Unit Ventilator
108 | Classroom | 439 | 29 |  | 690 | 15 | 15 | Unit Ventilator
109 | Classroom | 230 | 15 |  | 662 | 15 | 15 | Unit Ventilator
110 | Classroom | 348 | 23 |  | 669 | 15 | 15 | Unit Ventilator
111 | Classroom | 587 | 39 |  | 531 | 12 | 12 | Unit Ventilator
114 | Classroom | 0 | 0 | Yes | 630 | 14 | 14 | Unit Ventilator
115 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | Unit Ventilator
128 (117) | Counselor Office | 376 | 25 |  | 350 | 7 | 7 | Unit Ventilator
201 | Classroom | 595 | 39 |  | 775 | 17 | 17 | Unit Ventilator
202 | Classroom | 638 | 42 |  | 764 | 17 | 17 | Unit Ventilator
203 | Classroom | 300 | 20 |  | 340 | 7 | 7 | Unit Ventilator
204 | Classroom | 354 | 23 |  | 639 | 14 | 14 | Unit Ventilator
205 | Classroom | 458 | 30 |  | 682 | 15 | 15 | Unit Ventilator
206 | Classroom | 432 | 28 |  | 688 | 15 | 15 | Unit Ventilator
207 | Classroom | 606 | 40 |  | 686 | 15 | 15 | Unit Ventilator
209 | Classroom | 241 | 16 |  | 686 | 15 | 15 | Unit Ventilator
210 | Classroom | 598 | 39 |  | 1380 | 31 | 31 | Unit Ventilator
211 | Classroom | 408 | 27 |  | 690 | 15 | 15 | Unit Ventilator
212 | Meeting Room | 1055 | 70 |  | 312 | 7 | 7 | Unit Ventilator
215 | Classroom |  | 0 | Yes | 323 | 7 | 7 | Unit Ventilator
- | Auditorium | 0 | 0 |  | 3837 | 87 | 0 | House Fan
- | Cafeteria | 270 | 18 | Yes | 2128 | 48 | 48 | Unit Ventilator
- | Cafeteria Hall | 0 | 0 |  | 738 | 16 | 0 | Unit Ventilator
- | Library | 403 | 26 |  | 3024 | 68 | 26 | Unit Ventilator
- | Music Room | 425 | 28 |  | 966 | 21 | 21 | Unit Ventilator
Pre-K 3 | Classroom | 489 | 32 |  | 972 | 22 | 22 | Unit Ventilator
Pre-K 4 | Classroom | 335 | 22 |  | 920 | 20 | 20 | Unit Ventilator
- | Main Office |  | 0 | Yes | 552 | 12 | 12
- | Principal Office |  | 0 | Yes | 390 | 8 | 8
- | Nurses Office |  | 0 | Yes | 192 | 4 | 4
- | Gym | 4205 | 280 |  | 5280 | 120 | 120 | RTU
6 | Speech |  | 0 | Yes | 544 | 12 | 12
8 | Classroom |  | 0 | Yes | 851 | 19 | 19
20 | Special Needs |  | 0 | Yes | 661 | 15 | 15
- | Spanish Classroom | 0 | 0 | Yes | 900 | 20 | 20 | Unit Ventilator

## Miller
Sheet Last Modified: | 2021-04-28
School: | E. Spencer Miller- Philadelphia Learning Academy South (9-12) and Crossroads Acelerated Academy (7-8)
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
153 | Office | 0 | 0 |  | 187 | 4 | 0
158 | School Police Office | 267 | 17 |  | 540 | 12 | 12
167 | Staff Lounge | 0 | 0 |  | 532 | 12 | 0
170 | Office | 0 | 0 |  | 99 | 2 | 0
175 | Office | 0 | 0 |  | 154 | 3 | 0
181 | Office | 49 | 3 |  | 344 | 7 | 3
183 | Office | 10 | 0 |  | 110 | 2 | 0
184 | Office | 7 | 0 |  | 100 | 2 | 0
185 | Office | 17 | 1 |  | 220 | 5 | 1
186 | Office | 27 | 1 |  | 208 | 4 | 1
188 | Office | 201 | 13 |  | 77 | 1 | 1
192 | Office | 289 | 19 |  | 111 | 2 | 2
245 | Office | 17 | 1 |  | 170 | 3 | 1
246 | Office | 41 | 2 |  | 131 | 2 | 2
247 | Office | 33 | 2 |  | 167 | 3 | 2
248 | Office | 0 | 0 |  | 152 | 3 | 0
252 | Office | 0 | 0 |  | 516 | 11 | 0
254 | Office | 166 | 11 |  | 231 | 5 | 5
255 | Office | 46 | 3 |  | 98 | 2 | 2
256 | Office | 94 | 6 |  | 140 | 3 | 3
257 | Office | 396 | 26 |  | 120 | 2 | 2
258 | Office | 58 | 3 |  | 531 | 12 | 3
262 | Office | 111 | 7 |  | 102 | 2 | 2
266 | Office | 762 | 50 |  | 381 | 8 | 8
267 | Office | 949 | 63 |  | 437 | 9 | 9
274 | Office | 192 | 12 |  | 148 | 3 | 3
275 | Office | 130 | 8 |  | 117 | 2 | 2
276 | Office | 72 | 4 |  | 101 | 2 | 2
277 | Office | 176 | 11 |  | 147 | 3 | 3
278 | Office | 107 | 7 |  | 109 | 2 | 2
279 | Office | 104 | 6 |  | 106 | 2 | 2
280 | Office | 287 | 19 |  | 254 | 5 | 5
282 | Office | 311 | 20 |  | 272 | 6 | 6
286 | Office | 636 | 42 |  | 290 | 6 | 6
287 | Office | 104 | 6 |  | 107 | 2 | 2
290 | Office | 108 | 7 |  | 132 | 3 | 3
291 | Office | 107 | 7 |  | 151 | 3 | 3
292 | Office | 210 | 14 |  | 150 | 3 | 3
293 | Office | 186 | 12 |  | 153 | 3 | 3
- | 1st Flr Computer Room | 0 | 0 |  | 240 | 5 | 0
- | 1st Flr Corrider by B & E Section | 0 | 0 |  | 320 | 7 | 0
- | 1st Flr Kitchen | 8316 | 554 |  | 924 | 21 | 21
- | 1st Flr Kitchen Dry Food Area | 171 | 11 |  | 187 | 4 | 4
- | 1st Flr Kitchen Freezer Area | 85 | 5 |  | 420 | 9 | 5
- | 1st Flr Mechanical Room | 19 | 1 |  | 336 | 7 | 1
- | 2nd Floor Conference Room | 359 | 23 |  | 216 | 4 | 4
- | 2nd Floor Corridor by Elevator | 363 | 24 |  | 463 | 10 | 10
- | 2nd Floor Meeting Room | 139 | 9 |  | 79 | 1 | 1
- | 2nd Floor Mens Restroom by Elevator | 138 | 9 |  | 255 | 5 | 5
- | 2nd Floor Restroom Vestibule by Elevator | 157 | 10 |  | 73 | 1 | 1
- | 2nd Floor Womans Restroom by Elevator | 114 | 7 |  | 167 | 3 | 3
- | 2nd Flr Corridor by Admin Office | 195 | 13 |  | 218 | 4 | 4
- | 2nd Flr Corridor by G Section | 45 | 3 |  | 458 | 10 | 3
- | 2nd Flr Reception Office | 170 | 11 |  | 116 | 2 | 2
- | 1st Flr A - Common Area | 48 | 3 |  | 1251 | 28 | 3
A1 | Classroom | 58 | 3 |  | 960 | 21 | 3
A2 | Classroom | 66 | 4 |  | 990 | 22 | 4
A3 | Classroom | 60 | 4 |  | 990 | 22 | 4
A4 | Classroom | 56 | 3 |  | 997 | 22 | 3
- | 1st Flr B - Common Area | 747 | 49 |  | 960 | 21 | 21
B1 | Classroom | 304 | 20 |  | 868 | 19 | 19
B2 | Classroom | 488 | 32 |  | 945 | 21 | 21
B3 | Classroom | 942 | 62 |  | 980 | 22 | 22
B4 | Classroom | 961 | 64 |  | 910 | 20 | 20
- | C - Common Area 1st Flr | 1014 | 67 |  | 1285 | 29 | 29
C-1 | Classroom | 885 | 59 |  | 816 | 18 | 18
C-2 | Classroom | 1047 | 69 |  | 840 | 19 | 19
C-3 | Classroom | 1200 | 80 |  | 840 | 19 | 19
C-4 | Classroom | 828 | 55 |  | 868 | 19 | 19
- | Climate Masters Office | 150 | 10 |  | 821 | 18 | 10
- | Computer Support Specialist Office | 102 | 6 |  | 88 | 2 | 2
- | Corridor 2nd Floor near office 252 | 0 | 0 |  | 376 | 8 | 0
- | 1st Flr Corridor By B Section | 0 | 0 |  | 360 | 8 | 0
- | Corridor by D Section | 713 | 47 |  | 438 | 9 | 9
- | Corridor by Main Office | 38 | 2 |  | 610 | 13 | 2
- | Corridor by Office 258 | 107 | 7 |  | 160 | 3 | 3
- | 2nd Flr D - Common Area | 202 | 13 |  | 910 | 20 | 13
D1 | Classroom | 206 | 13 |  | 960 | 21 | 13
D2 | Classroom | 132 | 8 |  | 901 | 20 | 8
D3 | Classroom | 268 | 17 |  | 1007 | 22 | 17
D4 | Classroom | 209 | 13 |  | 972 | 22 | 13
- | Dr. Graham Principal Office | 111 | 7 |  | 823 | 18 | 7
- | 2nd Flr E - Common Area | 431 | 28 |  | 934 | 21 | 21
E1 | Classroom | 633 | 42 |  | 919 | 20 | 20
E2 | Classroom | 593 | 39 |  | 1021 | 23 | 23
E3 | Classroom | 594 | 39 |  | 1046 | 23 | 23
E4 | Classroom | 647 | 43 |  | 984 | 22 | 22
- | 2nd Flr G - Common Area | 12 | 0 |  | 1214 | 27 | 0
G1 | Classroom | 40 | 2 |  | 862 | 19 | 2
G2 | Classroom | 29 | 1 |  | 878 | 19 | 1
G3 | Classroom | 26 | 1 |  | 884 | 20 | 1
G4 | Classroom | 33 | 2 |  | 872 | 19 | 2
- | 1 st Flr Gym | 5785 | 385 |  | 3888 | 88 | 88
- | Late Check Office | 0 | 0 |  | 96 | 2 | 0
- | Main Entrance | 5 | 0 |  | 64 | 1 | 0
- | 1st Flr Media Room | 524 | 34 |  | 1539 | 34 | 34
- | Meeting Room | 21 | 1 |  | 90 | 2 | 1
- | Mens Restroom by Elevator | 26 | 1 |  | 190 | 4 | 1
- | Nurses Office | 584 | 38 |  | 412 | 9 | 9
- | Office Corridor | 228 | 15 |  | 702 | 15 | 15
- | Parking Lot Entry | 0 | 0 |  | 135 | 3 | 0
- | Reception | 47 | 3 |  | 521 | 11 | 3
- | Restroom Vestibule Between A1/A2 | 6 | 0 |  | 56 | 1 | 0
- | Restroom Vestibule Between A3/A4 | 4 | 0 |  | 56 | 1 | 0
- | Restroom Vestibule Between B1/B2 | 83 | 5 |  | 63 | 1 | 1
- | Restroom Vestibule Between B3/B4 | 49 | 3 |  | 63 | 1 | 1
- | Restroom Vestibule Between C1/C2 | 89 | 5 |  | 56 | 1 | 1
- | Restroom Vestibule Between C3/C4 | 93 | 6 |  | 63 | 1 | 1
- | Restroom Vestibule Between D1/D2 | 20 | 1 |  | 50 | 1 | 1
- | Restroom Vestibule Between D3/D4 | 27 | 1 |  | 51 | 1 | 1
- | Restroom Vestibule Between E1/E2 | 55 | 3 |  | 51 | 1 | 1
- | Restroom Vestibule Between E3/E4 | 54 | 3 |  | 51 | 1 | 1
- | Restroom Vestibule Between G1/G2 | 3 | 0 |  | 50 | 1 | 0
- | Restroom Vestibule Between G3/G4 | 2 | 0 |  | 51 | 1 | 0
- | 1st Flr Storage Room | 61 | 4 |  | 475 | 10 | 4
- | Truancy Office 1st Floor | 0 | 0 |  | 727 | 16 | 0
- | Vestibule by stairs/Rooms 266 & 267 | 153 | 10 |  | 219 | 4 | 4
- | Vistibule by Meeting Room | 132 | 8 |  | 252 | 5 | 5
- | Womans Restroom by 1st Floor Elevator | 26 | 1 |  | 169 | 3 | 1

## Mitchell
Sheet Last Modified: | 2021-05-03
School: | Mitchell Elementary School
EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
102 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
103 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
104 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
105 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
106 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
107 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
108 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
109 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
110 | Counselor's Office |  | 0 | Yes | 255 | 5 | 5 | House Fan
111 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
112 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
213 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
214 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
215 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
216 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
217 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
218 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
219 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
220 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
221 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
222 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
223 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
225 | Nurse |  | 0 | Yes | 378 | 8 | 8 | House Fan
324 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
325 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
326 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
327 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
328 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
329 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
330 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
331 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
332 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
333 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
334 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
B1 | Classroom |  | 0 | Yes | 756 | 17 | 17 | Unit Ventilator
B2 | B.E. Office |  | 0 | Yes | 200 | 4 | 4
B3 | Classroom |  | 0 | Yes | 609 | 13 | 13 | Unit Ventilator
B4 | Classroom |  | 0 | Yes | 980 | 22 | 22 | Unit Ventilator
B6 | Classroom |  | 0 | Yes | 1344 | 30 | 30 | Unit Ventilator
- | SP Office |  | 0 | Yes | 88 | 2 | 2
- | Library |  | 0 | Yes | 1504 | 34 | 34
- | Gym |  | 0 | Yes | 3495 | 79 | 79 | House Fan
- | Cafeteria Office |  | 0 | Yes | 134 | 3 | 3
- | Cafeteria |  | 0 | Yes | 2452 | 55 | 55 | House Fan
- | Main Office |  | 0 | Yes | 494 | 11 | 11 | House Fan
- | Principal's Office |  | 0 | Yes | 216 | 4 | 4 | House Fan
110C | Vice Principal's Office |  | 0 | Yes | 101 | 2 | 2
110A | Administrative Assistant's Office |  | 0 | Yes | 191 | 4 | 4
- | Teacher's Lounge/Multipurpose |  | 0 | Yes | 390 | 8 | 8 | House Fan
110B | Counselor's Office |  | 0 | Yes | 242 | 5 | 5 | House Fan

## MLK HS
Sheet Last Modified: | 2021-04-19
School: | The Promise Academy @ Martin Luther King High School
Vendor: | Meehan (Auditorium) | Chadwick (Building) | Exhaust
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 464 | 30 |  | 828 | 18 | 18
102 | Classroom | 315 | 21 |  | 828 | 18 | 18
104 | Classroom | 260 | 17 |  | 900 | 20 | 17
105 | Classroom | 162 | 10 |  | 1050 | 23 | 10
106 | Classroom | 476 | 31 |  | 900 | 20 | 20
107 | Classroom | 229 | 15 |  | 864 | 19 | 15
108 | Classroom | 489 | 32 |  | 850 | 19 | 19
109 | Classroom | 304 | 20 |  | 896 | 20 | 20
110 | Classroom |  | 0 |  | 800 | 18 | 0
116 | Classroom |  | 0 |  | 800 | 18 | 0
117 | Classroom | 296 | 19 |  | 924 | 21 | 19
118 | Classroom | 278 | 18 |  | 864 | 19 | 18
120 | Classroom | 105 | 7 |  | 864 | 19 | 7
121 | Classroom | 176 | 11 |  | 864 | 19 | 11
122 | Classroom | 420 | 28 |  | 1152 | 26 | 26
123 | Classroom | 86 | 5 |  | 864 | 19 | 5
124 | Classroom | 252 | 16 |  | 900 | 20 | 16
125 | Classroom | 203 | 13 |  | 864 | 19 | 13
201 | Classroom | 215 | 14 |  | 828 | 18 | 14
202 | Classroom | 201 | 13 |  | 864 | 19 | 13
204 | Classroom |  | 0 |  | 900 | 20 | 0
205 | Classroom | 416 | 27 |  | 1050 | 23 | 23
206 | Classroom | 47 | 3 |  | 900 | 20 | 3
207 | Classroom | 90 | 6 |  | 864 | 19 | 6
208 | Classroom | 212 | 14 |  | 850 | 19 | 14
209 | Classroom | 360 | 24 |  | 896 | 20 | 20
210 | Classroom | 0 | 0 |  | 800 | 18 | 0
216 | Classroom | 469 | 31 |  | 800 | 18 | 18
217 | Classroom | 130 | 8 |  | 924 | 21 | 8
218 | Classroom | 293 | 19 |  | 864 | 19 | 19
220 | Classroom | 318 | 21 |  | 864 | 19 | 19
221 | Classroom | 204 | 13 |  | 864 | 19 | 13
222 | Classroom | 210 | 14 |  | 1152 | 26 | 14
223 | Classroom | 170 | 11 |  | 864 | 19 | 11
224 | Classroom | 207 | 13 |  | 900 | 20 | 13
225 | Classroom | 150 | 10 |  | 864 | 19 | 10
301 | Classroom | 161 | 10 |  | 828 | 18 | 10
302 | Classroom | 178 | 11 |  | 864 | 19 | 11
303 | Classroom |  | 0 | Yes | 805 | 18 | 18
304 | Classroom | 391 | 26 |  | 900 | 20 | 20
305 | Classroom | 244 | 16 |  | 1050 | 23 | 16
306 | Classroom | 347 | 23 |  | 900 | 20 | 20
307 | Classroom | 99 | 6 |  | 864 | 19 | 6
308 | Classroom | 217 | 14 |  | 850 | 19 | 14
309 | Classroom | 65 | 4 |  | 896 | 20 | 4
310 | Classroom | 347 | 23 |  | 800 | 18 | 18
313 | Classroom |  | 0 | Yes | 1368 | 31 | 31
316 | Classroom | 297 | 19 |  | 800 | 18 | 18
317 | Classroom | 201 | 13 |  | 924 | 21 | 13
318 | Classroom | 275 | 18 |  | 864 | 19 | 18
320 | Classroom | 303 | 20 |  | 864 | 19 | 19
321 | Classroom | 85 | 5 |  | 864 | 19 | 5
322 | Classroom | 310 | 20 |  | 1152 | 26 | 20
323 | Classroom | 310 | 20 |  | 864 | 19 | 19
324 | Classroom | 213 | 14 |  | 900 | 20 | 14
325 | Classroom | 84 | 5 |  | 864 | 19 | 5
327 | Classroom |  | 0 | Yes | 1824 | 41 | 41
- | Auditorium | 13590 | 906 |  | 4350 | 98 | 98

## Moffet
Sheet Last Modified: | 2021-03-18
School: | John Moffet Elementary School
Vendor: | Devine Brothers |  | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101A | Classroom | 97 | 6 |  | 360 | 8 | 6 | AHU
104 | Classroom | 225 | 15 |  | 704 | 16 | 15 | Unit Ventilator
105 | Classroom | 205 | 13 |  | 575 | 13 | 13 | Unit Ventilator
107 | Classroom | 271 | 18 |  | 805 | 18 | 18 | Unit Ventilator
108 | Classroom | 327 | 21 |  | 782 | 17 | 17 | Unit Ventilator
112 | Classroom | 524 | 34 |  | 896 | 20 | 20 | Unit Ventilator
113 | Classroom | 293 | 19 |  | 928 | 21 | 19 | Unit Ventilator
114 | Classroom | 441 | 29 |  | 986 | 22 | 22 | Unit Ventilator
115 | Classroom | 337 | 22 |  | 868 | 19 | 19 | Unit Ventilator
119 | Nurse | 178 | 11 |  | 77 | 1 | 1 | AHU
201 | Classroom | 105 | 7 |  | 315 | 7 | 7 | Unit Ventilator
202 | Classroom | 745 | 49 |  | 891 | 20 | 20 | Unit Ventilator
203 | Classroom | 301 | 20 |  | 754 | 17 | 17 | Unit Ventilator
204 | Classroom | 357 | 23 |  | 754 | 17 | 17 | Unit Ventilator
205 | Classroom | 267 | 17 |  | 667 | 15 | 15 | Unit Ventilator
208 | Classroom | 183 | 12 |  | 924 | 21 | 12 | Unit Ventilator
209 | Classroom | 542 | 36 |  | 667 | 15 | 15 | Unit Ventilator
211 | Classroom | 543 | 36 |  | 648 | 14 | 14 | Unit Ventilator
213 | Classroom | 114 | 7 |  | 352 | 8 | 7 | Unit Ventilator
214 | Classroom | 210 | 14 |  | 957 | 21 | 14 | Unit Ventilator
215 | Classroom | 261 | 17 |  | 754 | 17 | 17 | Unit Ventilator
216 | Classroom | 470 | 31 |  | 754 | 17 | 17 | Unit Ventilator
217 | Classroom | 666 | 44 |  | 957 | 21 | 21 | Unit Ventilator
218 | Classroom | 260 | 17 |  | 330 | 7 | 7 | Unit Ventilator
219 | Classroom | 0 | 0 |  | 1100 | 25 | 0 | Unit Ventilator
221 | Classroom | 449 | 29 |  | 884 | 20 | 20 | Unit Ventilator
223 | Classroom | 403 | 26 |  | 340 | 7 | 7 | AHU
225 | Classroom | 266 | 17 |  | 858 | 19 | 17 | Unit Ventilator
228A | Classroom | 60 | 4 |  | 252 | 5 | 4 | AHU
229 | Classroom | 47 | 3 |  | 336 | 7 | 3 | AHU
- | Auditorium | 773 | 51 |  | 2478 | 56 | 51 | AHU
- | Faculty Lounge | 125 | 8 |  | 361 | 8 | 8 | Unit Ventilator
- | Library | 1025 | 68 |  | 1674 | 38 | 38 | AHU
- | Office | 110 | 7 |  | 70 | 1 | 1 | AHU
- | Main Office | 87 | 5 |  | 496 | 11 | 5 | Unit Ventilator
- | Principals Office | 140 | 9 |  | 294 | 6 | 6 | Unit Ventilator

## Moore
Sheet Last Modified: | 2021-04-26
School: | J. Hampton Moore Elementary School
| Mobile Classrooms | Main Building | Little School House
Vendor: | Devine | Main Retest | LSH Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Moore Main
- | Auditorium | 224 | 14 |  | 3015 | 68 | 14 | AHU
- | Gym | 145 | 9 | Yes | 4500 | 102 | 102 | AHU
101 | Classroom | 518 | 34 |  | 1055 | 23 | 23 | Univent
102 | Classroom | 504 | 33 |  | 1055 | 23 | 23 | Univent
103 | Classroom | 364 | 24 |  | 624 | 14 | 14 | Univent
104 | Classroom | 116 | 7 | Yes | 458 | 10 | 10 | Univent
105 | Classroom | 408 | 27 |  | 1082 | 24 | 24 | Univent
106 | Classroom | 237 | 15 | Yes | 951 | 21 | 21 | Univent
107 | Classroom | 535 | 35 |  | 951 | 21 | 21 | Univent
108 | Classroom | 503 | 33 |  | 951 | 21 | 21 | Univent
109 | Classroom | 220 | 14 | Yes | 951 | 21 | 21 | Univent
110 | Classroom | 113 | 7 | Yes | 951 | 21 | 21 | Univent
110A | Classroom | 237 | 15 |  | 951 | 21 | 15 | Univent
112 | Classroom | 325 | 21 |  | 951 | 21 | 21 | Univent
113 | Classroom | 472 | 31 |  | 951 | 21 | 21 | Univent
114 | Classroom | 487 | 32 |  | 951 | 21 | 21 | Univent
115 | Classroom | 236 | 15 |  | 383 | 8 | 8 | Univent
201 | Classroom | 480 | 32 |  | 976 | 22 | 22 | Univent
202 | Classroom | 319 | 21 |  | 976 | 22 | 21 | Univent
203 | Classroom | 251 | 16 | Yes | 951 | 21 | 21 | Univent
203B | Classroom |  | 0 | Yes | 624 | 14 | 14
204 | Classroom | 291 | 19 | Yes | 951 | 21 | 21 | Univent
205A | Classroom | 261 | 17 | Yes | 452 | 10 | 10 | Univent
205B | Classroom | 130 | 8 | Yes | 642 | 14 | 14 | Univent
206 | Classroom | 326 | 21 |  | 970 | 22 | 21 | Univent
207 | Classroom | 424 | 28 |  | 951 | 21 | 21 | Univent
207A | Classroom |  | 0 | Yes | 239 | 5 | 5 | N/A
208 | Classroom | 527 | 35 |  | 951 | 21 | 21 | Univent
209 | Classroom | 399 | 26 |  | 951 | 21 | 21 | Univent
210A | Classroom | 108 | 7 | Yes | 458 | 10 | 10 | Univent
210B | Classroom | 335 | 22 | Yes | 458 | 10 | 10 | Univent
211 | Classroom | 433 | 28 |  | 951 | 21 | 21 | Univent
212 | Classroom | 244 | 16 | Yes | 951 | 21 | 21 | Univent
213 | Classroom | 0 | 0 | Yes | 951 | 21 | 21 | Univent
214 | Classroom | 64 | 4 | Yes | 820 | 18 | 18 | Univent
215 | Classroom | 454 | 30 |  | 951 | 21 | 21 | Univent
216 | Classroom | 444 | 29 |  | 951 | 21 | 21 | Univent
217 | Classroom | 520 | 34 |  | 951 | 21 | 21 | Univent
218 | Classroom | 347 | 23 |  | 951 | 21 | 21 | Univent
219 | Counselor Office |  | 0 | Yes | 170 | 3 | 3
- | Principals Office | 0 | 0 | Yes | 400 | 9 | 9
Assistant Principal | Office |  | 0 | Yes | 172 | 3 | 3
Teachers Lounge | Room |  | 0 | Yes | 170 | 3 | 3
2nd Floor Copy Room | Room |  | 0 | Yes | 172 | 3 | 3
- | Nurse Office | 0 | 0 | Yes | 800 | 18 | 18 | Univent
Moore LSH
- | Office | 224 | 14 |  | 200 | 4 | 4 | FCU
- | Kitchen | 145 | 9 |  | 624 | 14 | 9 | FCU
- | Faculty Lounge | 130 | 8 | Yes | 200 | 4 | 4 | FCU
P101 | Classroom |  | 0 | Yes | 120 | 2 | 2
P102 | Classroom |  | 0 | Yes | 120 | 2 | 2
P110 | Classroom | 361 | 24 |  | 950 | 21 | 21 | Univent
P111 | Classroom | 593 | 39 |  | 950 | 21 | 21 | Univent
P112 | Classroom | 379 | 25 |  | 950 | 21 | 21 | Univent
P113 | Classroom | 463 | 30 |  | 950 | 21 | 21 | Univent
P114 | Classroom | 747 | 49 |  | 950 | 21 | 21 | Univent
P114 | Hallway | 130 | 8 |  | 780 | 17 | 8 | FCU
P115 | Classroom | 361 | 24 |  | 950 | 21 | 21 | Univent
P116 | Classroom | 491 | 32 |  | 950 | 21 | 21 | Univent
P117 | Classroom | 430 | 28 |  | 950 | 21 | 21 | Univent
P124 | Classroom | 999 | 66 |  | 950 | 21 | 21 | Univent
P124 | Hallway | 80 | 5 |  | 1122 | 25 | 5 | FCU
P125 | Classroom | 476 | 31 |  | 950 | 21 | 21 | Univent
P126 | Classroom | 304 | 20 |  | 950 | 21 | 20 | Univent
P127 | Classroom | 1009 | 67 |  | 950 | 21 | 21 | Univent
Moore Modular
A-1 | Classroom | 568 | 37 |  | 781 | 17 | 17 | Univent
A-2 | Classroom | 453 | 30 |  | 781 | 17 | 17 | Univent
A-3 | Classroom | 441 | 29 |  | 781 | 17 | 17 | Univent
A-4 | Classroom | 360 | 24 |  | 781 | 17 | 17 | Univent
A-5 | Classroom | 214 | 14 | Yes | 781 | 17 | 17 | Univent
A-6 | Classroom | 125 | 8 | Yes | 781 | 17 | 17 | Univent
A-7 | Classroom | 465 | 31 |  | 781 | 17 | 17 | Univent
A-8 | Classroom | 629 | 41 |  | 781 | 17 | 17 | Univent

## Morris
Sheet Last Modified: | 2021-04-12
School: | Robert Morris Elementary School
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 192 | 12 | Yes | 1284.2 | 29 | 29 | Univent
101 | Classroom | 171 | 11 | Yes | 1410 | 32 | 32 | Univent
200 | Classroom | 185 | 12 | Yes | 858.35 | 19 | 19 | Univent
201 | Classroom | 72 | 4 | Yes | 602.69 | 13 | 13 | Univent
202 | Classroom | 218 | 14 |  | 848.83 | 19 | 14 | Univent
203 | Classroom | 200 | 13 | Yes | 820.72 | 18 | 18 | Univent
204 | Classroom | 163 | 10 | Yes | 845.87 | 19 | 19 | Univent
206 | Classroom | 85 | 5 |  | 846.81 | 19 | 5 | Univent
208 | Classroom | 152 | 10 |  | 829.54 | 18 | 10 | Univent
210 | Classroom | 0 | 0 |  | 837.2 | 19 | 0 | Univent
212 | Lunch Room | 137 | 9 |  | 875.6 | 19 | 9 | Univent
213 | Classroom | 74 | 4 |  | 874.92 | 19 | 4 | Univent
214 | Classroom | 125 | 8 |  | 847.77 | 19 | 8 | Univent
215 | Classroom | 286 | 19 |  | 839.71 | 19 | 19 | Univent
216 | Classroom | 94 | 6 |  | 847.89 | 19 | 6 | Univent
217 | Classroom | 114 | 7 | Yes | 463.38 | 10 | 10 | Univent
218 | Classroom | 283 | 18 |  | 1037.4 | 23 | 18 | Univent
219 | Kitchen | 261 | 17 |  | 1203.6 | 27 | 17 | Univent
300 | Classroom | 86 | 5 | Yes | 856.08 | 19 | 19 | Univent
301 | Classroom | 273 | 18 |  | 601.22 | 13 | 13 | Univent
302 | Classroom | 225 | 15 |  | 847.77 | 19 | 15 | Univent
303 | Classroom | 266 | 17 |  | 818.22 | 18 | 17 | Univent
304 | Classroom | 86 | 5 |  | 842.65 | 19 | 5 | Univent
306 | Classroom | 169 | 11 |  | 849.23 | 19 | 11 | Univent
308 | Classroom | 129 | 8 | Yes | 828.1 | 18 | 18 | Univent
310/312/314 | Library | 734 | 48 |  | 2102.2 | 47 | 47 | Univent
313 | Classroom | 264 | 17 |  | 975.08 | 22 | 17 | Univent
315 | Classroom | 217 | 14 |  | 1220.1 | 27 | 14 | Univent
316 | Classroom | 139 | 9 |  | 845.19 | 19 | 9 | Univent
317 | Classroom | 152 | 10 | Yes | 462.24 | 10 | 10 | Univent
319 | Art Room | 0 | 0 | Yes | 1042.4 | 23 | 23 | Univent
400 | Classroom | 58 | 3 |  | 857.02 | 19 | 3 | Univent
401 | Classroom | 121 | 8 | Yes | 601.71 | 13 | 13 | Univent
402 | Classroom | 169 | 11 |  | 845.61 | 19 | 11 | Univent
403 | Classroom | 498 | 33 |  | 816.82 | 18 | 18 | Univent
404 | Classroom | 92 | 6 |  | 848.28 | 19 | 6 | Univent
406 | Classroom | 60 | 4 |  | 844.56 | 19 | 4 | Univent
408 | Classroom | 55 | 3 | Yes | 829.09 | 18 | 18 | Univent
410 | Classroom | 0 | 0 |  | 849.23 | 19 | 0 | Univent
412 | Lunch Room | 106 | 7 |  | 858 | 19 | 7 | Univent
413 | Classroom | 313 | 20 |  | 870.72 | 19 | 19 | Univent
414 | Classroom | 291 | 19 |  | 847.18 | 19 | 19 | Univent
415 | Classroom | 147 | 9 | Yes | 836.29 | 19 | 19 | Univent
416 | Classroom | 106 | 7 | Yes | 847.31 | 19 | 19 | Univent
417 | Faculty | 158 | 10 |  | 446.16 | 10 | 10 | Univent
418 | Classroom | 34 | 2 | Yes | 1044.2 | 23 | 23 | Univent
419 | Music Room | 511 | 34 |  | 1039.5 | 23 | 23 | Univent
- | Auditorium | 1066 | 71 |  | 5308.2 | 120 | 71 | Univent
- | Counselor's Office | 70 | 4 |  | 473.95 | 10 | 4 | Univent
- | Gymnasium | 1100 | 73 |  | 3688 | 83 | 73 | Univent
- | Nurse's Office |  | 0 | Yes | 261.04 | 5 | 5 | N/A
- | Principal's Office |  | 0 | Yes | 294.25 | 6 | 6 | N/A
- | Main Office | 387 | 25 |  | 1372.7 | 31 | 25 | Univent

## Morrison
Sheet Last Modified: | 2021-03-18
School: | Andrew Morrison Elementary School
Vendor: | EMCOR Fluidics | EMCOR Retest 1-15-21 | Retest 2-22-21
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
5 | Music Rm |  | 0 | Yes | 813 | 18 | 18 | House Fan
8 | Art Rm |  | 0 | Yes | 886 | 20 | 20 | House Fan
101A | Nurse |  | 0 | Yes | 376 | 8 | 8 | House Fan
101B | Counselor |  | 0 |  | 341 | 7 | 0 | House Fan
102 | Classroom |  | 0 | Yes | 701 | 15 | 15 | House Fan
103 | Classroom |  | 0 | Yes | 734 | 16 | 16 | House Fan
104 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
106 | Lounge |  | 0 | Yes | 526 | 11 | 11 | House Fan
107 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
108 | Classroom |  | 0 | Yes | 566 | 12 | 12 | House Fan
109 | Classroom | 376 | 25 |  | 765 | 17 | 17 | Univent
110 | Classroom | 427 | 28 |  | 792 | 18 | 18 | Univent
111 | Classroom | 408 | 27 |  | 781 | 17 | 17 | Univent
112 | Classroom | 469 | 31 |  | 792 | 18 | 18 | Univent
113 | Classroom | 380 | 25 |  | 767 | 17 | 17 | Univent
114 | Office / Classroom | 271 | 18 |  | 351 | 7 | 7 | Univent
115 | Gym |  | 0 |  | 4693 | 106 | 0 | House Fan
200 | Office |  | 0 |  | 168 | 3 | 0 | House Fan
201 | Classroom |  | 0 |  | 726 | 16 | 0 | House Fan
202 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan
203 | Classroom |  | 0 |  | 731 | 16 | 0 | House Fan
204 | Classroom |  | 0 |  | 718 | 16 | 0 | House Fan
204A | Office |  | 0 |  | 322 | 7 | 0 | House Fan
204B | Office |  | 0 | Yes | 150 | 3 | 3 | N/A
204C | Office |  | 0 |  | 84 | 1 | 0 | N/A
205 | Classroom |  | 0 |  | 698 | 15 | 0 | House Fan
206 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan
207 | Classroom |  | 0 |  | 698 | 15 | 0 | House Fan
208 | Classroom |  | 0 |  | 643 | 14 | 0 | House Fan
212 | Classroom | 48 | 3 |  | 398 | 9 | 3 | Univent
213 | Classroom | 194 | 12 |  | 742 | 16 | 12 | Univent
214 | Classroom | 197 | 13 |  | 864 | 19 | 13 | Univent
215 | Office | 0 | 0 |  | 100 | 2 | 0 | Univent
216 | Classroom | 411 | 27 |  | 762 | 17 | 17 | Univent
217 | Classroom | 365 | 24 |  | 734 | 16 | 16 | Univent
218 | Office / Classroom | 269 | 17 |  | 356 | 8 | 8 | Univent
300 | Classroom |  | 0 |  | 644 | 14 | 0 | House Fan
301a | Office |  | 0 |  | 163 | 3 | 0 | House Fan
302 | Classroom |  | 0 |  | 688 | 15 | 0 | House Fan
303 | Classroom |  | 0 |  | 736 | 16 | 0 | House Fan
304 | Classroom |  | 0 |  | 666 | 15 | 0 | House Fan
306 | Classroom |  | 0 |  | 1085 | 24 | 0 | House Fan
306A | Library |  | 0 |  | 1166 | 26 | 0 | House Fan
307 | Classroom |  | 0 |  | 687 | 15 | 0 | House Fan
308 | Classroom |  | 0 |  | 798 | 18 | 0 | House Fan
312 | Classroom | 224 | 14 |  | 1070 | 24 | 14 | Rooftop Unit
313 | Classroom | 0 | 0 |  | 944 | 21 | 0 | Rooftop Unit
314 | Classroom | 332 | 22 |  | 1117 | 25 | 22 | Rooftop Unit
314 | Office | 0 | 0 |  | 372 | 8 | 0 | Univent
314A | Office |  | 0 |  | 372 | 8 | 0 | House Fan
315A | Teacher's Lounge | 0 | 0 |  | 294 | 6 | 0 | Univent
316 | Office / Classroom | 130 | 8 |  | 356 | 8 | 8 | Rooftop Unit
- | Auditorium |  | 0 |  | 3657 | 83 | 0 | House Fan
- | Gym | 857 | 57 |  | 4693 | 106 | 57 | Univent
- | Lunch Rm |  | 0 |  | 4331 | 98 | 0 | House Fan
- | Main Office |  | 0 | Yes | 395 | 8 | 8 | House Fan
- | Principals Office |  | 0 | Yes | 269 | 6 | 6 | House Fan

## Morton
Sheet Last Modified: | 2021-04-23
School: | Thomas G. Morton Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 0 | 0 | Yes | 988 | 22 | 22 | Univent
101 | Classroom | 0 | 0 | Yes | 875 | 19 | 19 | Univent
102 | Classroom | 374 | 24 |  | 792 | 18 | 18 | Air Coil Unit
104B | Storage | 77 | 5 |  | 84 | 1 | 1 | Univent
108A | Nurse Office | 125 | 8 |  | 90 | 2 | 2 | Univent
108B | Audio | 40 | 2 |  | 224 | 5 | 2 | Univent
108C | Examination | 36 | 2 |  | 234 | 5 | 2 | Univent
110 | Classroom | 0 | 0 |  | 513 | 11 | 0 | Univent
111 | Classroom | 309 | 20 | Yes | 252 | 5 | 5 | Univent
200 | Classroom | 0 | 0 | Yes | 1071 | 24 | 24 | Univent
201 | Classroom | 0 | 0 | Yes | 754 | 17 | 17 | Univent
202 | Classroom | 432 | 28 | Yes | 754 | 17 | 17 | Univent
203 | Classroom | 475 | 31 |  | 8112 | 184 | 31 | Univent
204 | Classroom | 399 | 26 |  | 438 | 9 | 9 | Univent
205 | Classroom | 0 | 0 | Yes | 1015 | 23 | 23 | Univent
206 | Classroom | 0 | 0 | Yes | 1305 | 29 | 29 | Univent
207 | Classroom | 0 | 0 | Yes | 1305 | 29 | 29 | Univent
208 | Classroom | 329 | 21 | Yes | 1015 | 23 | 23 | Univent
209 | Classroom | 280 | 18 | Yes | 408 | 9 | 9 | Univent
210 | Classroom | 0 | 0 | Yes | 725 | 16 | 16 | Univent
211 | Classroom | 0 | 0 | Yes | 841 | 19 | 19 | Univent
212 | Classroom | 0 | 0 | Yes | 264 | 6 | 6 | Univent
213 | Classroom | 437 | 29 |  | 725 | 16 | 16 | Univent
214A | Classroom | 94 | 6 |  | 190 | 4 | 4 | Univent
214B | Classroom | 162 | 10 |  | 624 | 14 | 10 | Univent
300 | Classroom | 309 | 20 |  | 780 | 17 | 17 | Univent
301 | Classroom | 0 | 0 |  | 725 | 16 | 0 | Univent
302 | Classroom | 685 | 45 |  | 240 | 5 | 5 | Univent
303 | Classroom | 486 | 32 |  | 754 | 17 | 17 | Univent
304 | Classroom | 448 | 29 | Yes | 725 | 16 | 16 | Univent
305 | Classroom | 291 | 19 |  | 312 | 7 | 7 | Univent
306 | Classroom | 483 | 32 | Yes | 754 | 17 | 17 | Univent
307 | Classroom | 415 | 27 | Yes | 756 | 17 | 17 | Univent
308 | Library | 1124 | 74 |  | 2975 | 67 | 67 | Univent
308 | Library Office | 0 | 0 |  | 462 | 10 | 0 | Univent
309 | Classroom | 283 | 18 | Yes | 806 | 18 | 18 | Univent
310 | Classroom | 628 | 41 |  | 700 | 15 | 15 | Univent
311 | Classroom | 294 | 19 |  | 754 | 17 | 17 | Univent
312 | Classroom | 349 | 23 |  | 754 | 17 | 17 | Univent
313 | Classroom | 547 | 36 |  | 486 | 11 | 11 | Univent
315 | Classroom | 544 | 36 |  | 754 | 17 | 17 | Univent
316 | Classroom | 324 | 21 |  | 754 | 17 | 17 | Univent
317 | Classroom | 431 | 28 |  | 870 | 19 | 19 | Univent
318 | Classroom | 305 | 20 |  | 312 | 7 | 7 | Univent
319 | Classroom | 0 | 0 | Yes | 650 | 14 | 14 | Univent
320 | Classroom | 431 | 28 |  | 728 | 16 | 16 | Univent
- | Auditorium | 5700 | 380 |  | 2646 | 60 | 60 | Air Coil Unit
- | Cafeteria | 2196 | 146 | Yes | 2726 | 61 | 61 | Air Coil Unit
- | Conference | 83 | 5 |  | 171 | 3 | 3 | Univent
- | Counselors Office A | 87 | 5 |  | 99 | 2 | 2 | Univent
- | Counselors Office B | 91 | 6 |  | 128 | 2 | 2 | Univent
- | Counselors Office C | 148 | 9 |  | 100 | 2 | 2 | Univent
- | Gym | 1927 | 128 |  | 4640 | 105 | 105 | Air Coil Unit
- | Lounge | 311 | 20 |  | 351 | 7 | 7 | Univent
- | Main Office | 285 | 19 |  | 380 | 8 | 8 | Univent
- | Copy Room | 53 | 3 |  | 60 | 1 | 1 | Univent
- | Nurse | 83 | 5 |  | 123 | 2 | 2 | Univent
- | Principal Office | 159 | 10 |  | 228 | 5 | 5 | Univent
- | Vice Principal Office | 54 | 3 |  | 99 | 2 | 2 | Univent

## Motivation @ Turner
Sheet Last Modified: | 2021-04-29
School: | Motivation High School KIPP Turner West Middle School
Vendor: | Capital
Vendor: | Devine |  | Devine Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
A-PreK Corridor | Corridor | 314 | 20 |  | 600 | 13 | 13 | Univent
A-PreK North Entrance-A | Corridor | 490 | 32 |  | 243 | 5 | 5 | Univent
A-PreK North Entrance-B | Corridor | 548 | 36 |  | 480 | 10 | 10 | Univent
A-PreK South Corridor | Corridor | 324 | 21 |  | 550 | 12 | 12 | Univent
A-Wing Head Start Mech. Rm | Head Start PreK A169 & A170 | 349 | 23 |  | 1440 | 32 | 23 | Air Handling Unit
A-Wing-Café Mech. Rm | 2nd & 3rd Flr. Staff Seminar Rms | 1734 | 115 |  |  | 0 | 0 | Air Handling Unit
A-Wing-Café Mech. Rm | 3rd Flr |  | 0 |  | 50 | 1 | 0 | Air Handling Unit
A-Wing-Café Mech. Rm | 2nd Flr |  | 0 |  | 50 | 1 | 0 | Air Handling Unit
A-Wing-Café Mech. Rm | Ground Flr. Administration | 351 | 23 |  |  | 0 | 0 | Air Handling Unit
A130 | Gym | 410 | 27 |  | 2552 | 58 | 27 | Heating Ventilation Unit
A108 Locker Rm | A108 | 0 | 0 |  |  | 0 | 0 | Heating Ventilation Unit
A152 Locker Rm | A152 | 1340 | 89 |  | 690 | 15 | 15 | Heating Ventilation Unit
A162 Storage | A154 Corrective Gym | 306 | 20 |  | 5192 | 118 | 20 | Heating Ventilation Unit
A165 | Storage | 0 | 0 |  | 5192 | 118 | 0 | Heating Ventilation Unit
B-157 | B-155 Fitness Rm | 1593 | 106 |  | 1150 | 26 | 26 | Univent
MER Rm B146 | B-Wing | 555 | 37 |  | 1012 | 23 | 23 | Air Handling Unit
B-Wing B137 | B-139 A, B, C, D | 2003 | 133 |  | 4134 | 93 | 93 | Air Handling Unit
B101 Cafeteria | B-Wing Roof | 320 | 21 |  | 9405 | 213 | 21 | Air Handling Unit
House Coord North 3rd & 2nd Flr | B-Wing Roof | 67 | 4 |  |  | 0 | 0 | Air Handling Unit
B318 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit
B218 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit
House Coord South 3rd & 2nd Flr | B-Wing Roof | 126 | 8 |  |  | 0 | 0 | Air Handling Unit
B306 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit
B206 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit
B325 IMC Library | B-Wing Roof | 7 | 0 |  | 851 | 19 | 0 | Air Handling Unit
139A | Classroom |  | 0 |  | 880 | 20 | 0
139B | Classroom |  | 0 |  | 987 | 22 | 0
139C | Classroom |  | 0 |  | 884 | 20 | 0
139D | Classroom |  | 0 |  | 1035 | 23 | 0
151 | Classroom |  | 0 | Yes | 1824 | 41 | 41
152 | Classroom |  | 0 | Yes | 1170 | 26 | 26
B196 | Classroom | 376 | 25 |  | 567 | 12 | 12 | Univent
B197 | Classroom | 755 | 50 |  | 962 | 21 | 21 | Univent
B198 | Classroom | 739 | 49 |  | 792 | 18 | 18 | Univent
B200 | Classroom | 1468 | 97 |  | 1564 | 35 | 35 | Univent
B201 | Classroom | 673 | 44 |  | 850 | 19 | 19 | Univent
B202 | Classroom | 172 | 11 |  | 748 | 17 | 11 | Univent
B203 | Classroom | 673 | 44 |  | 748 | 17 | 17 | Univent
B204 | Classroom | 143 | 9 |  | 759 | 17 | 9 | Univent
B205 | Classroom | 555 | 37 |  | 720 | 16 | 16 | Univent
B207 | Classroom | 629 | 41 |  | 748 | 17 | 17 | Univent
B208 | Classroom | 640 | 42 |  | 759 | 17 | 17 | Univent
B209 | Classroom | 108 | 7 |  | 816 | 18 | 7 | Univent
B210 | Classroom | 630 | 42 |  | 720 | 16 | 16 | Univent
B211 | Classroom | 350 | 23 |  | 720 | 16 | 16 | Univent
B212 | Classroom | 538 | 35 |  | 1326 | 30 | 30 | Univent
B213 | Classroom | 244 | 16 |  | 759 | 17 | 16 | Univent
B214 | Classroom | 0 | 0 |  | 759 | 17 | 0 | Univent
B215 | Classroom | 341 | 22 |  | 748 | 17 | 17 | Univent
B216 | Classroom | 339 | 22 |  | 748 | 17 | 17 | Univent
B217 | Classroom | 273 | 18 |  | 624 | 14 | 14 | Univent
B219 | Classroom | 378 | 25 |  | 748 | 17 | 17 | Univent
B220 | Classroom | 242 | 16 |  | 759 | 17 | 16 | Univent
B221 | Classroom | 456 | 30 |  | 816 | 18 | 18 | Univent
B222 | Classroom | 633 | 42 |  | 598 | 13 | 13 | Univent
B223 | Classroom | 642 | 42 |  | 690 | 15 | 15 | Univent
B301 | Classroom | 200 | 13 |  | 850 | 19 | 13 | Univent
B302 | Classroom | 129 | 8 |  | 748 | 17 | 8 | Univent
B304 | Classroom | 630 | 42 |  | 1564 | 35 | 35 | Univent
B305 | Classroom | 150 | 10 |  | 720 | 16 | 10 | Univent
306 | Classroom |  | 0 | Yes | 900 | 20 | 20
B307 | Classroom | 193 | 12 |  | 748 | 17 | 12 | Univent
B308 | Classroom | 110 | 7 |  | 759 | 17 | 7 | Univent
B309 | Classroom | 186 | 12 |  | 816 | 18 | 12 | Univent
B310 | Classroom | 196 | 13 |  | 720 | 16 | 13 | Univent
B311 | Classroom | 222 | 14 |  | 720 | 16 | 14 | Univent
B312 | Classroom | 691 | 46 |  | 1326 | 30 | 30 | Univent
B313 | Classroom | 264 | 17 |  | 759 | 17 | 17 | Univent
B314 | Classroom | 436 | 29 |  | 759 | 17 | 17 | Univent
B315 | Classroom | 198 | 13 |  | 748 | 17 | 13 | Univent
B316 | Classroom | 160 | 10 |  | 748 | 17 | 10 | Univent
B317 | Classroom | 198 | 13 |  | 624 | 14 | 13 | Univent
318 | Classroom |  | 0 | Yes | 900 | 20 | 20
B319 | Classroom | 304 | 20 |  | 748 | 17 | 17 | Univent
B320 | Classroom | 144 | 9 |  | 759 | 17 | 9 | Univent
B321 | Classroom | 290 | 19 |  | 816 | 18 | 18 | Univent
B322 | Classroom | 213 | 14 |  | 598 | 13 | 13 | Univent
B323 | Classroom | 156 | 10 |  | 690 | 15 | 10 | Univent
B324 | Classroom | 577 | 38 |  | 1435 | 32 | 32 | Univent
Main Office | Main Office |  | 0 | Yes | 950 | 21 | 21
Teachers Lounge | Lounge |  | 0 | Yes | 728 | 16 | 16
Nurse | Office |  | 0 | Yes | 910 | 20 | 20
C-Wing | Auditorium Music Rm | 346 | 23 | Yes | 1476 | 33 | 33 | Air Handling Unit
C-Wing | Auditorium Comm. Rm. | 1811 | 120 |  | 7392 | 168 | 120 | Air Handling Unit
C-Wing | Auditorium/ Auditorium Stage | 3862 | 257 |  | 1890 | 42 | 42 | Air Handling Unit
Head Start Mech Rm. | B110 Learning Lab & B104 Student Store | 457 | 30 |  | 81 | 1 | 1 | Air Handling Unit

## Munoz-Marin
Sheet Last Modified: | 2021-05-03
School: | Luis Munoz – Marin Elementary School
Vendor: | Chadwick
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100B | CORRIDOR | 149 | 9 |  | 618 | 14 | 9 | Air Handling Unit
100E | CORRIDOR | 115 | 7 |  | 1780 | 40 | 7 | Air Handling Unit
100F | CORRIDOR | 250 | 16 |  | 1210 | 27 | 16 | Air Handling Unit
100G | CORRIDOR | 142 | 9 |  | 1404 | 31 | 9 | Air Handling Unit
100H | CORRIDOR |  | 0 |  | 1780 | 40 | 0 | Air Handling Unit
102 | Classroom | 193 | 12 |  | 792 | 18 | 12 | Air Handling Unit
104 | Classroom | 225 | 15 | Yes | 805 | 18 | 18 | Air Handling Unit
105 | Classroom | 195 | 13 | Yes | 713 | 16 | 16 | Air Handling Unit
106 | Classroom | 213 | 14 | Yes | 713 | 16 | 16 | Air Handling Unit
107 | Classroom | 170 | 11 | Yes | 682 | 15 | 15 | Air Handling Unit
108 | Classroom | 202 | 13 | Yes | 682 | 15 | 15 | Air Handling Unit
109 | Classroom | 227 | 15 |  | 682 | 15 | 15 | Air Handling Unit
110 | Classroom | 212 | 14 | Yes | 682 | 15 | 15 | Air Handling Unit
111 | Classroom | 469 | 31 |  | 700 | 15 | 15 | Air Handling Unit
115 | LOBBY | 648 | 43 |  | 1368 | 31 | 31 | Air Handling Unit
116 | - | 215 | 14 |  | 609 | 13 | 13 | Air Handling Unit
118 | - | 177 | 11 | Yes | 672 | 15 | 15 | Air Handling Unit
120 | - | 188 | 12 | Yes | 768 | 17 | 17 | Air Handling Unit
121 | HEALTH | 87 | 5 |  | 816 | 18 | 5 | Air Handling Unit
124A | OFFICE | 19 | 1 |  | 120 | 2 | 1 | Air Handling Unit
125 | SPE. | 17 | 1 | Yes | 336 | 7 | 7 | Air Handling Unit
125 | OCC | 51 | 3 |  | 272 | 6 | 3 | Air Handling Unit
126 | FAM MGMT | 272 | 18 |  | 1215 | 27 | 18 | Air Handling Unit
127 | CLASSROOM | 56 | 3 |  | 670 | 15 | 3 | Air Handling Unit
127B |  | 15 |  |  | 39 |  | 0 | Air Handling Unit
127C |  | 18 |  |  | 149 |  | 0 | Air Handling Unit
160 | Classroom | 27 | 1 |  | 39 | 0 | 0 | Air Handling Unit
161 | Classroom | 33 | 2 |  | 375 | 8 | 2 | Air Handling Unit
162 | Classroom | 55 | 3 |  | 114 | 2 | 2 | Air Handling Unit
163 | Classroom | 62 | 4 |  | 114 | 2 | 2 | Air Handling Unit
164 | Classroom | 33 | 2 |  | 117 | 2 | 2 | Air Handling Unit
166 | Classroom | 23 | 1 |  | 102 | 2 | 1 | Air Handling Unit
168 | Classroom | 33 | 2 |  | 109 | 2 | 2 | Air Handling Unit
169 | Classroom | 23 | 1 |  | 81 | 1 | 1 | Air Handling Unit
170 | Classroom | 35 | 2 |  | 134 | 3 | 2 | Air Handling Unit
171 | OFFICE | 223 | 14 |  | 148 | 3 | 3 | Air Handling Unit
172 | - | 58 | 3 |  | 148 | 3 | 3 | Air Handling Unit
173 | PRINCIPAL | 87 | 5 |  | 304 | 6 | 5 | Air Handling Unit
176 | - | 114 | 7 |  | 148 | 3 | 3 | Air Handling Unit
177 | - | 69 | 4 |  | 134 | 3 | 3 | Air Handling Unit
180 | CONFR | 54 | 3 |  | 244 | 5 | 3 | Air Handling Unit
181 | ASS PRINC | 100 | 6 |  | 188 | 4 | 4 | Air Handling Unit
181A | OFFICE | 42 | 2 |  | 125 | 2 | 2 | Air Handling Unit
182 | - | 42 | 2 |  | 131 | 2 | 2 | Air Handling Unit
183 | - | 42 | 2 |  | 97 | 2 | 2 | Air Handling Unit
200A | CORRIDOR | 160 | 10 |  | 1780 | 40 | 10 | Air Handling Unit
200C | CORRIDOR | 148 | 9 |  | 1780 | 40 | 9 | Air Handling Unit
200D | CORRIDOR | 240 | 16 |  | 1359 | 30 | 16 | Air Handling Unit
200E | CORRIDOR | 100 | 6 |  | 1404 | 31 | 6 | Air Handling Unit
200F | - | 156 | 10 |  | 100 | 2 | 2 | Air Handling Unit
201 | Classroom | 204 | 13 | Yes | 714 | 16 | 16 | Univent and Air Handling Unit
202 | Classroom | 94 | 6 | Yes | 713 | 16 | 16 | Univent and Air Handling Unit
203 | Classroom | 68 | 4 | Yes | 704 | 16 | 16 | Univent and Air Handling Unit
204 | Classroom | 418 | 27 |  | 764 | 17 | 17 | Univent and Air Handling Unit
205 | Classroom | 152 | 10 | Yes | 764 | 17 | 17 | Univent and Air Handling Unit
206 | Classroom | 241 | 16 | Yes | 764 | 17 | 17 | Univent and Air Handling Unit
207 | Classroom | 148 | 9 |  | 648 | 14 | 9 | Univent and Air Handling Unit
208 | IMC | 338 | 22 |  | 1757 | 39 | 22 | Air Handling Unit
209 | Classroom | 272 | 18 |  | 648 | 14 | 14 | Univent and Air Handling Unit
213 | Classroom | 155 | 10 |  | 764 | 17 | 10 | Univent and Air Handling Unit
214 | Classroom | 140 | 9 |  | 118 | 2 | 2 | Univent
214 | IMC | 311 | 20 |  | 1405 | 31 | 20 | Air Handling Unit
214A | WORK | 32 | 2 |  | 118 | 2 | 2 | Air Handling Unit
215 | Classroom | 232 | 15 | Yes | 840 | 19 | 19 | Univent and Air Handling Unit
216A | OFFICE | 64 | 4 |  | 165 | 3 | 3 | Air Handling Unit
217 | Classroom | 200 | 13 |  | 782 | 17 | 13 | Univent and Air Handling Unit
218 | Classroom | 120 | 8 |  | 374 | 8 | 8 | Univent
218B | STR. | 65 | 4 | Yes | 2255 | 51 | 51 | Air Handling Unit
218S | Classroom | 71 | 4 |  | 241 | 5 | 4 | Air Handling Unit
219 | Classroom | 153 | 10 | Yes | 7825 | 177 | 177 | Univent and Air Handling Unit
220 | Classroom | 117 | 7 | Yes | 648 | 14 | 14 | Univent and Air Handling Unit
221 | Classroom | 253 | 16 | Yes | 764 | 17 | 17 | Univent and Air Handling Unit
222 | OFFICE | 50 | 3 |  | 1105 | 25 | 3 | Air Handling Unit
223 | Classroom | 188 | 12 | Yes | 690 | 15 | 15 | Univent and Air Handling Unit
225 | Classroom | 73 | 4 | Yes | 870 | 19 | 19 | Univent
225 | COMP. | 124 | 8 |  | 96 | 2 | 2 | Air Handling Unit
226 | TECH. | 94 | 6 | Yes | 906 | 20 | 20 | Air Handling Unit
226 (right) | Classroom | 104 | 6 |  | 343 | 7 | 6 | Univent
226(left) | Classroom | 191 | 12 |  | 104 | 2 | 2 | Univent
226C | SHOP | 91 | 6 |  | 104 | 2 | 2 | Air Handling Unit
227 | Classroom | 150 | 10 |  | 660 | 15 | 10 | Univent and Air Handling Unit
300b | Corridor | 191 | 12 |  | 1404 | 31 | 12 | Air Handling Unit
300d | Corridor | 225 | 15 |  | 1359 | 30 | 15 | Air Handling Unit
301 | Classroom | 224 | 14 | Yes | 714 | 16 | 16 | Univent and Air Handling Unit
302 | Classroom | 229 | 15 | Yes | 757 | 17 | 17 | Univent and Air Handling Unit
303 | Classroom | 188 | 12 | Yes | 704 | 16 | 16 | Univent and Air Handling Unit
304 | Classroom | 194 | 12 | Yes | 757 | 17 | 17 | Univent and Air Handling Unit
305 | Classroom | 232 | 15 | Yes | 704 | 16 | 16 | Univent and Air Handling Unit
306 | Classroom | 243 | 16 | Yes | 757 | 17 | 17 | Univent and Air Handling Unit
307 | Classroom | 139 | 9 | Yes | 648 | 14 | 14 | Univent and Air Handling Unit
308 | Classroom | 86 | 5 |  | 734 | 16 | 5 | Univent and Air Handling Unit
309 | Classroom | 120 | 8 | Yes | 648 | 14 | 14 | Univent and Air Handling Unit
313 | Classroom | 156 | 10 | Yes | 1160 | 26 | 26 | Univent and Air Handling Unit
314 | Classroom | 119 | 7 | Yes | 1163 | 26 | 26 | Univent and Air Handling Unit
315 | Classroom | 107 | 7 | Yes | 713 | 16 | 16 | Univent and Air Handling Unit
316 | Classroom | 49 | 3 | Yes | 782 | 17 | 17 | Univent and Air Handling Unit
317 | Classroom | 99 | 6 | Yes | 782 | 17 | 17 | Univent and Air Handling Unit
318 | Classroom | 118 | 7 | Yes | 684 | 15 | 15 | Univent and Air Handling Unit
319 | Classroom | 358 | 23 |  | 782 | 17 | 17 | Univent and Air Handling Unit
320 | Classroom | 252 | 16 |  | 648 | 14 | 14 | Univent and Air Handling Unit
321 | Classroom | 454 | 30 |  | 648 | 14 | 14 | Univent and Air Handling Unit
322 | OFFICE | 0 | 0 |  | 100 | 2 | 0 | Air Handling Unit
- | AUDITORIUM | 2082 | 138 |  | 2938 | 66 | 66 | Air Handling Unit
- | CAFETERIA | 251 | 16 | Yes | 4402 | 100 | 100 | Air Handling Unit

## Nebinger
Sheet Last Modified: | 2021-04-29
School: | George W. Nebinger Elementary-Middle School
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 44 | 1 | 1 | House Fan
102 | Classroom |  | 0 | Yes | 880 | 20 | 20 | House Fan
103 | Classroom |  | 0 |  | 644 | 14 | 0 | House Fan
104 | Classroom |  | 0 |  | 644 | 14 | 0 | House Fan
105 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan
106 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan
107 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
201 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
202 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
203 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan
204 | Classroom |  | 0 | Yes | 899 | 20 | 20 | House Fan
204A | Classroom |  | 0 | Yes | 285 | 6 | 6 | House Fan
205 | Classroom |  | 0 | Yes | 330 | 7 | 7 | House Fan
206 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan
207 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
208 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
301 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
302 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
303 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan
304 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan
305 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan
305A | Classroom |  | 0 |  | 450 | 10 | 0 | House Fan
306 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan
307 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
308 | Classroom |  | 0 | Yes | 750 | 17 | 17 | House Fan
401 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
402 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
- | Gym |  | 0 |  | 2870 | 65 | 0 | House Fan
- | Main Office |  | 0 | Yes | 330 | 7 | 7 | House Fan
- | Principal's Office |  | 0 | Yes | 247 | 5 | 5 | House Fan
- | Health Room |  | 0 | Yes | 99 | 2 | 2 | House Fan

## Northeast HS
Sheet Last Modified: | 2021-03-18
School: | Northeast High School
Vendor: | Capital Programs | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Devine Brothers Data
1 | Classroom | 591 | 39 |  | 705 | 16 | 16 | Unit Ventilator
2 | Classroom | 520 | 34 |  | 619 | 14 | 14 | Unit Ventilator
3 | Classroom | 546 | 36 |  | 759 | 17 | 17 | Unit Ventilator
4 | Classroom | 545 | 36 |  | 749 | 17 | 17 | Unit Ventilator
5 | Classroom | 586 | 39 |  | 807 | 18 | 18 | Unit Ventilator
6 | Classroom | 564 | 37 |  | 782 | 17 | 17 | Unit Ventilator
7 | Classroom | 572 | 38 |  | 761 | 17 | 17 | Unit Ventilator
8 | Classroom | 539 | 35 |  | 775 | 17 | 17 | Unit Ventilator
9 | Classroom | 280 | 18 |  | 762 | 17 | 17 | Unit Ventilator
10 | Classroom | 271 | 18 |  | 749 | 17 | 17 | Unit Ventilator
11 | Classroom | 337 | 22 |  | 770 | 17 | 17 | Unit Ventilator
12 | Classroom | 633 | 42 |  | 1673 | 38 | 38 | Unit Ventilator
13 | Classroom | 541 | 36 |  | 1744 | 39 | 36 | Unit Ventilator
14 | Classroom | 334 | 22 |  | 1047 | 23 | 22 | Unit Ventilator
15 | Classroom | 507 | 33 |  | 1526 | 34 | 33 | Unit Ventilator
16A | Classroom | 238 | 15 |  | 731 | 16 | 15 | Unit Ventilator
16B | Classroom | 264 | 17 |  | 885 | 20 | 17 | Unit Ventilator
17A | Classroom | 380 | 25 |  | 661 | 15 | 15 | Unit Ventilator
17B | Classroom | 419 | 27 |  | 853 | 19 | 19 | Unit Ventilator
17C | Classroom | 259 | 17 |  | 1050 | 23 | 17 | Unit Ventilator
18B | Classroom | 0 | 0 |  | 962 | 21 | 0 | Unit Ventilator
18D | Classroom | 0 | 0 |  | 843 | 19 | 0 | Unit Ventilator
19B | Classroom | 374 | 24 |  | 862 | 19 | 19 | Unit Ventilator
21 | Offices | 0 | 0 |  | 1233 | 28 | 0 | Vertical Fan Coil Unit
22 | Office | 230 | 15 |  | 172 | 3 | 3 | Unit Ventilator
23 | Classroom | 260 | 17 |  | 741 | 16 | 16 | Unit Ventilator
24 | Classroom | 129 | 8 |  | 370 | 8 | 8 | Unit Ventilator
27 | Teacher's Lounge | 378 | 25 |  | 1205 | 27 | 25 | Unit Ventilator
31 | Classroom | 0 | 0 |  | 562 | 12 | 0 | Unit Ventilator
32 | Classrm. Lab | 2251 | 150 |  | 824 | 18 | 18 | Unit Ventilator
32A | Classrm. Lab | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator
34A | Office | 0 | 0 |  | 187 | 4 | 0 | Unit Ventilator
33 | Classroom | 499 | 33 |  | 571 | 12 | 12 | Unit Ventilator
35 | Office | 0 | 0 |  | 459 | 10 | 0 | Unit Ventilator
105 | Offices | 517 | 34 |  | 519 | 11 | 11 | Unit Ventilator
106 | Classroom | 748 | 49 |  | 1031 | 23 | 23 | Unit Ventilator
108 | Classroom | 739 | 49 |  | 948 | 21 | 21 | Unit Ventilator
109 | Classroom | 508 | 33 |  | 940 | 21 | 21 | Unit Ventilator
110 | Library | 610 | 40 |  | 386 | 8 | 8 | Unit Ventilator
111 | Classroom | 553 | 36 |  | 993 | 22 | 22 | Unit Ventilator
112 | Classroom | 602 | 40 |  | 980 | 22 | 22 | Unit Ventilator
113 | Classroom | 535 | 35 |  | 883 | 20 | 20 | Unit Ventilator
114 | Classroom | 363 | 24 |  | 717 | 16 | 16 | Unit Ventilator
115 | Room | 541 | 36 |  | 965 | 21 | 21 | Unit Ventilator
116 | Classroom | 623 | 41 |  | 745 | 16 | 16 | Unit Ventilator
117 | Classroom | 0 | 0 |  | 686 | 15 | 0 | Unit Ventilator
118 | Classroom | 543 | 36 |  | 842 | 19 | 19 | Unit Ventilator
119 | Classroom | 436 | 29 |  | 766 | 17 | 17 | Unit Ventilator
120 | Classroom | 370 | 24 |  | 741 | 16 | 16 | Unit Ventilator
121 | Classroom | 370 | 24 |  | 767 | 17 | 17 | Unit Ventilator
122 | Classroom | 495 | 33 |  | 1571 | 35 | 33 | Unit Ventilator
123 | Classroom | 403 | 26 |  | 738 | 16 | 16 | Unit Ventilator
124 | Classroom | 458 | 30 |  | 1410 | 32 | 30 | Unit Ventilator
125 | Classroom | 392 | 26 |  | 802 | 18 | 18 | Unit Ventilator
126 | Classroom | 326 | 21 |  | 698 | 15 | 15 | Unit Ventilator
127 | Classroom | 425 | 28 |  | 751 | 17 | 17 | Unit Ventilator
130 | Classroom | 481 | 32 |  | 1091 | 24 | 24 | Unit Ventilator
131 | Classroom | 409 | 27 |  | 713 | 16 | 16 | Unit Ventilator
132 | Classroom | 726 | 48 |  | 1038 | 23 | 23 | Unit Ventilator
133 | Classroom | 679 | 45 |  | 1627 | 36 | 36 | Unit Ventilator
133A | Office | 0 | 0 |  | 293 | 6 | 0 | Unit Ventilator
134 | Classroom | 181 | 12 |  | 402 | 9 | 9 | Unit Ventilator
136 | Classroom | 712 | 47 |  | 1206 | 27 | 27 | Unit Ventilator
137 | Classroom | 537 | 35 |  | 773 | 17 | 17 | Unit Ventilator
138 | Classroom | 453 | 30 |  | 1240 | 28 | 28 | Unit Ventilator
139 | Classroom | 601 | 40 |  | 798 | 18 | 18 | Unit Ventilator
140 | Classroom | 356 | 23 |  | 694 | 15 | 15 | Unit Ventilator
141 | Classroom | 510 | 34 |  | 773 | 17 | 17 | Unit Ventilator
143 | Classroom | 368 | 24 |  | 778 | 17 | 17 | Unit Ventilator
150 | Classroom | 118 | 7 |  | 845 | 19 | 7 | Unit Ventilator
152 | Classroom | 127 | 8 |  | 881 | 20 | 8 | Unit Ventilator
154 | Classroom | 0 | 0 |  | 874 | 19 | 0 | Unit Ventilator
156 | Classroom | 132 | 8 |  | 815 | 18 | 8 | Unit Ventilator
158 | Classroom | 160 | 10 |  | 849 | 19 | 10 | Unit Ventilator
160 | Classroom | 158 | 10 |  | 835 | 18 | 10 | Unit Ventilator
162 | Classroom | 0 | 0 |  | 711 | 16 | 0 | Unit Ventilator
175 | Classroom | 480 | 32 |  | 1223 | 27 | 27 | Unit Ventilator
200 | Classroom | 137 | 9 |  | 715 | 16 | 9 | Unit Ventilator
201 | Classroom | 548 | 36 |  | 728 | 16 | 16 | Unit Ventilator
202 | Classroom | 525 | 35 |  | 755 | 17 | 17 | Unit Ventilator
203 | Classroom | 232 | 15 |  | 555 | 12 | 12 | Unit Ventilator
203A | Classroom | 418 | 27 |  | 546 | 12 | 12 | Unit Ventilator
204 | Classroom | 523 | 34 |  | 572 | 13 | 13 | Unit Ventilator
205 | Classroom | 441 | 29 |  | 1073 | 24 | 24 | Unit Ventilator
206 | Classroom | 463 | 30 |  | 677 | 15 | 15 | Unit Ventilator
207 | Classroom | 790 | 52 |  | 651 | 14 | 14 | Unit Ventilator
208 | Classroom | 704 | 46 |  | 724 | 16 | 16 | Unit Ventilator
209 | Classroom | 769 | 51 |  | 1069 | 24 | 24 | Unit Ventilator
210 | Classroom | 410 | 27 |  | 730 | 16 | 16 | Unit Ventilator
211 | Classroom | 730 | 48 |  | 1069 | 24 | 24 | Unit Ventilator
212 | Classroom | 504 | 33 |  | 662 | 15 | 15 | Unit Ventilator
213 | Classroom | 650 | 43 |  | 1100 | 25 | 25 | Unit Ventilator
214 | Classroom | 522 | 34 |  | 713 | 16 | 16 | Unit Ventilator
215 A&B | Offices | 842 | 56 |  | 410 | 9 | 9 | Unit Ventilator
215 C&D | Offices | 833 | 55 |  | 410 | 9 | 9 | Unit Ventilator
216 | Classroom | 552 | 36 |  | 678 | 15 | 15 | Unit Ventilator
218 | Classroom | 527 | 35 |  | 677 | 15 | 15 | Unit Ventilator
219A | Classroom | 313 | 20 |  | 607 | 13 | 13 | Unit Ventilator
219B | Classroom | 322 | 21 |  | 446 | 10 | 10 | Unit Ventilator
220 | Classroom | 534 | 35 |  | 662 | 15 | 15 | Unit Ventilator
221A | Classroom | 307 | 20 |  | 717 | 16 | 16 | Unit Ventilator
221B | Classroom | 334 | 22 |  | 391 | 8 | 8 | Unit Ventilator
222 | Classroom | 547 | 36 |  | 792 | 18 | 18 | Unit Ventilator
223A | Classroom | 267 | 17 |  | 598 | 13 | 13 | Unit Ventilator
223C | Classroom | 426 | 28 |  | 373 | 8 | 8 | Unit Ventilator
225 | Classroom | 708 | 47 |  | 1445 | 32 | 32 | Unit Ventilator
227A | Classroom | 311 | 20 |  | 590 | 13 | 13 | Unit Ventilator
227B | Classroom | 298 | 19 |  | 494 | 11 | 11 | Unit Ventilator
228 | Classroom | 525 | 35 |  | 784 | 17 | 17 | Unit Ventilator
229B | Classroom | 165 | 11 |  | 525 | 11 | 11 | Unit Ventilator
229C | Classroom | 325 | 21 |  | 570 | 12 | 12 | Unit Ventilator
230 | Classroom | 503 | 33 |  | 657 | 14 | 14 | Unit Ventilator
231 | Classroom | 562 | 37 |  | 751 | 17 | 17 | Unit Ventilator
232 | Classroom | 592 | 39 |  | 691 | 15 | 15 | Unit Ventilator
233 | Classroom | 557 | 37 |  | 705 | 16 | 16 | Unit Ventilator
234 | Classroom | 532 | 35 |  | 703 | 15 | 15 | Unit Ventilator
235 | Classroom | 458 | 30 |  | 704 | 16 | 16 | Unit Ventilator
236 | Classroom | 405 | 27 |  | 701 | 15 | 15 | Unit Ventilator
237 | Room | 148 | 9 |  | 384 | 8 | 8 | Unit Ventilator
238 | Classroom | 389 | 25 |  | 675 | 15 | 15 | Unit Ventilator
240 | Classroom | 411 | 27 |  | 685 | 15 | 15 | Unit Ventilator
242 | Classroom | 479 | 31 |  | 711 | 16 | 16 | Unit Ventilator
244 | Classroom | 518 | 34 |  | 634 | 14 | 14 | Unit Ventilator
1st Fl. Corridor | Corridor | 0 | 0 |  | 892 | 20 | 0 | Unit Ventilator
2nd Fl. Corr. | 2nd Fl. Corr. | 0 | 0 |  | 9100 | 206 | 0 | Unit Ventilator
- | Auditorium | 1799 | 119 |  | 12288 | 279 | 119 | Heating Ventilation Unit
- | Band Room | 254 | 16 |  | 1028 | 23 | 16 | Heating Ventilation Unit
Boys Gym #1 | Gym | 336 | 22 |  | 3701 | 84 | 22 | Heating Ventilation Unit
Boys Gym #1 | Gym | 307 | 20 |  | 3701 | 84 | 20 | Heating Ventilation Unit
Boys Gym #2 | Gym | 2587 | 172 |  | 3701 | 84 | 84 | Heating Ventilation Unit
Boys Gym #2 | Gym | 1367 | 91 |  | 3701 | 84 | 84 | Heating Ventilation Unit
Boys Lckr. Rm. | Locker Rm. | 1229 | 81 |  | 5966 | 135 | 81 | Heating Ventilation Unit
Cafeteria | Cafeteria | 1685 | 112 |  | 12073 | 274 | 112 | Heating Ventilation Unit
Girls Gym #1 | Gym | 317 | 21 |  | 3514 | 79 | 21 | Heating Ventilation Unit
Girls Gym #1 | Gym | 397 | 26 |  | 3514 | 79 | 26 | Heating Ventilation Unit
Girls Gym #2 | Gym | 187 | 12 |  | 3514 | 79 | 12 | Heating Ventilation Unit
Girls Lckr. Rm. | Locker Rm. | 0 | 0 |  | 3920 | 89 | 0 | Heating Ventilation Unit
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator
Library | Library | 2751 | 183 |  | 1816 | 41 | 41 | Heating Ventilation Unit
Library | Library | 453 | 30 |  | 454 | 10 | 10 | Unit Ventilator
Library | Library | 525 | 35 |  | 454 | 10 | 10 | Unit Ventilator
Library | Library | 509 | 33 |  | 454 | 10 | 10 | Unit Ventilator
Library | Library | 477 | 31 |  | 454 | 10 | 10 | Unit Ventilator
Main office | Offices | 446 | 29 |  | 2450 | 55 | 29 | Unit Ventilator
Stage | Stage | 235 | 15 |  | 1743 | 39 | 15 | Unit Ventilator
Stage | Stage | 262 | 17 |  | 1743 | 39 | 17 | Unit Ventilator

## Olney ES and Annex
Sheet Last Modified: | 2021-04-29
School: | Olney Elementary School
Vendor: | Devine Main Building ABR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
101 | Classroom | 180 | 12 |  | 520 | 11 | 11 | AIr Handling Unit
102 | Classroom | 122 | 8 |  | 520 | 11 | 8 | AIr Handling Unit
103 | Classroom | 142 | 9 |  | 520 | 11 | 9 | AIr Handling Unit
104 | Classroom | 527 | 35 |  | 520 | 11 | 11 | AIr Handling Unit
107 | Classroom | 63 | 4 |  | 667 | 15 | 4 | Univent
108 | Classroom | 235 | 15 |  | 840 | 19 | 15 | Univent
111 | Classroom | 88 | 5 |  | 378 | 8 | 5 | Univent
201 | Classroom | 289 | 19 |  | 682 | 15 | 15 | Univent
203 | Classroom | 327 | 21 |  | 928 | 21 | 21 | Univent
204 | Classroom | 286 | 19 |  | 756 | 17 | 17 | Univent
205 | Classroom | 303 | 20 |  | 784 | 17 | 17 | Univent
206 | Classroom | 296 | 19 |  | 812 | 18 | 18 | Univent
207 | Classroom | 309 | 20 |  | 594 | 13 | 13 | Univent
208 | Classroom | 324 | 21 |  | 748 | 17 | 17 | Univent
209 | Classroom | 282 | 18 |  | 1232 | 28 | 18 | Univent
210 | Classroom | 327 | 21 |  | 330 | 7 | 7 | Univent
211 | Classroom | 326 | 21 |  | 756 | 17 | 17 | Univent
301 | Classroom | 0 | 0 |  | 682 | 15 | 0 | Univent
302 | Classroom | 328 | 21 |  | 682 | 15 | 15 | Univent
303 | Classroom | 281 | 18 |  | 899 | 20 | 18 | Univent
304 | Classroom | 280 | 18 |  | 729 | 16 | 16 | Univent
305 | Classroom | 324 | 21 |  | 812 | 18 | 18 | Univent
306 | Classroom | 285 | 19 |  | 783 | 17 | 17 | Univent
307 | Classroom | 279 | 18 |  | 594 | 13 | 13 | Univent
308 | Classroom | 291 | 19 |  | 782 | 17 | 17 | Univent
309 | Classroom | 325 | 21 |  | 638 | 14 | 14 | Univent
310 | Classroom | 328 | 21 |  | 638 | 14 | 14 | Univent
311 | Classroom | 309 | 20 |  | 756 | 17 | 17 | Univent
- | Main Office |  | 0 |  | 480 | 10 | 0
- | Principal's Office | 173 | 11 |  | 396 | 9 | 9 | Univent
- | Boys' Cafeteria |  | 0 | Yes | 1271 | 28 |  | Active Pure
- | Girls' Cafeteria |  | 0 | Yes | 943 | 21 |  | Active Pure
Annex
1 | Classroom |  | 0 | Yes | 684 | 15 | 15
2 | Classroom |  | 0 | Yes | 1050 | 23 | 23
3 | Classroom |  | 0 | Yes | 792 | 18 | 18
4 | Classroom |  | 0 | Yes | 840 | 19 | 19
5 | Classroom |  | 0 | Yes | 1104 | 25 | 25
6 | Classroom |  | 0 | Yes | 700 | 15 | 15
7 | Classroom |  | 0 | Yes | 1050 | 23 | 23
8 | Classroom |  | 0 | Yes | 816 | 18 | 18
9 | Classroom |  | 0 | Yes | 840 | 19 | 19
10 | Classroom |  | 0 | Yes | 875 | 19 | 19
- | Lobby |  | 0 | Yes | 180 | 4 | 4
- | Counselor Office |  | 0 | Yes | 108 | 2 | 2
- | Asst Principal's Office |  | 0 | Yes | 89 | 2 | 2
- | Gym |  | 0 | Yes | 4328 | 98 | 98 | Hydroxyl Unit
- | Nurse Open area (Office D) and Early Lit |  | 0 | Yes | 547 | 12 | 12
- | Conference room (medical waiting) |  | 0 | Yes | 141 | 3 | 3

## One Bright Ray
Sheet Last Modified: | 2021-03-18
School: | One Bright Ray- Elmwood
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 313 | 20 |  |  | 0 | 0 | Air Handling Unit
102 | Classroom | 189 | 12 |  |  | 0 | 0 | Air Handling Unit
103 | Classroom | 249 | 16 |  |  | 0 | 0 | Air Handling Unit
104 | Classroom | 215 | 14 |  |  | 0 | 0 | Air Handling Unit
105 | Classroom | 250 | 16 |  |  | 0 | 0 | Air Handling Unit
105 | Principal's Office | 58 | 3 |  |  | 0 | 0 | Air Handling Unit
- | Dean of Students Office | 56 | 3 |  |  | 0 | 0 | Air Handling Unit
- | Faculty Lounge | 69 | 4 |  |  | 0 | 0 | Air Handling Unit
- | Foyer / Hallway | 147 | 9 |  |  | 0 | 0 | Air Handling Unit
- | Open Space / Classroom | 475 | 31 |  |  | 0 | 0 | Air Handling Unit
- | SW Office | 48 | 3 |  |  | 0 | 0 | Air Handling Unit

## Overbrook Ed. Center
Sheet Last Modified: | 2021-04-30
School: | Overbrook Educational Center Elementary School
Vendor: | Goldner | Retest
School: | Overbrook Education Center Annex
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
- | Boiler Room | 602 | 40 |  | 1496 | 34 | 34 | AHU
- | BE Office |  | 0 |  | 491 | 11 | 0 | AHU
- | Cafeteria | 233 | 15 | Yes | 1936 | 44 | 44 | AHU
- | Corridor | 49 | 3 |  |  | 0 | 0 | AHU
- | Kitchen | 53 | 3 |  | 440 | 10 | 3 | AHU
- | Music Room | 204 | 13 |  | 748 | 17 | 13 | AHU
- | Computer Room | 79 | 5 |  | 176 | 4 | 4 | AHU
- | 1st Flr Entryway | 42 | 2 |  | 396 | 9 | 2 | AHU
- | Exam Office | 32 | 2 |  | 176 | 4 | 2 | AHU
- | Gym Office | 28 | 1 |  | 132 | 3 | 1 | AHU
- | Gym /Stage | 1257 | 83 |  | 2332 | 53 | 53 | AHU
- | Gym Lobby | 109 | 7 |  |  | 0 | 0 | AHU
1st flr Hallway | Corridor | 20 | 1 |  |  | 0 | 0 | AHU
1st flr Lobby | Main Lobby | 71 | 4 |  | 396 | 9 | 4 | AHU
1st flr Main Office | Administration | 65 | 4 |  | 220 | 5 | 4 | AHU
1st flr Nurse's Office | Medical | 38 | 2 |  | 264 | 6 | 2 | AHU
1st flr Office | Principal | 49 | 3 |  | 220 | 5 | 3 | AHU
1st flr Office | Copy Room | 19 | 1 |  | 88 | 2 | 1 | AHU
1st flr Office | Conference Room | 47 | 3 |  | 176 | 4 | 3 | AHU
201 | Faculty Lounge | 161 | 10 |  | 220 | 5 | 5 | AHU
204 | Office | 171 | 11 | Yes | 176 | 4 | 4 | RTU
206 | Classroom | 370 | 24 |  | 660 | 15 | 15 | Univent
207 | Classroom | 353 | 23 |  | 748 | 17 | 17 | Univent
208 | Classroom | 446 | 29 |  | 748 | 17 | 17 | Univent
209 | Classroom | 475 | 31 |  | 572 | 13 | 13 | Univent
210 | Classroom | 425 | 28 |  | 660 | 15 | 15 | Univent
211 | Classroom (Life Skills) | 536 | 35 |  | 748 | 17 | 17 | Univent
2nd flr Library | Library | 344 | 22 |  | 1496 | 34 | 22 | AHU
2nd flr Art | Classroom | 74 | 4 |  | 924 | 21 | 4 | AHU
2nd Flr Hallway | Corridor | 197 | 13 |  |  | 0 | 0 | AAON unit
2nd flr Science | Classroom | 84 | 5 |  | 836 | 19 | 5 | AHU
301 | Classroom | 452 | 30 |  | 220 | 5 | 5 | RTU
302 | Office | 284 | 18 |  | 176 | 4 | 4 | AHU
304 | Classroom | 463 | 30 |  | 660 | 15 | 15 | Univent
305 | Classroom | 517 | 34 |  | 748 | 17 | 17 | Univent
306 | Classroom | 550 | 36 |  | 704 | 16 | 16 | Univent
307 | Classroom | 596 | 39 |  | 572 | 13 | 13 | Univent
308 | Classroom | 461 | 30 |  | 660 | 15 | 15 | Univent
309 | Classroom | 1030 | 68 |  | 748 | 17 | 17 | Univent
316 | Classroom |  | 0 | Yes | 695 | 15 | 15
Annex Building
5 | Kitchen |  | 0 | Yes | 157 | 3 | 3
6 | Office |  | 0 | Yes | 122 | 2 | 2
7 | Lobby |  | 0 |  | 890 | 20 | 0
1 | Classroom |  | 0 | Yes | 1077 | 24 | 24
2 | Classroom |  | 0 | Yes | 404 | 9 | 9
25 | Classroom |  | 0 | Yes | 555 | 12 | 12
24 | Office |  | 0 | Yes | 177 | 4 | 4
22 | Classroom |  | 0 | Yes | 902 | 20 | 20
21 | Classroom |  | 0 | Yes | 297 | 6 | 6
31 | Classroom |  | 0 | Yes | 304 | 6 | 6
32 | Classroom |  | 0 | Yes | 909 | 20 | 20
34 | Classroom |  | 0 |  | 232 | 5 | 0

## Overbrook Elementary
Sheet Last Modified: | 2021-03-18
School: | Overbrook Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 825 | 55 |  | 720 | 16 | 16 | House fan
2 | Classroom | 798 | 53 |  | 720 | 16 | 16 | House fan
3 | Classroom | 872 | 58 |  | 720 | 16 | 16 | House fan
4 | Classroom | 838 | 55 |  | 528 | 12 | 12 | House fan
5 | Classroom | 579 | 38 |  | 720 | 16 | 16 | House fan
6 | Classroom | 499 | 33 |  | 720 | 16 | 16 | House fan
7 | Classroom | 816 | 54 |  | 768 | 17 | 17 | House fan
8 | Classroom | 614 | 40 |  | 768 | 17 | 17 | House fan
9 | Classroom | 788 | 52 |  | 768 | 17 | 17 | House fan
12 | Classroom | 522 | 34 |  | 720 | 16 | 16 | House fan
13 | Classroom | 581 | 38 |  | 720 | 16 | 16 | House fan
14 | Classroom | 472 | 31 |  | 720 | 16 | 16 | House fan
15 | Classroom | 412 | 27 |  | 720 | 16 | 16 | House fan
16 | Classroom | 505 | 33 |  | 720 | 16 | 16 | House fan
17 | Classroom | 524 | 34 |  | 720 | 16 | 16 | House fan
18 | Classroom | 508 | 33 |  | 768 | 17 | 17 | House fan
19 | Classroom | 654 | 43 |  | 768 | 17 | 17 | House fan
20 | Classroom | 498 | 33 |  | 768 | 17 | 17 | House fan
- | Boys Bathroom | 826 | 55 |  | 736 | 16 | 16 | House fan
- | Cafeteria | 1236 | 82 |  | 1560 | 35 | 35 | House fan
- | Faculty bathroom | 40 | 2 |  | 64 | 1 | 1 | House fan
- | Girls Bathroom | 445 | 29 |  | 340 | 7 | 7 | House fan

## Overbrook High
Sheet Last Modified: | 2021-04-30
School: | Overbrook High School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
10 | - |  | 0 |  | 1041 | 23 | 0
11 | - |  | 0 |  | 1450 | 32 | 0
100 | Classroom |  | 0 |  | 1409 | 32 | 0
100A | Classroom |  | 0 | Yes | 435 | 9 | 9
100B | Classroom |  | 0 | Yes | 479 | 10 | 10
100C | Classroom |  | 0 | Yes | 1407 | 31 | 31
101 | Classroom |  | 0 | Yes | 832 | 18 | 18
102 | Classroom |  | 0 |  | 742 | 16 | 0
103 | Classroom |  | 0 |  | 692 | 15 | 0
104 | Classroom |  | 0 |  | 649 | 14 | 0
105 | Classroom |  | 0 |  | 990 | 22 | 0
105A | Classroom |  | 0 |  | 228 | 5 | 0
106A | Classroom |  | 0 |  | 535 | 12 | 0
160B | Classroom |  | 0 |  | 534 | 12 | 0
107 | Classroom |  | 0 |  | 703 | 15 | 0
108 | Classroom |  | 0 |  | 677 | 15 | 0
109A | Classroom |  | 0 |  | 551 | 12 | 0
109B | Classroom |  | 0 |  | 507 | 11 | 0
110 | Classroom |  | 0 |  | 931 | 21 | 0
117 | Classroom |  | 0 |  | 515 | 11 | 0
118 | Classroom |  | 0 |  | 556 | 12 | 0
119 | Classroom |  | 0 |  | 753 | 17 | 0
120 | Classroom |  | 0 |  | 1026 | 23 | 0
121 | Classroom |  | 0 |  | 1048 | 23 | 0
200 | Classroom |  | 0 |  | 304 | 6 | 0
201 | Classroom |  | 0 |  | 496 | 11 | 0
201 | Classroom |  | 0 |  | 490 | 11 | 0
202 | Classroom |  | 0 |  | 486 | 11 | 0
204 | Classroom |  | 0 |  | 881 | 20 | 0
205 | Classroom |  | 0 |  | 733 | 16 | 0
206 | Classroom |  | 0 |  | 1003 | 22 | 0
207 | Classroom |  | 0 |  | 718 | 16 | 0
209 | Classroom |  | 0 |  | 337 | 7 | 0
210 | Classroom |  | 0 |  | 460 | 10 | 0
211 | Classroom |  | 0 |  | 713 | 16 | 0
212 | Classroom |  | 0 |  | 728 | 16 | 0
213 | Classroom |  | 0 |  | 902 | 20 | 0
214 | Classroom |  | 0 |  | 796 | 18 | 0
215 | Classroom |  | 0 |  | 3413 | 77 | 0
216 | Classroom |  | 0 |  | 850 | 19 | 0
217 | Classroom |  | 0 |  | 712 | 16 | 0
218 | Classroom |  | 0 |  | 700 | 15 | 0
219 | Classroom |  | 0 |  | 719 | 16 | 0
220 | Classroom |  | 0 |  | 359 | 8 | 0
221 | Classroom |  | 0 |  | 877 | 19 | 0
222 | Classroom |  | 0 |  | 877 | 19 | 0
223 | Classroom |  | 0 |  | 729 | 16 | 0
224 | Classroom |  | 0 |  | 731 | 16 | 0
225 | Classroom |  | 0 |  | 694 | 15 | 0
300 | Classroom |  | 0 |  | 747 | 16 | 0
301 | Classroom |  | 0 |  | 724 | 16 | 0
302 | Classroom |  | 0 |  | 737 | 16 | 0
303 | Classroom |  | 0 |  | 907 | 20 | 0
304 | Classroom |  | 0 |  | 941 | 21 | 0
305 | Classroom |  | 0 |  | 724 | 16 | 0
306 | Classroom |  | 0 |  | 738 | 16 | 0
307 | Classroom |  | 0 |  | 739 | 16 | 0
308 | Classroom |  | 0 |  | 834 | 18 | 0
309 | Classroom |  | 0 |  | 733 | 16 | 0
311 | Classroom |  | 0 |  | 721 | 16 | 0
312 | Classroom |  | 0 |  | 704 | 16 | 0
313 | Classroom |  | 0 |  | 491 | 11 | 0
314 | Classroom |  | 0 |  | 669 | 15 | 0
315 | Classroom |  | 0 |  | 673 | 15 | 0
316 | Classroom |  | 0 | Yes | 762 | 17 | 17
317 | Classroom |  | 0 | Yes | 917 | 20 | 20
318 | Classroom |  | 0 |  | 669 | 15 | 0
319 | Classroom |  | 0 |  | 681 | 15 | 0
320 | Classroom |  | 0 |  | 724 | 16 | 0
321 | Classroom |  | 0 |  | 712 | 16 | 0
322 | Classroom |  | 0 |  | 499 | 11 | 0
323 | Classroom |  | 0 |  | 437 | 9 | 0
324 | Classroom |  | 0 |  | 801 | 18 | 0
325 | Classroom |  | 0 |  | 936 | 21 | 0
326 | Classroom |  | 0 |  | 690 | 15 | 0
327 | Classroom |  | 0 |  | 191 | 4 | 0
328 | Classroom |  | 0 |  | 683 | 15 | 0
329 | Classroom |  | 0 |  | 711 | 16 | 0
330 | Classroom |  | 0 |  | 690 | 15 | 0
331 | Classroom |  | 0 |  | 204 | 4 | 0
332 | Classroom |  | 0 |  | 687 | 15 | 0
333 | Classroom |  | 0 |  | 720 | 16 | 0
334 | Classroom |  | 0 |  | 817 | 18 | 0
- | Main Office |  | 0 |  | 1057 | 24 | 0
- | Principal Office |  | 0 |  | 562 | 12 | 0
- | Auditorium Balcony |  | 0 |  | 1436 | 32 | 0
- | Auditorium |  | 0 |  | 8711 | 197 | 0
- | Teachers Lounge |  | 0 |  | 310 | 7 | 0
- | Cafeteria A |  | 0 |  | 2778 | 63 | 0
- | Cafeteria B |  | 0 |  | 4516 | 102 | 0

## Palumbo
Sheet Last Modified: | 2021-04-29
School: | Academy @ Palumbo High School
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
103 | Graphics Arts | 1248 | 83 |  | 1058 | 24 | 24 | Air Handling Unit
104 | Fine Arts | 271 | 18 |  | 782 | 17 | 17 | Air Handling Unit
118 | Conference Room | 1440 | 96 |  | 690 | 15 | 15 | Air Handling Unit
129 | Main Office | 723 | 48 |  | 528 | 12 | 12 | Air Handling Unit
132 | Mixed Choir | 736 | 49 |  | 966 | 21 | 21 | Air Handling Unit
134 | Music Theory | 1170 | 78 |  | 946 | 21 | 21 | Air Handling Unit
135 | Intro to Music | 1709 | 113 |  | 968 | 22 | 22 | Air Handling Unit
136 | Music Equipment Storage | 609 | 40 |  | 396 | 9 | 9 | Air Handling Unit
204 | Creative Writing | 843 | 56 |  | 660 | 15 | 15 | Air Handling Unit
205 | Computer Lab | 653 | 43 |  | 768 | 17 | 17 | Air Handling Unit
206 | Environment Club | 713 | 47 |  | 690 | 15 | 15 | Air Handling Unit
207 | Language & Journalism | 1069 | 71 |  | 690 | 15 | 15 | Air Handling Unit
212 | Visitor's Locker Room | 615 | 41 |  | 720 | 16 | 16 | Air Handling Unit
221 | History | 618 | 41 |  | 690 | 15 | 15 | Air Handling Unit
223 | Literature | 750 | 50 |  | 1104 | 25 | 25 | Air Handling Unit
224 | English / History | 113 | 7 |  | 660 | 15 | 7 | Air Handling Unit
231 | Office | 595 | 39 |  | 484 | 11 | 11 | Air Handling Unit
301 | Forensics / Algebra 2 | 604 | 40 |  | 528 | 12 | 12 | Air Handling Unit
302 | Dean's Office | 1510 | 100 |  | 440 | 10 | 10 | Air Handling Unit
305 | History | 257 | 17 |  | 690 | 15 | 15 | Air Handling Unit
306 | Spanish | 554 | 36 |  | 690 | 15 | 15 | Air Handling Unit
307 | American History | 282 | 18 |  | 690 | 15 | 15 | Air Handling Unit
312 | Cardio & Weight Lifting | 615 | 41 |  | 720 | 16 | 16 | Air Handling Unit
321 | Spanish | 666 | 44 |  | 690 | 15 | 15 | Air Handling Unit
321 | History | 532 | 35 |  | 690 | 15 | 15 | Air Handling Unit
322 | History | 1582 | 105 |  | 690 | 15 | 15 | Air Handling Unit
323 | Spanish | 567 | 37 |  | 690 | 15 | 15 | Air Handling Unit
332 | Black History | 84 | 5 |  | 638 | 14 | 5 | Air Handling Unit
333 | History | 1066 | 71 |  | 792 | 18 | 18 | Air Handling Unit
334 | Psychologist | 0 | 0 |  | 567 | 12 | 0 | Air Handling Unit
336 | Spanish | 0 | 0 |  | 1058 | 24 | 0 | Air Handling Unit
403 | Physics Lab | 322 | 21 |  | 1056 | 24 | 21 | Air Handling Unit
407 | Biology Lab | 587 | 39 |  | 1440 | 32 | 32 | Air Handling Unit
411 | Chemistry | 651 | 43 |  | 720 | 16 | 16 | Air Handling Unit
412 | Unknown | 668 | 44 |  | 720 | 16 | 16 | Air Handling Unit
421 | Spanish | 117 | 7 |  | 690 | 15 | 7 | Air Handling Unit
422 | Chinese | 965 | 64 |  | 690 | 15 | 15 | Air Handling Unit
423 | English 1 | 628 | 41 |  | 690 | 15 | 15 | Air Handling Unit
432 | Literature | 484 | 32 |  | 760 | 17 | 17 | Air Handling Unit
433 | History | 142 | 9 |  | 760 | 17 | 9 | Air Handling Unit
436 | Science | 769 | 51 |  | 1058 | 24 | 24 | Air Handling Unit
437 | Geometry | 723 | 48 |  | 552 | 12 | 12 | Air Handling Unit
501 | Algebra 2 | 677 | 45 |  | 768 | 17 | 17 | Air Handling Unit
502 | Forensics / Algebra | 415 | 27 |  | 768 | 17 | 17 | Air Handling Unit
503 | Statistics | 483 | 32 |  | 768 | 17 | 17 | Air Handling Unit
504 | Algebra | 190 | 12 |  | 768 | 17 | 12 | Air Handling Unit
506 | Algebra | 707 | 47 |  | 768 | 17 | 17 | Air Handling Unit
507 | Computer Science | 420 | 28 |  | 768 | 17 | 17 | Air Handling Unit
521 | Algebra | 190 | 12 |  | 690 | 15 | 12 | Air Handling Unit
522 | Math | 2026 | 135 |  | 968 | 22 | 22 | Air Handling Unit
524 | Algebra | 1222 | 81 |  | 770 | 17 | 17 | Air Handling Unit
529 | Film | 493 | 32 |  | 660 | 15 | 15 | Air Handling Unit
201A | Exercise | 323 | 21 |  | 23 | 0 | 0 | Air Handling Unit
201B | Exercise | 627 | 41 |  | 1771 | 40 | 40 | Air Handling Unit
304A | Computer Lab | 571 | 38 |  | 500 | 11 | 11 | Air Handling Unit
304B | Computer Lab | 637 | 42 |  | 446 | 10 | 10 | Air Handling Unit
329A | Admin. Office | 605 | 40 |  | 660 | 15 | 15 | Air Handling Unit
329B | Admin. Office | 196 | 13 |  | 660 | 15 | 13 | Air Handling Unit
337A | Study Skills / AS | 860 | 57 |  | 337 | 7 | 7 | Air Handling Unit
337B | Study Skills / AS | 975 | 65 |  | 552 | 12 | 12 | Air Handling Unit
404A | Chemistry Lab | 230 | 15 |  | 720 | 16 | 15 | Air Handling Unit
404B | Chemistry Lab | 2087 | 139 |  | 720 | 16 | 16 | Air Handling Unit
409A | Office | 43 | 2 |  | 280 | 6 | 2 | Air Handling Unit
409B | Office | 123 | 8 |  | 280 | 6 | 6 | Air Handling Unit
429A | Robotics | 574 | 38 |  | 1320 | 30 | 30 | Air Handling Unit
429B | Robotics | 652 | 43 |  | 429 | 9 | 9 | Air Handling Unit
434A | Algebra | 541 | 36 |  | 434 | 9 | 9 | Air Handling Unit
434B | Algebra | 276 | 18 |  | 1188 | 27 | 18 | Air Handling Unit
B14 | Storage | 594 | 39 |  | 374 | 8 | 8 | Air Handling Unit
B15 | Storage | 237 | 15 |  | 384 | 8 | 8 | Air Handling Unit
B16 | Storage | 37 | 2 |  | 90 | 2 | 2 | Air Handling Unit
B17 | Storage | 326 | 21 |  | 364 | 8 | 8 | Air Handling Unit
B19 | Storage | 723 | 48 |  | 1013 | 23 | 23 | Air Handling Unit
B24-A | Storage | 723 | 48 |  | 1013 | 23 | 23 | Air Handling Unit
B24-B | Storage | 461 | 30 |  | 1013 | 23 | 23 | Air Handling Unit
- | Auditorium | 16042 | 1069 |  | 12420 | 282 | 282 | Air Handling Unit
- | Gyms and Cafeteria | 7343 | 489 |  | 21078 | 479 | 479 | Air Handling Unit
- | Home Locker Room | 417 | 27 |  | 720 | 16 | 16 | Air Handling Unit
- | Locker Room | 417 | 27 |  | 720 | 16 | 16 | Air Handling Unit
- | Main Library | 1095 | 73 |  | 4608 | 104 | 73 | Air Handling Unit
- | Library A | 1256 | 83 |  | 238 | 5 | 5 | Air Handling Unit
- | Library B | 1078 | 71 |  | 238 | 5 | 5 | Air Handling Unit
- | Library Storage | 917 | 61 |  | 288 | 6 | 6 | Air Handling Unit
- | Men's Room | 50 | 3 |  | 252 | 5 | 3 | Air Handling Unit
- | Ladies Room | 46 | 3 |  | 252 | 5 | 3 | Air Handling Unit
- | Safe Room | 1158 | 77 |  | 675 | 15 | 15 | Air Handling Unit
B18 | Storage | 477 | 31 |  | 723 | 16 | 16
B20 | Storage | 461 | 30 |  | 1013 | 23 | 23
B21 | Storage | 736 | 49 |  | 966 | 21 | 21
B22 | Storage | 723 | 48 |  | 528 | 12 | 12
B23 | Storage | 323 | 21 |  | 23 | 0 | 0
B24 | Storage | 627 | 41 |  | 1771 | 40 | 40
B25 | Storage | 843 | 56 |  | 660 | 15 | 15
B26 | Storage | 113 | 7 |  | 660 | 15 | 7
B27 | Storage | 595 | 39 |  | 484 | 11 | 11
B28 | Storage | 604 | 40 |  | 528 | 12 | 12
B29 | Storage | 1510 | 100 |  | 440 | 10 | 10
B30 | Storage | 571 | 38 |  | 500 | 11 | 11
B31 | Storage | 637 | 42 |  | 446 | 10 | 10
B32 | Storage | 666 | 44 |  | 690 | 15 | 15
B33 | Storage | 567 | 37 |  | 690 | 15 | 15
B34 | Storage | 605 | 40 |  | 660 | 15 | 15
B35 | Storage | 196 | 13 |  | 660 | 15 | 13
B36 | Storage | 84 | 5 |  | 638 | 14 | 5
B37 | Storage | 1066 | 71 |  | 792 | 18 | 18
B38 | Storage | 0 | 0 |  | 567 | 12 | 0
B39 | Storage | 0 | 0 |  | 1058 | 24 | 0
B40 | Storage | 860 | 57 |  | 337 | 7 | 7
B41 | Storage | 975 | 65 |  | 552 | 12 | 12
B42 | Storage | 322 | 21 |  | 1056 | 24 | 21
B43 | Storage | 230 | 15 |  | 720 | 16 | 15
B44 | Storage | 2087 | 139 |  | 720 | 16 | 16
B45 | Storage | 628 | 41 |  | 690 | 15 | 15
B46 | Storage | 574 | 38 |  | 1320 | 30 | 30
B47 | Storage | 652 | 43 |  | 429 | 9 | 9
B48 | Storage | 484 | 32 |  | 760 | 17 | 17
B49 | Storage | 142 | 9 |  | 760 | 17 | 9
B50 | Storage | 541 | 36 |  | 434 | 9 | 9
B51 | Storage | 276 | 18 |  | 1188 | 27 | 18
B52 | Storage | 769 | 51 |  | 1058 | 24 | 24
B53 | Storage | 723 | 48 |  | 552 | 12 | 12
B54 | Storage | 677 | 45 |  | 768 | 17 | 17
B55 | Storage | 415 | 27 |  | 768 | 17 | 17
B56 | Storage | 483 | 32 |  | 768 | 17 | 17
B57 | Storage | 1222 | 81 |  | 770 | 17 | 17
B58 | Storage | 493 | 32 |  | 660 | 15 | 15
B59 | Storage | 1158 | 77 |  |  | 0 | 0
B60 | Storage | 26166 | 1744 |  |  | 0 | 0
B61 | Storage | 594 | 39 |  | 374 | 8 | 8
B62 | Storage | 237 | 15 |  | 384 | 8 | 8
B63 | Storage | 37 | 2 |  | 90 | 2 | 2
B64 | Storage | 1170 | 78 |  | 946 | 21 | 21
B65 | Storage | 1709 | 113 |  | 968 | 22 | 22
B66 | Storage | 609 | 40 |  | 396 | 9 | 9
B67 | Storage | 1248 | 83 |  | 1058 | 24 | 24
B68 | Storage | 271 | 18 |  | 782 | 17 | 17
B69 | Storage | 1440 | 96 |  | 690 | 15 | 15
B70 | Storage | 653 | 43 |  | 768 | 17 | 17
B71 | Storage | 713 | 47 |  | 690 | 15 | 15
B72 | Storage | 1069 | 71 |  | 690 | 15 | 15
B73 | Storage | 615 | 41 |  | 720 | 16 | 16
B74 | Storage | 417 | 27 |  | 720 | 16 | 16
B75 | Storage | 618 | 41 |  | 690 | 15 | 15
B76 | Storage | 750 | 50 |  | 1104 | 25 | 25
B77 | Storage | 257 | 17 |  | 690 | 15 | 15
B78 | Storage | 554 | 36 |  | 690 | 15 | 15
B79 | Storage | 282 | 18 |  | 690 | 15 | 15
B80 | Storage | 615 | 41 |  | 720 | 16 | 16
B81 | Storage | 532 | 35 |  | 690 | 15 | 15
B82 | Storage | 1582 | 105 |  | 690 | 15 | 15
B83 | Storage | 917 | 61 |  | N/A | 0 | 0
B84 | Storage | 1256 | 83 |  | N/A | 0 | 0
B85 | Storage | 1078 | 71 |  | N/A | 0 | 0
B86 | Storage | 587 | 39 |  | 1440 | 32 | 32
B87 | Storage | 651 | 43 |  | 720 | 16 | 16
B88 | Storage | 668 | 44 |  | 720 | 16 | 16
B89 | Storage | 117 | 7 |  | 690 | 15 | 7
B90 | Storage | 965 | 64 |  | 690 | 15 | 15
B91 | Storage | 417 | 27 |  |  | 0 | 0
B92 | Storage | 190 | 12 |  | 768 | 17 | 12
B93 | Storage | 707 | 47 |  | 768 | 17 | 17
B94 | Storage | 420 | 28 |  | 768 | 17 | 17
B95 | Storage | 190 | 12 |  | 690 | 15 | 12
B96 | Storage | 2026 | 135 |  | 968 | 22 | 22
B97 | Storage | 16042 | 1069 |  | 12420 | 282 | 282
B98 | Storage | 7343 | 489 |  | 21078 | 479 | 479
B99 | Storage | 1095 | 73 |  | 4608 | 104 | 73
B100 | Storage | 43 | 2 |  | 280 | 6 | 2
B101 | Storage | 123 | 8 |  | 280 | 6 | 6
B102 | Storage | 50 | 3 |  | 252 | 5 | 3
B103 | Storage | 46 | 3 |  | 252 | 5 | 3

## Parkway NW @ Hill-Freedman
Sheet Last Modified: | 2021-03-18
School: | Parkway Northwest High School former Hill, JE (Hill-Freedman)
Vendor: | Goldner |  | Goldner Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
108 | Room | 676 | 45 |  | 676 | 15 | 15 | Univent
109 | Room | 333 | 22 |  | 714 | 16 | 16 | Fan Coil Unit
110 | Room | 168 | 11 |  | 1015 | 23 | 11 | Univent
130 | Room | 564 | 37 |  | 630 | 14 | 14 | Univent
131 | Room | 476 | 31 |  | 580 | 13 | 13 | Univent
132 | Room | 528 | 35 |  | 580 | 13 | 13 | Univent
133 | Room | 452 | 30 |  | 469 | 10 | 10 | Univent
134 | Room | 496 | 33 |  | 1015 | 23 | 23 | Univent
135 | Room | 304 | 20 |  | 812 | 18 | 18 | Univent
136 | Room | 424 | 28 |  | 424 | 9 | 9 | Univent
203 | Room | 409 | 27 |  | 600 | 13 | 13 | Univent
204 | Room | 363 | 24 |  | 667 | 15 | 15 | Univent
205 | Room | 376 | 25 |  | 720 | 16 | 16 | Univent
206 | Room | 350 | 23 |  | 810 | 18 | 18 | Univent
207 | Room | 371 | 24 |  | 783 | 17 | 17 | Univent
210 | Room | 482 | 32 |  | 1116 | 25 | 25 | Fan Coil Unit
211 | Room | 329 | 21 |  | 957 | 21 | 21 | Univent
221 | Room | 300 | 20 |  | 580 | 13 | 13 | Univent
222 | Room | 75 | 5 |  | 580 | 13 | 5 | Univent
223 | Room | 523 | 34 |  | 580 | 13 | 13 | Univent
224 | Room | 717 | 47 |  | 580 | 13 | 13 | Univent
225 | Room | 250 | 16 |  | 580 | 13 | 13 | Univent
226 | Room | 163 | 10 |  | 580 | 13 | 10 | Univent
- | Auditurium | 912 | 60 |  | 1050 | 23 | 23 | Univent
- | Gym | 969 | 64 |  | 2460 | 55 | 55 | Univent
- | Main Office | 0 | 0 |  | 399 | 9 | 0

## Patterson
Sheet Last Modified: | 2021-04-30
School: | John M. Patterson Elementary School |  |  | House fan Abated
Vendor: | Devine Brothers Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom |  | 0 | Yes | 648 | 14 | 14 | House Fan
2 | Classroom |  | 0 | Yes | 648 | 14 | 14 | House Fan
3 | Classroom |  | 0 | Yes | 648 | 14 | 14 | House Fan
100 | Office | 0 | 0 |  | 143 | 3 | 0 | House Fan
101 | Classroom | 659 | 43 |  | 704 | 16 | 16 | House Fan
102 | Classroom | 568 | 37 |  | 616 | 14 | 14 | House Fan
103 | Classroom | 403 | 26 |  | 616 | 14 | 14 | House Fan
104 | Classroom | 663 | 44 |  | 616 | 14 | 14 | House Fan
105 | Classroom | 518 | 34 |  | 616 | 14 | 14 | House Fan
106 | Classroom | 639 | 42 |  | 616 | 14 | 14 | House Fan
107 | Classroom | 698 | 46 |  | 616 | 14 | 14 | House Fan
108 | Classroom | 656 | 43 |  | 704 | 16 | 16 | House Fan
109 | Classroom | 658 | 43 |  | 704 | 16 | 16 | House Fan
110 | Classroom | 722 | 48 |  | 704 | 16 | 16 | House Fan
200 | Classroom | 0 | 0 | Yes | 704 | 16 | 16 | House Fan
200A | Counselor | 0 | 0 |  | 240 | 5 | 0 | House Fan
201 | Classroom | 373 | 24 |  | 704 | 16 | 16 | House Fan
202 | Classroom | 578 | 38 |  | 703 | 15 | 15 | House Fan
203 | Classroom | 504 | 33 |  | 616 | 14 | 14 | House Fan
204 | Classroom | 474 | 31 |  | 616 | 14 | 14 | House Fan
205 | Classroom | 421 | 28 |  | 616 | 14 | 14 | House Fan
206 | Classroom | 541 | 36 |  | 616 | 14 | 14 | House Fan
207 | Classroom | 637 | 42 |  | 616 | 14 | 14 | House Fan
208 | Classroom | 209 | 13 |  | 704 | 16 | 13 | House Fan
209 | Classroom | 585 | 39 |  | 704 | 16 | 16 | House Fan
210 | Classroom | 583 | 38 |  | 410 | 9 | 9 | House Fan
300 | Classroom | 394 | 26 |  | 704 | 16 | 16 | House Fan
301 | Classroom | 530 | 35 |  | 704 | 16 | 16 | House Fan
302 | Classroom | 511 | 34 |  | 704 | 16 | 16 | House Fan
303 | Classroom | 576 | 38 |  | 704 | 16 | 16 | House Fan
304 | Classroom | 359 | 23 |  | 616 | 14 | 14 | House Fan
305 | Classroom | 561 | 37 |  | 616 | 14 | 14 | House Fan
306 | Classroom | 604 | 40 |  | 616 | 14 | 14 | House Fan
307 | Classroom | 103 | 6 |  | 616 | 14 | 6 | House Fan
308 | Classroom | 418 | 27 |  | 704 | 16 | 16 | House Fan
309 | Classroom | 101 | 6 |  | 704 | 16 | 6 | House Fan
310 | Classroom | 429 | 28 |  | 704 | 16 | 16 | House Fan
- | Auditorium | 5125 | 341 |  | 2880 | 65 | 65 | House Fan
- | Admin Office | 0 | 0 | Yes | 88 | 2 | 2 | House Fan
- | Principal Office |  | 0 | Yes | 120 | 2 | 2 | House Fan
- | Book Room Storage | 0 | 0 |  | 230 | 5 | 0 | House Fan
- | Boiler Rm. | 22650 | 1510 |  | 1440 | 32 | 32 | House Fan
- | Small Cafeteria | 689 | 45 |  | 1232 | 28 | 28 | House Fan
- | Kitchen | 212 | 14 |  | 200 | 4 | 4 | House Fan
- | Gym/Cafeteria | 0 | 0 | Yes | 3762 | 85 | 85 | House Fan
- | Storage | 574 | 38 |  |  | 0 | 0 | House Fan
- | Music | 375 | 25 |  | 560 | 12 | 12 | House Fan
- | Nurse's Room | 0 | 0 | Yes | 336 | 7 | 7 | House Fan
- | Teacher's Lounge | 0 | 0 | Yes | 410 | 9 | 9 | House Fan

## Penn Alexander
Sheet Last Modified: | 2021-04-20
School: | Penn Alexander Elementary-Middle School
Vendor: | Devine Brothers |  | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B24 | Classroom | 37 | 2 |  | 130 | 2 | 2 | Air Handling Unit
B26 | Classroom | 120 | 8 |  | 216 | 4 | 4 | Air Handling Unit
B28 | Classroom | 483 | 32 |  | 722 | 16 | 16 | Air Handling Unit
106 | Classroom | 1065 | 71 |  | 806 | 18 | 18 | Air Handling Unit
108 | Classroom | 310 | 20 |  | 842 | 19 | 19 | Univent
109 | Classroom | 311 | 20 |  | 759 | 17 | 17 | Univent
110 | Classroom | 305 | 20 |  | 693 | 15 | 15 | Univent
113 | Classroom | 220 | 14 |  | 222 | 5 | 5 | Air Handling Unit
117 | Classroom | 285 | 19 |  | 741 | 16 | 16 | Univent
118 | Classroom | 329 | 21 |  | 759 | 17 | 17 | Univent
119 | Classroom | 315 | 21 |  | 683 | 15 | 15 | Univent
123 | Classroom | 0 | 0 |  | 150 | 3 | 0 | Air Handling Unit
125 | Classroom | 73 | 4 |  | 209 | 4 | 4 | Air Handling Unit
126 | Classroom | 13 | 0 |  | 99 | 2 | 0 | Air Handling Unit
127 | Classroom | 14 | 0 |  | 99 | 2 | 0 | Air Handling Unit
128 | Classroom | 10 | 0 | Yes | 99 | 2 | 2 | Air Handling Unit
129 | Classroom | 84 | 5 | Yes | 291 | 6 | 6 | Air Handling Unit
131 | Classroom | 302 | 20 |  | 694 | 15 | 15 | Univent
133 | Classroom | 0 | 0 | Yes | 644 | 14 | 14 | Univent
134 | Classroom | 330 | 22 |  | 683 | 15 | 15 | Univent
201 | Classroom | 491 | 32 |  | 875 | 19 | 19 | Air Handling Unit
202 | Classroom | 74 | 4 |  | 324 | 7 | 4 | Air Handling Unit
208 | Classroom | 0 | 0 | Yes | 842 | 19 | 19 | Univent
209 | Classroom | 0 | 0 | Yes | 759 | 17 | 17 | Univent
210 | Classroom | 0 | 0 | Yes | 693 | 15 | 15 | Univent
213 | Classroom | 75 | 5 |  | 222 | 5 | 5 | Air Handling Unit
217 | Classroom | 0 | 0 | Yes | 741 | 16 | 16 | Univent
218 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | Univent
219 | Classroom | 0 | 0 | Yes | 683 | 15 | 15 | Univent
220 | Classroom | 241 | 16 |  | 224 | 5 | 5 | Air Handling Unit
221 | Classroom | 0 | 0 | Yes | 96 | 2 | 2 | Air Handling Unit
222 | Classroom | 0 | 0 |  | 169 | 3 | 0 | Air Handling Unit
225 | Classroom | 0 | 0 | Yes | 209 | 4 | 4 | Air Handling Unit
227 | Classroom | 0 | 0 |  | 99 | 2 | 0 | Air Handling Unit
228 | Classroom | 0 | 0 |  | 154 | 3 | 0 | Air Handling Unit
229 | Classroom | 0 | 0 |  | 108 | 2 | 0 | Air Handling Unit
230 | Classroom | 318 | 21 |  | 736 | 16 | 16 | Univent
231 | Classroom | 301 | 20 |  | 840 | 19 | 19 | Univent
233 | Classroom | 266 | 17 |  | 739 | 16 | 16 | Univent
234 | Classroom | 328 | 21 |  | 671 | 15 | 15 | Univent
301 | Classroom | 1176 | 78 |  | 1005 | 22 | 22 | Air Handling Unit
302 | Classroom | 0 | 0 |  | 324 | 7 | 0 | Univent
308 | Classroom | 0 | 0 | Yes | 842 | 19 | 19 | Univent
309 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | Univent
310 | Classroom | 0 | 0 | Yes | 693 | 15 | 15 | Univent
317 | Classroom | 0 | 0 | Yes | 741 | 16 | 16 | Univent
318 | Classroom | 0 | 0 | Yes | 759 | 17 | 17 | Univent
319 | Classroom | 0 | 0 | Yes | 683 | 15 | 15 | Univent
320 | Classroom | 0 | 0 |  | 320 | 7 | 0 | Air Handling Unit
- | Cafeteria | 7801 | 520 |  | 3766 | 85 | 85 | Air Handling Unit
- | GYM | 1362 | 90 |  | 4271 | 97 | 90 | Air Handling Unit
- | Library | 550 | 36 |  | 2658 | 60 | 36 | Air Handling Unit
- | Main Office | 205 | 13 |  | 1063 | 24 | 13 | Air Handling Unit

## Penn Treaty
Sheet Last Modified: | 2021-04-28
School: | Penn Treaty High School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | classroom |  | 0 | Yes | 624 | 14 | 14 | House Fan
102 | Administration |  | 0 | Yes | 336 | 7 | 7 | House Fan
102A | classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan
104 | classroom |  | 0 | Yes | 1539 | 34 | 34 | House Fan
105 | classroom |  | 0 | Yes | 594 | 13 | 13 | House Fan
106 | classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan
107 | classroom |  | 0 | Yes | 920 | 20 | 20 | House Fan
108 | Administration |  | 0 | Yes | 780 | 17 | 17 | House Fan
109 | classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan
110 | classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan
110A | classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan
111 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan
115 | Auditorium |  | 0 |  | 3594 | 81 | 0 | House Fan
H11A | Main office |  | 0 |  | 560 | 12 | 0 | House Fan
H11b | Main office |  | 0 |  | 576 | 13 | 0 | House Fan
H12 | Main office |  | 0 |  | 1150 | 26 | 0 | House Fan
H13 | Main office |  | 0 |  | 792 | 18 | 0 | House Fan
H13a | Main office |  | 0 |  | 312 | 7 | 0 | House Fan
H13b | Main office |  | 0 |  | 814 | 18 | 0 | House Fan
H13c | Main office |  | 0 |  | 275 | 6 | 0 | House Fan
H13d | Main office |  | 0 |  | 1150 | 26 | 0 | House Fan
201 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan
202 | classroom |  | 0 |  | 690 | 15 | 0 | House Fan
203 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan
203A | classroom |  | 0 |  | 253 | 5 | 0 | House Fan
204 | classroom |  | 0 |  | 130 | 2 | 0 | House Fan
204A | classroom |  | 0 |  | 552 | 12 | 0 | House Fan
205 | Nurse |  | 0 | Yes | 325 | 7 | 7 | House Fan
207 | Main office |  | 0 | Yes | 667 | 15 | 15 | House Fan
207A | Speech |  | 0 | Yes | 70 | 1 | 1 | House Fan
207B | Office |  | 0 |  | 120 | 2 | 0 | House Fan
207D | Principal Office |  | 0 | Yes | 300 | 6 | 6 | House Fan
207G | Conference Room |  | 0 | Yes | 144 | 3 | 3 | House Fan
208 | classroom |  | 0 |  | 1056 | 24 | 0 | House Fan
209 | classroom |  | 0 |  | 1032 | 23 | 0 | House Fan
210 | IMC |  | 0 | Yes | 2352 | 53 | 53 | House Fan
213 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan
214 | classroom |  | 0 |  | 624 | 14 | 0 | House Fan
217 | Auditorium |  | 0 |  | 2304 | 52 | 0 | House Fan
301 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan
301A | Administration |  | 0 |  | 375 | 8 | 0 | House Fan
303 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan
303A | Admin |  | 0 |  | 275 | 6 | 0 | House Fan
304 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan
305 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan
305A | classroom |  | 0 |  | 912 | 20 | 0 | House Fan
307 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan
308 | classroom |  | 0 |  | 672 | 15 | 0 | House Fan
309 | classroom |  | 0 |  | 744 | 16 | 0 | House Fan
310 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan
311 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan
312 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan
313 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan
314 | classroom |  | 0 |  | 624 | 14 | 0 | House Fan
315 | Admin |  | 0 |  | 238 | 5 | 0 | House Fan
316 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan
317 | classroom |  | 0 |  | 672 | 15 | 0 | House Fan
401 | classroom |  | 0 |  | 624 | 14 | 0 | House Fan
402A | Admin |  | 0 |  | 828 | 18 | 0 | House Fan
402 | classroom |  | 0 |  | 322 | 7 | 0 | House Fan
403 | classroom |  | 0 |  | 1032 | 23 | 0 | House Fan
404 | classroom |  | 0 |  | 984 | 22 | 0 | House Fan
405 | classroom |  | 0 |  | 984 | 22 | 0 | House Fan
406 | classroom |  | 0 |  | 984 | 22 | 0 | House Fan
407 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan
408 | classroom |  | 0 |  | 1008 | 22 | 0 | House Fan
409 | classroom |  | 0 |  | 1008 | 22 | 0 | House Fan
410 | classroom |  | 0 |  | 1008 | 22 | 0 | House Fan
412 | Admin |  | 0 |  | 506 | 11 | 0 | House Fan
412A | classroom |  | 0 |  | 768 | 17 | 0 | House Fan
412b | classroom |  | 0 |  | 84 | 1 | 0 | House Fan
412c | Admin |  | 0 |  | 484 | 11 | 0 | House Fan
413 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan
414 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan
415 | Cafe |  | 0 |  | 2200 | 50 | 0 | House Fan
417 | Kitchen |  | 0 | Yes | 455 | 10 | 10 | House Fan
417A | kitchen |  | 0 |  | 700 | 15 | 0 | House Fan
419 | Cafe |  | 0 |  | 2150 | 48 | 0 | House Fan
- | boys gym |  | 0 |  | 4725 | 107 | 0 | House Fan
- | girls gym |  | 0 |  | 4725 | 107 | 0 | House Fan

## Pennell
Sheet Last Modified: | 2021-03-24
School: | Joseph Pennell Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | - | 0 | 0 | Yes | 1152 | 26 | 26 | Univent
2 | - | 0 | 0 | Yes | 1152 | 26 | 26 | Univent
101 | Classroom | 0 | 0 |  | 288 | 6 | 0 | Air Handling Unit
102 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | Air Handling Unit
103 | Classroom | 0 | 0 | Yes | 875 | 19 | 19 | Air Handling Unit
104 | Classroom | 0 | 0 | Yes | 175 | 3 | 3 | Air Handling Unit
104A | Classroom | 0 | 0 |  | 375 | 8 | 0 | Air Handling Unit
104B | Classroom | 0 | 0 |  | 175 | 3 | 0 | Air Handling Unit
104C | Classroom | 0 | 0 |  | 125 | 2 | 0 | Air Handling Unit
105 | Classroom | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit
106 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit
107 | Classroom | 0 | 0 | Yes | 1025 | 23 | 23 | Air Handling Unit
110 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Handling Unit
201 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit
202 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit
203 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit
204 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit
205 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit
206 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit
207 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit
208 | Classroom | 0 | 0 | Yes | 984 | 22 | 22 | Air Handling Unit
209 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit
210 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit
211 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit
301 | Classroom | 0 | 0 |  | 816 | 18 | 0 | Air Handling Unit
302 | Classroom | 0 | 0 |  | 816 | 18 | 0 | Air Handling Unit
303 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit
304 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit
305 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit
306 | Classroom | 0 | 0 | Yes | 875 | 19 | 19 | Air Handling Unit
307 | Classroom | 0 | 0 |  | 816 | 18 | 0 | Air Handling Unit
308 | Classroom | 0 | 0 | Yes | 910 | 20 | 20 | Air Handling Unit
309 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit
310 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit
311 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit
- | Basement Boys Room | 0 | 0 |  | 650 | 14 | 0 | Air Handling Unit
- | Basement Corridor | 0 | 0 |  | 352 | 8 | 0 | Air Handling Unit
- | Gym | 0 | 0 | Yes | 5096 | 115 | 115 | Air Handling Unit
- | Library | 0 | 0 |  | 1593 | 36 | 0 | Air Handling Unit
- | Nurse | 0 | 0 | Yes | 384 | 8 | 8 | Air Handling Unit
- | Counselor Office |  | 0 |  | 384 | 8 | 0
- | Office |  | 0 | Yes | 456 | 10 | 10
- | Principal's Office |  | 0 | Yes | 234 | 5 | 5

## Pennypacker
Sheet Last Modified: | 2021-04-27
School: | Samuel Pennypacker Elementary-Middle School
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B2 | Classroom | 0 | 0 | Yes | 928 | 21 | 21 | House Fan
B3 | Classroom | 923 | 61 |  | 1160 | 26 | 26 | House Fan
B4 | Classroom | 0 | 0 | Yes | 1260 | 28 | 28 | House Fan
B8 | Classroom | 488 | 32 |  | 576 | 13 | 13 | House Fan
B9 | Classroom | 439 | 29 |  | 460 | 10 | 10 | House Fan
B10 | Classroom | 425 | 28 |  | 576 | 13 | 13 | House Fan
101 | Classroom | 545 | 36 |  | 1131 | 25 | 25 | House Fan
102 | Classroom | 440 | 29 |  | 841 | 19 | 19 | House Fan
103 | Classroom | 545 | 36 |  | 870 | 19 | 19 | House Fan
104 | Classroom | 611 | 40 |  | 870 | 19 | 19 | House Fan
105 | Classroom | 340 | 22 |  | 841 | 19 | 19 | House Fan
106 | Classroom | 395 | 26 |  | 841 | 19 | 19 | House Fan
107 | Classroom | 503 | 33 |  | 841 | 19 | 19 | House Fan
108 | Classroom | 650 | 43 |  | 899 | 20 | 20 | House Fan
109 | Classroom | 437 | 29 |  | 841 | 19 | 19 | House Fan
110 | Classroom | 459 | 30 |  | 899 | 20 | 20 | House Fan
201 | Classroom | 351 | 23 |  | 899 | 20 | 20 | House Fan
202 | Classroom | 424 | 28 |  | 841 | 19 | 19 | House Fan
203 | Classroom | 390 | 26 |  | 870 | 19 | 19 | House Fan
204 | Classroom | 338 | 22 |  | 841 | 19 | 19 | House Fan
205 | Classroom | 649 | 43 |  | 841 | 19 | 19 | House Fan
208 | Classroom | 586 | 39 |  | 899 | 20 | 20 | House Fan
209 | Classroom | 508 | 33 |  | 841 | 19 | 19 | House Fan
210 | Classroom | 356 | 23 |  | 899 | 20 | 20 | House Fan
212 | Storage | 0 | 0 |  | 360 | 8 | 0 | House Fan
301 | Classroom | 382 | 25 |  | 899 | 20 | 20 | House Fan
302 | Classroom | 653 | 43 |  | 841 | 19 | 19 | House Fan
303 | Classroom | 355 | 23 |  | 870 | 19 | 19 | House Fan
304 | Classroom | 407 | 27 |  | 841 | 19 | 19 | House Fan
305 | Classroom | 583 | 38 |  | 841 | 19 | 19 | House Fan
306 | Classroom | 554 | 36 |  | 870 | 19 | 19 | House Fan
307 | Classroom | 513 | 34 |  | 841 | 19 | 19 | House Fan
308 | Classroom | 515 | 34 |  | 899 | 20 | 20 | House Fan
309 | Classroom | 676 | 45 |  | 841 | 19 | 19 | House Fan
310 | Classroom | 422 | 28 |  | 899 | 20 | 20 | House Fan
311 | Classroom | 550 | 36 |  | 720 | 16 | 16 | House Fan
312 | Classroom | 0 | 0 | Yes | 138 | 3 | 3 | House Fan
- | Auditorium | 1967 | 131 |  | 4272 | 97 | 97 | House Fan
- | Counselor's Office | 0 | 0 | Yes | 386 | 8 | 8 | House Fan
- | Gym/Café | 0 | 0 | Yes | 3608 | 82 | 82 | House Fan
- | Nurse | 0 | 0 | Yes | 361 | 8 | 8 | House Fan
- | Library | 928 | 61 |  | 1620 | 36 | 36 | House Fan
- | Main Office | 0 | 0 | Yes | 342 | 7 | 7 | House Fan
- | Principals Office | 0 | 0 | Yes | 346 | 7 | 7 | House Fan
- | Teacher's Lounge | 0 | 0 |  | 105 | 2 | 0 | House Fan

## Penrose TB Read
Sheet Last Modified: | 2021-04-23
School: | Penrose Elementary School- Main Building
Main Exhaust Report
School: | Penrose Little School House
| Penrose LSH Exhaust Report | LSH Part 2 and Exhaust | LSH Part 3 and Exhaust
School: | TB Read – former Motivation High School Building
| TB Read Exhaust Report | TB Read Exhaust Retest
Vendor: | Chadwick
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Penrose Main Building
101 | Classroom | 373 | 24 |  | 884 | 20 | 20 | Rooftop Unit
102 | Classroom | 387 | 25 |  | 884 | 20 | 20 | Rooftop Unit
103 | Classroom | 359 | 23 |  | 884 | 20 | 20 | Rooftop Unit
104 | Classroom | 505 | 33 |  | 884 | 20 | 20 | Rooftop Unit
105 | Classroom | 469 | 31 |  | 884 | 20 | 20 | Rooftop Unit
106 | office | 119 | 7 |  | 315 | 7 | 7 | Rooftop Unit
106a | principal | 26 | 1 |  | 72 | 1 | 1 | Rooftop Unit
106b | council | 36 | 2 |  | 176 | 4 | 2 | Rooftop Unit
107 | Classroom | 99 | 6 |  | 884 | 20 | 6 | Rooftop Unit
111 | Classroom | 233 | 15 |  | 884 | 20 | 15 | Rooftop Unit
113 | Classroom | 256 | 17 |  | 884 | 20 | 17 | Rooftop Unit
115 | Classroom | 287 | 19 |  | 884 | 20 | 19 | Rooftop Unit
116 | cafe | 330 | 22 |  | 1794 | 40 | 22 | Rooftop Unit
116 | Classroom | 387 | 25 |  | 884 | 20 | 20 | Rooftop Unit
117 | Classroom | 337 | 22 |  | 884 | 20 | 20 | Rooftop Unit
118 | Classroom | 306 | 20 |  | 884 | 20 | 20 | Rooftop Unit
119 | Classroom | 297 | 19 |  | 884 | 20 | 19 | Rooftop Unit
121 | Classroom | 291 | 19 |  | 884 | 20 | 19 | Rooftop Unit
201 | Classroom | 704 | 46 |  | 884 | 20 | 20 | Rooftop Unit
202 | Classroom | 475 | 31 |  | 884 | 20 | 20 | Rooftop Unit
203 | Classroom | 697 | 46 |  | 884 | 20 | 20 | Rooftop Unit
204 | Classroom | 457 | 30 |  | 884 | 20 | 20 | Rooftop Unit
205 | Classroom | 292 | 19 |  | 884 | 20 | 19 | Rooftop Unit
206 | Classroom | 399 | 26 |  | 496 | 11 | 11 | Rooftop Unit
207 | Classroom | 574 | 38 |  | 884 | 20 | 20 | Rooftop Unit
211 | Classroom | 423 | 28 |  | 884 | 20 | 20 | Rooftop Unit
213 | Classroom | 159 | 10 |  | 884 | 20 | 10 | Rooftop Unit
214 | Classroom | 202 | 13 |  | 884 | 20 | 13 | Rooftop Unit
215 | Classroom | 208 | 13 |  | 884 | 20 | 13 | Rooftop Unit
216 | Classroom | 144 | 9 |  | 884 | 20 | 9 | Rooftop Unit
217 | Classroom | 142 | 9 |  | 884 | 20 | 9 | Rooftop Unit
218 | Classroom | 153 | 10 |  | 1768 | 40 | 10 | Rooftop Unit
219 | Classroom | 131 | 8 |  | 884 | 20 | 8 | Rooftop Unit
221 | Classroom | 151 | 10 |  | 884 | 20 | 10 | Rooftop Unit
Penrose Little School House
1 | Classroom | 289 | 19 |  | 978 | 22 | 19 | Blower Coil Unit
2 | Classroom | 340 | 22 |  | 978 | 22 | 22 | Blower Coil Unit
3 | Classroom | 289 | 19 |  | 978 | 22 | 19 | Blower Coil Unit
4 | Classroom | 340 | 22 |  | 978 | 22 | 22 | Blower Coil Unit
5 | Classroom | 350 | 23 |  | 978 | 22 | 22 | Blower Coil Unit
6 | Classroom | 374 | 24 |  | 978 | 22 | 22 | Blower Coil Unit
7 | Classroom | 374 | 24 |  | 978 | 22 | 22 | Blower Coil Unit
8 | Classroom | 493 | 32 |  | 978 | 22 | 22 | Blower Coil Unit
9 | Classroom | 311 | 20 |  | 978 | 22 | 20 | Blower Coil Unit
10 | Classroom | 493 | 32 |  | 978 | 22 | 22 | Blower Coil Unit
11 | Classroom | 311 | 20 |  | 978 | 22 | 20 | Blower Coil Unit
- | multipurpose | 2960 | 197 |  | 2067 | 46 | 46 | Blower Coil Unit
- | Corridor | 58 | 3 |  | 684 | 15 | 3 | Blower Coil Unit
- | Boy's Restroom | 59 | 3 |  | 200 | 4 | 3 | Blower Coil Unit
- | Girl's Rest Room | 64 | 4 |  | 200 | 4 | 4 | Blower Coil Unit
- | General Office |  | 0 |  | 146 | 3 | 0 | Blower Coil Unit
- | Principal's Office |  | 0 |  | 72 | 1 | 0 | Blower Coil Unit
- | Psychiastrist's Office |  | 0 |  | 72 | 1 | 0 | Blower Coil Unit
TB Read
101 | Classroom | 324 | 21 |  | 792 | 18 | 18 | Heating Ventilation Unit
102 | Classroom | 101 | 6 | Yes | 792 | 18 | 18 | Heating Ventilation Unit
103 | Classroom | 492 | 32 |  | 792 | 18 | 18 | Heating Ventilation Unit
104 | Classroom | 584 | 38 |  | 792 | 18 | 18 | Heating Ventilation Unit
105 | Classroom | 400 | 26 |  | 792 | 18 | 18 | Heating Ventilation Unit
201 | Classroom | 443 | 29 |  | 792 | 18 | 18 | Heating Ventilation Unit
202 | Classroom | 1636 | 109 |  | 792 | 18 | 18 | Heating Ventilation Unit
203 | Classroom | 717 | 47 |  | 792 | 18 | 18 | Heating Ventilation Unit
204 | Classroom | 948 | 63 |  | 792 | 18 | 18 | Heating Ventilation Unit
205 | Classroom | 397 | 26 |  | 792 | 18 | 18 | Heating Ventilation Unit
14 | Computer Lab | 473 | 31 |  | 792 | 18 | 18 | Heating Ventilation Unit
- | Corridor #1 | 795 | 53 |  | 1298 | 29 | 29 | Heating Ventilation Unit
- | Corridor #2 | 413 | 27 |  | 1600 | 36 | 27 | Heating Ventilation Unit
- | GYM | 7270 | 484 |  | 8969 | 203 | 203 | Heating Ventilation Unit
- | Library | 442 | 29 |  | 874 | 19 | 19 | Heating Ventilation Unit

## PLA North CEP
Sheet Last Modified: | 2021-05-03
School: | Philadelphia Learning Academy North/ Camelot Academy East/ Crossroads Academy at Hunting Park (former CEP Hunting Park) Alternative School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
3 | Room (Split Level South) | 25.1 | 1 |  | 86 | 1 | 1 | Rooftop Unit
5 | Room (Split Level South) | 141.2 | 9 |  | 396 | 9 | 9 | Rooftop Unit
005A | Room (Split Level South) | 19.8 | 1 |  | 87 | 1 | 1 | Rooftop Unit
6 | Room | 27 | 1 |  | 83 | 1 | 1 | Rooftop Unit
006A | Room | 13.9 | 0 |  | 80 | 1 | 0 | Rooftop Unit
006B | Room | 13.2 | 0 |  | 79 | 1 | 0 | Rooftop Unit
10 | Room | 6.5 | 0 |  | 84 | 1 | 0 | Rooftop Unit
010A | Room | 53.2 | 3 |  | 80 | 1 | 1 | Rooftop Unit
103 | Room | 19.6 | 1 |  | 87 | 1 | 1 | Rooftop Unit
104 | Room | 19.3 | 1 |  | 85 | 1 | 1 | Rooftop Unit
105 | Room | 27.4 | 1 |  | 81 | 1 | 1 | Rooftop Unit
106 | Room | 22 | 1 |  | 83 | 1 | 1 | Rooftop Unit
108 | Room | 13.8 | 0 |  | 89 | 2 | 0 | Rooftop Unit
109 | Room | 13.3 | 0 |  | 92 | 2 | 0 | Rooftop Unit
110 | Room | 14.9 | 0 |  | 269 | 6 | 0 | Rooftop Unit
113 | Room (Split Level South) | 56.2 | 3 |  | 134 | 3 | 3 | Rooftop Unit
114 | Room (Split Level South) | 26.2 | 1 |  | 136 | 3 | 1 | Rooftop Unit
115 | Room (Split Level South) | 41 | 2 |  | 139 | 3 | 2 | Rooftop Unit
116 | Room (Split Level South) | 25.3 | 1 |  | 139 | 3 | 1 | Rooftop Unit
117 | Room (Split Level South) | 80 | 5 |  | 355 | 8 | 5 | Rooftop Unit
120 | Admin Office | -231 | -15 |  | 92 | 2 | -15 | Rooftop Unit
121 | Admin Office | 145 | 9 |  | 396 | 9 | 9 | Rooftop Unit
122 | Admin Office | 208 | 13 |  | 94 | 2 | 2 | Rooftop Unit
123 | Admin Office | 97 | 6 |  | 92 | 2 | 2 | Rooftop Unit
124 | Admin Office | -65 | -4 |  | 92 | 2 | -4 | Rooftop Unit
126 | Admin Office | 57 | 3 |  | 139 | 3 | 3 | Rooftop Unit
127 | Admin Office | -417 | -27 |  | 95 | 2 | -27 | Rooftop Unit
129 | Admin Office | -65 | -4 |  | 355 | 8 | -4 | Rooftop Unit
130 | Admin Office | -52 | -3 | Yes | 140 | 3 | 3 | Rooftop Unit
133 | Admin Office | 104 | 6 |  | 266 | 6 | 6 | Rooftop Unit
133A | Admin Office | 322 | 21 |  | 927 | 21 | 21 | Rooftop Unit
133B | Admin Office | 316 | 21 |  | 927 | 21 | 21 | Rooftop Unit
134 | Media Room | 195 | 13 |  | 1769 | 40 | 13 | Rooftop Unit
135 | Admin Office | 253 | 16 |  | 709 | 16 | 16 | Rooftop Unit
136 | Media Room | 465 | 31 |  | 407 | 9 | 9 | Rooftop Unit
142 | Admin Office | 339 | 22 |  | 225 | 5 | 5 | Rooftop Unit
147 | AEP Office | 146 | 9 |  | 413 | 9 | 9 | Rooftop Unit
148 | AEP Office | -245 | -16 |  | 92 | 2 | -16 | Rooftop Unit
149 | AEP Office | -104 | -6 |  | 94 | 2 | -6 | Rooftop Unit
150 | AEP Office | -38 | -2 |  | 136 | 3 | -2 | Rooftop Unit
151 | AEP Office | 178 | 11 |  | 179 | 4 | 4 | Rooftop Unit
152 | AEP Office | 10 | 0 |  | 91 | 2 | 0 | Rooftop Unit
153 | AEP Office | 36 | 2 |  | 92 | 2 | 2 | Rooftop Unit
154 | AEP Office | 69 | 4 |  | 96 | 2 | 2 | Rooftop Unit
155 | AEP Office | 179 | 11 |  | 184 | 4 | 4 | Rooftop Unit
156 | AEP Office | -34 | -2 |  | 80 | 1 | -2 | Rooftop Unit
157 | AEP Office | 70 | 4 |  | 79 | 1 | 1 | Rooftop Unit
158 | AEP Office | 119 | 7 |  | 85 | 1 | 1 | Rooftop Unit
159 | AEP Office | 21 | 1 |  | 84 | 1 | 1 | Rooftop Unit
160 | AEP Office | 184 | 12 |  | 142 | 3 | 3 | Rooftop Unit
161 | Library Office | -59 | -3 |  | 91 | 2 | -3 | Rooftop Unit
162 | Library Office | -99 | -6 |  | 269 | 6 | -6 | Rooftop Unit
164 | Main Library | 980 | 65 |  | 973 | 22 | 22 | Rooftop Unit
174 | Office | -270 | -18 |  | 83 | 1 | -18 | Rooftop Unit
175 | Office | 80 | 5 |  | 82 | 1 | 1 | Rooftop Unit
180 | Office | 87 | 5 |  | 93 | 2 | 2 | Rooftop Unit
181 | Office | -31 | -2 |  | 92 | 2 | -2 | Rooftop Unit
182 | Office | 166 | 11 |  | 92 | 2 | 2 | Rooftop Unit
184 | Office | 122 | 8 |  | 93 | 2 | 2 | Rooftop Unit
185 | Office | 27 | 1 |  | 92 | 2 | 1 | Rooftop Unit
186A | Office | -272 | -18 |  | 449 | 10 | -18 | Rooftop Unit
186B | Office | -47 | -3 |  | 449 | 10 | -3 | Rooftop Unit
187 | Office | -182 | -12 |  | 94 | 2 | -12 | Rooftop Unit
188 | Office | 100 | 6 |  | 92 | 2 | 2 | Rooftop Unit
189 | Office | 78 | 5 |  | 227 | 5 | 5 | Rooftop Unit
192 | Office | -269 | -17 |  | 72 | 1 | -17 | Rooftop Unit
193 | Office | 283 | 18 |  | 82 | 1 | 1 | Rooftop Unit
194 | Office | 106 | 7 |  | 48 | 1 | 1 | Rooftop Unit
195 | Office | 78 | 5 |  | 232 | 5 | 5 | Rooftop Unit
196 | Classroom | 190 | 12 |  | 528 | 12 | 12 | Rooftop Unit
201 | Classroom | 248 | 16 |  | 712 | 16 | 16 | Rooftop Unit
204 | Electrical Closet | 13 | 0 |  | 80 | 1 | 0 | Rooftop Unit
205 | IT Room | -3 | 0 |  | 84 | 1 | 0 | Rooftop Unit
207 | Closet | 0 | 0 |  | 136 | 3 | 0 | Rooftop Unit
210 | Office | -127 | -8 |  | 96 | 2 | -8 | Rooftop Unit
211 | Office | -20 | -1 |  | 94 | 2 | -1 | Rooftop Unit
212 | Office | 0 | 0 |  | 96 | 2 | 0 | Rooftop Unit
213 | Room |  | 0 | Yes | 880 | 20 | 20
213A | Office | 63 | 4 |  | 180 | 4 | 4 | Rooftop Unit
213B | Office | 284 | 18 |  | 792 | 18 | 18 | Rooftop Unit
214 | Office | -12 | 0 |  | 89 | 2 | 0 | Rooftop Unit
215 | Office | 0 | 0 |  | 92 | 2 | 0 | Rooftop Unit
217 | Office | -31 | -2 |  | 96 | 2 | -2 | Rooftop Unit
218 | Office | -23 | -1 |  | 86 | 1 | -1 | Rooftop Unit
219 | Office | 0 | 0 |  | 93 | 2 | 0 | Rooftop Unit
221 | IT Room | 13 | 0 |  | 52 | 1 | 0 | Rooftop Unit
222 | Electrical Closet | 195 | 13 |  | 94 | 2 | 2 | Rooftop Unit
223 | Closet | 0 | 0 |  | 55 | 1 | 0 | Rooftop Unit
303 | Room (Split Level South) | 44.8 | 2 |  | 86 | 1 | 1 | Rooftop Unit
304 | Room (Split Level South) | 124.3 | 8 |  | 231 | 5 | 5 | Rooftop Unit
307 | Room (Split Level South) | 118.2 | 7 |  | 312 | 7 | 7 | Rooftop Unit
311 | Room (Split Level South) | 13.3 | 0 |  | 136 | 3 | 0 | Rooftop Unit
311A | Room (Split Level South) | 20 | 1 |  | 63 | 1 | 1 | Rooftop Unit
311B | Room (Split Level South) | 12 | 0 |  | 86 | 1 | 0 | Rooftop Unit
313 | Room | 19.9 | 1 |  | 98 | 2 | 1 | Rooftop Unit
314 | Room | 21.2 | 1 |  | 85 | 1 | 1 | Rooftop Unit
316 | Room | 61.9 | 4 |  | 449 | 10 | 4 | Rooftop Unit
320 | Room | 19.3 | 1 |  | 87 | 1 | 1 | Rooftop Unit
321 | Room | 15.7 | 1 |  | 89 | 2 | 1 | Rooftop Unit
322 | Room | 17.4 | 1 |  | 87 | 1 | 1 | Rooftop Unit
H01 | Room (Split Level South) | 34.4 | 2 |  | 89 | 2 | 2 | Rooftop Unit
H01 | Room | 14.6 | 0 |  | 72 | 1 | 0 | Rooftop Unit
H21 | Room (Split Level South) | 159.2 | 10 |  | 446 | 10 | 10 | Rooftop Unit
H21 | Room | 6.9 | 0 |  | 52 | 1 | 0 | Rooftop Unit
L4/L5 | Room | 83.8 | 5 |  | 225 | 5 | 5 | Rooftop Unit
A1 | Classroom | 594 | 39 | Yes | 794 | 18 | 18 | Rooftop Unit
A2 | Classroom | 876 | 58 |  | 793 | 18 | 18 | Rooftop Unit
A3 | Classroom | 219 | 14 |  | 795 | 18 | 14 | Rooftop Unit
A4 | Classroom | 905 | 60 |  | 796 | 18 | 18 | Rooftop Unit
B1 | Classroom | 430 | 28 |  | 793 | 18 | 18 | Rooftop Unit
B2 | Classroom | 1048 | 69 |  | 792 | 18 | 18 | Rooftop Unit
B3 | Classroom | 84 | 5 |  | 794 | 18 | 5 | Rooftop Unit
B4 | Classroom | 769 | 51 |  | 794 | 18 | 18 | Rooftop Unit
C1 | Classroom | 551 | 36 |  | 797 | 18 | 18 | Rooftop Unit
C2 | Classroom | 927 | 61 |  | 795 | 18 | 18 | Rooftop Unit
C3 | Classroom | 115 | 7 |  | 794 | 18 | 7 | Rooftop Unit
C4 | Classroom | 70 | 4 |  | 795 | 18 | 4 | Rooftop Unit
D1 | Classroom | 587 | 39 |  | 797 | 18 | 18 | Rooftop Unit
D2 | Classroom | 935 | 62 |  | 795 | 18 | 18 | Rooftop Unit
D3 | Classroom | 14 | 0 |  | 793 | 18 | 0 | Rooftop Unit
D4 | Classroom | 617 | 41 |  | 796 | 18 | 18 | Rooftop Unit
E1 | Classroom | 312 | 20 | Yes | 794 | 18 | 18 | Rooftop Unit
E2 | Classroom | 752 | 50 | Yes | 796 | 18 | 18 | Rooftop Unit
E3 | Classroom | 269 | 17 |  | 793 | 18 | 17 | Rooftop Unit
E4 | Classroom | 715 | 47 | Yes | 795 | 18 | 18 | Rooftop Unit
G1 | Classroom | 66 | 4 | Yes | 794 | 18 | 18 | Rooftop Unit
G2 | Classroom | 857 | 57 | Yes | 796 | 18 | 18 | Rooftop Unit
G3 | Classroom | 197 | 13 | Yes | 793 | 18 | 18 | Rooftop Unit
G4 | Classroom | 813 | 54 | Yes | 797 | 18 | 18 | Rooftop Unit
Gym | Recreational Area 1 | 442 | 29 |  | 1276 | 29 | 29 | Rooftop Unit
Gym | Gym Cafeteria | 306 | 20 |  | 886 | 20 | 20 | Rooftop Unit
Gym | Recreational Area 1 | 630 | 42 |  | 1848 | 42 | 42 | Rooftop Unit
Gym | Gym 2A | 716 | 47 |  | 9196 | 209 | 47 | Rooftop Unit
Gym | Gym 2B | 601 | 40 |  | 9196 | 209 | 40 | Rooftop Unit
Gym | Vestibule | 0 | 0 |  | 176 | 4 | 0 | Rooftop Unit
H1 | Classroom | 807 | 53 |  | 796 | 18 | 18 | Rooftop Unit
H17 | Hallway | 91 | 6 |  | 264 | 6 | 6 | Rooftop Unit
H2 | Classroom | 706 | 47 |  | 794 | 18 | 18 | Rooftop Unit
H3 | Classroom | -660 | -44 |  | 793 | 18 | -44 | Rooftop Unit
H4 | Classroom | 11 | 0 |  | 795 | 18 | 0 | Rooftop Unit
Hallway | Hallway (Split Level South) | 47.9 | 3 |  | 136 | 3 | 3 | Rooftop Unit
Hunter | Office | 229 | 15 |  | 664 | 15 | 15 | Rooftop Unit
Hunting Park | Lobby | 1738 | 115 |  | 5069 | 115 | 115 | Rooftop Unit
J | Hallway | 0 | 0 |  | 616 | 14 | 0 | Rooftop Unit
J1 | Classroom | -493 | -32 | Yes | 529 | 12 | 12 | Rooftop Unit
J2 | Classroom | 381 | 25 |  | 792 | 18 | 18 | Rooftop Unit
J3 | Classroom | 493 | 32 |  | 528 | 12 | 12 | Rooftop Unit
J4 | Classroom | 1208 | 80 |  | 528 | 12 | 12 | Rooftop Unit
K | Hallway | 0 | 0 |  | 616 | 14 | 0 | Rooftop Unit
K1 | Classroom | 189 | 12 |  | 792 | 18 | 12 | Rooftop Unit
K2 | Classroom | 682 | 45 |  | 794 | 18 | 18 | Rooftop Unit
K3 | Classroom | 130 | 8 | Yes | 796 | 18 | 18 | Rooftop Unit
K4 | Classroom | 617 | 41 |  | 797 | 18 | 18 | Rooftop Unit
Kitchen | Kitchen | 1953 | 130 |  | 880 | 20 | 20 | Rooftop Unit
Kitchen | Lounge | -3 | 0 |  | 73 | 1 | 0 | Rooftop Unit
L | Hallway | 0 | 0 |  | 704 | 16 | 0 | Rooftop Unit
L1 | Classroom | 79 | 5 | Yes | 794 | 18 | 18 | Rooftop Unit
L2 | Classroom | 636 | 42 |  | 793 | 18 | 18 | Rooftop Unit
L3 | Classroom | 109 | 7 | Yes | 792 | 18 | 18 | Rooftop Unit
L4 | Classroom | 707 | 47 |  | 797 | 18 | 18 | Rooftop Unit
Lobby | Main Lobby North | 147 | 9 |  | 410 | 9 | 9 | Rooftop Unit
M | Hallway | 0 | 0 |  | 704 | 16 | 0 | Rooftop Unit
M1 | Classroom | 226 | 15 |  | 794 | 18 | 15 | Rooftop Unit
M2 | Classroom | 855 | 57 |  | 796 | 18 | 18 | Rooftop Unit
M3 | Classroom | 17 | 1 |  | 793 | 18 | 1 | Rooftop Unit
M4 | Classroom | 684 | 45 |  | 795 | 18 | 18 | Rooftop Unit
Men's Bathroom | Men's Bathroom | 0 | 0 |  | 132 | 3 | 0 | Rooftop Unit
MS0S1 | Office | 432 | 28 |  | 528 | 12 | 12 | Rooftop Unit
MS0S2 | Office | 1153 | 76 |  | 880 | 20 | 20 | Rooftop Unit
MS2 | MS2 (Woodshop) | 480 | 32 |  | 1408 | 32 | 32 | Rooftop Unit
MS2 | MS2 (Woodshop) | 768 | 51 |  | 1408 | 32 | 32 | Rooftop Unit
MS6 | Office | 107 | 7 |  | 176 | 4 | 4 | Rooftop Unit
MS7 | Office | 0 | 0 |  | 132 | 3 | 0 | Rooftop Unit
N1 | Classroom | 612 | 40 |  | 794 | 18 | 18 | Rooftop Unit
N2 | Classroom (with office) | 100 | 6 |  | 796 | 18 | 6 | Rooftop Unit
N3 | Classroom (with office) | 1490 | 99 |  | 795 | 18 | 18 | Rooftop Unit
N4 | Classroom | 781 | 52 |  | 796 | 18 | 18 | Rooftop Unit
Office | Office | 12 | 0 |  | 132 | 3 | 0 | Rooftop Unit
S11 | AEP Office | -244 | -16 |  | 396 | 9 | -16 | Rooftop Unit
- | Staff Lounge | 242.6 | 16 |  | 528 | 12 | 12 | Rooftop Unit
- | Women's Bathroom | 0 | 0 |  | 132 | 3 | 0 | Rooftop Unit

## Pollock
Sheet Last Modified: | 2021-04-23
School: | Robert B. Pollock Elementary School
Vendor: | EMCORE Fluidics | Retest Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 313 | 20 |  | 945 | 21 | 20 | Perimeter Heater
2 | Classroom | 385 | 25 |  | 945 | 21 | 21 | Perimeter Heater
3 | Classroom | 141 | 9 | Yes | 945 | 21 | 21 | Perimeter Heater
4 | Classroom | 406 | 27 |  | 945 | 21 | 21 | Perimeter Heater
5 | Classroom | 222 | 14 | Yes | 945 | 21 | 21 | Perimeter Heater
6 | Classroom | 278 | 18 |  | 720 | 16 | 16 | Perimeter Heater
7 | Classroom | 270 | 18 |  | 945 | 21 | 18 | Perimeter Heater
8 | Classroom | 329 | 21 |  | 945 | 21 | 21 | Perimeter Heater
9 | Classroom | 301 | 20 |  | 945 | 21 | 20 | Perimeter Heater
10 | Classroom | 482 | 32 |  | 945 | 21 | 21 | Perimeter Heater
11 | Classroom | 0 | 0 | Yes | 945 | 21 | 21 | Perimeter Heater
12 | Classroom | 369 | 24 |  | 945 | 21 | 21 | Perimeter Heater
13 | Classroom | 282 | 18 |  | 945 | 21 | 18 | Perimeter Heater
14 | Classroom | 338 | 22 |  | 945 | 21 | 21 | Perimeter Heater
15 | Classroom | 275 | 18 |  | 945 | 21 | 18 | Perimeter Heater
16 | Classroom | 311 | 20 |  | 840 | 19 | 19 | Perimeter Heater
17 | Classroom | 294 | 19 |  | 945 | 21 | 19 | Perimeter Heater
101 | Classroom | 505 | 33 |  | 1450 | 32 | 32 | Perimeter Heater
102 | Classroom | 280 | 18 |  | 945 | 21 | 18 | Perimeter Heater
103 | Classroom | 305 | 20 |  | 945 | 21 | 20 | Perimeter Heater
104 | Classroom | 277 | 18 |  | 945 | 21 | 18 | Perimeter Heater
105 | Classroom | 273 | 18 |  | 945 | 21 | 18 | Perimeter Heater
106 | Classroom | 707 | 47 |  | 945 | 21 | 21 | Perimeter Heater
107 | Classroom |  | 0 | Yes | 945 | 21 | 21
108 | Classroom | 315 | 21 |  | 594 | 13 | 13 | Perimeter Heater
110 | Classroom | 301 | 20 | Yes | 945 | 21 | 21 | Perimeter Heater
111 | Classroom | 276 | 18 |  | 480 | 10 | 10 | Perimeter Heater
112 | Classroom | 276 | 18 |  | 945 | 21 | 18 | Perimeter Heater
113 | Classroom | 272 | 18 |  | 945 | 21 | 18 | Perimeter Heater
114 | Classroom | 277 | 18 |  | 945 | 21 | 18 | Perimeter Heater
115 | Classroom | 275 | 18 |  | 945 | 21 | 18 | Perimeter Heater
116 | Classroom | 289 | 19 |  | 945 | 21 | 19 | Perimeter Heater
117A | Classroom | 579 | 38 |  | 1890 | 42 | 38 | Perimeter Heater
118 | Classroom | 323 | 21 |  | 945 | 21 | 21 | Perimeter Heater
- | Main Office |  | 0 | Yes | 674 | 15 | 15
- | Principals Office |  | 0 | Yes | 96 | 2 | 2
- | Nurses Office |  | 0 | Yes | 96 | 2 | 2
- | Office |  | 0 | Yes | 108 | 2 | 2
- | Auditorium | 5528 | 368 |  | 4240 | 96 | 96 | Air Handling Unit
- | Cafeteria | 5093 | 339 |  | 4032 | 91 | 91 | Air Handling Unit
- | Confrence Room | 275 | 18 |  | 374 | 8 | 8 | Perimeter Heater
- | Gym | 3930 | 262 |  | 3901 | 88 | 88 | Air Handling Unit
- | Kindergarten Classroom | 438 | 29 |  | 1450 | 32 | 29 | Perimeter Heater
- | First Flr Office | 0 | 0 |  | 674 | 15 | 0 | Perimeter Heater
- | P1 Bungalow Building | 527 | 35 |  | 1248 | 28 | 28 | Perimeter Heater
- | P2 Bungalow Building | 298 | 19 |  | 806 | 18 | 18 | Perimeter Heater
- | P3 Bungalow Building | 385 | 25 |  | 1040 | 23 | 23 | Perimeter Heater

## Potter-Thomas
Sheet Last Modified: | 2021-04-21
School: | Potter Thomas Promise Academy Elementary School
Vendor: | Goldner | Retest
Devine 2nd Retest 2-15-21
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 322 | 21 |  | 1350 | 30 | 21 | Univent
102 | Classroom | 387 | 25 |  | 1590 | 36 | 25 | Univent
103 | Classroom | 374 | 24 |  | 1590 | 36 | 24 | Univent
104 | Classroom | 817 | 54 |  | 1590 | 36 | 36 | Univent
105 | Classroom | 296 | 19 |  | 1024 | 23 | 19 | Univent
106 | Music Room | 216 | 14 |  | 754 | 17 | 14 | Univent
106 | Computer Lab | 149 | 9 | Yes | 1989 | 45 | 45 | Univent
201 | Classroom | 245 | 16 |  | 812 | 18 | 16 | Univent
202 | Classroom | 275 | 18 |  | 870 | 19 | 18 | Univent
203 | Classroom | 329 | 21 |  | 870 | 19 | 19 | Univent
204 | Classroom | 350 | 23 |  | 870 | 19 | 19 | Univent
205 | Classroom | 356 | 23 |  | 870 | 19 | 19 | Univent
206 | Classroom | 338 | 22 |  | 783 | 17 | 17 | Univent
207 | Classroom | 469 | 31 |  | 841 | 19 | 19 | Univent
208 | Classroom | 397 | 26 |  | 870 | 19 | 19 | Univent
209 | Classroom | 257 | 17 |  | 870 | 19 | 17 | Univent
210 | Classroom | 368 | 24 |  | 870 | 19 | 19 | Univent
211 | Classroom | 348 | 23 |  | 870 | 19 | 19 | Univent
212 | Classroom | 291 | 19 |  | 870 | 19 | 19 | Univent
213 | Classroom | 280 | 18 |  | 870 | 19 | 18 | Univent
214 | Classroom | 319 | 21 |  | 870 | 19 | 19 | Univent
215 | Classroom | 297 | 19 |  | 870 | 19 | 19 | Univent
216 | Classroom | 286 | 19 |  | 870 | 19 | 19 | Univent
217 | Classroom | 392 | 26 |  | 896 | 20 | 20 | Univent
218 | Classroom | 296 | 19 |  | 870 | 19 | 19 | Univent
219 | Classroom | 307 | 20 |  | 870 | 19 | 19 | Univent
220 | Classroom | 235 | 15 |  | 870 | 19 | 15 | Univent
221 | Classroom | 293 | 19 |  | 870 | 19 | 19 | Univent
222 | Classroom | 312 | 20 |  | 783 | 17 | 17 | Univent
223 | Classroom | 238 | 15 |  | 870 | 19 | 15 | Univent
224 | Classroom | 300 | 20 |  | 870 | 19 | 19 | Univent
226 | Classroom | 365 | 24 |  | 942 | 21 | 21 | Univent
226A | - |  | 0 | Yes | 269 | 6 | 6
228 | Classroom | 364 | 24 |  | 942 | 21 | 21 | Univent
228A | - |  | 0 | Yes | 269 | 6 | 6
- | Art room | 642 | 42 |  | 1800 | 40 | 40 | Univent
| Art Room B |  | 0 |  | 260 | 5 | 0
- | Cafeteria/Theatre | 0 | 0 | Yes | 5280 | 120 | 120 | Air Handling Unit
| ESOL Suite |  | 0 | Yes | 119 | 2 | 2
- | Community Room | 239 | 15 |  | 839 | 19 | 15 | Univent
- | Gym | 0 | 0 |  | 5016 | 114 | 0 | Air Handling Unit
- | Gym Offices | 0 | 0 | Yes | 200 | 4 | 4 | Air Handling Unit
- | Kitchen | 273 | 18 |  | 1332 | 30 | 18 | Air Handling Unit
- | Library | 5562 | 370 |  | 1944 | 44 | 44 | Air Handling Unit
Counselor | Office |  | 0 | Yes | 261 | 5 | 5
- | Main Office | 1418 | 94 |  | 1800 | 40 | 40 | Air Handling Unit
- | Faculty lounge |  | 0 |  | 840 | 19 | 0

## Powel
Sheet Last Modified: | 2021-04-29
School: | Powel/SLAMS Elementary School
Vendor: | Capital Retest 3-31-2021
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Report Classroom ID / Area ID Number | Posted Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
026 | 026 | Electrical room |  | 0 |  | 502 | 11 | 0 | Fan Coil Unit
021 | 021 | Lockers | 98 | 6 |  | 114 | 2 | 2 | Fan Coil Unit
023 | 023 | Lockers | 101 | 6 |  | 149 | 3 | 3 | Fan Coil Unit
017 | 017 | Storage | 203 | 13 |  | 330 | 7 | 7 | Fan Coil Unit
018 | 018 | Workshop | 362 | 24 |  | 305 | 6 | 6 | Fan Coil Unit
103 | 101 | Cafeteria | 3580 | 238 |  | 3579 | 81 | 81 | Rooftop Unit
104 | - | Corridor | 498 | 33 |  | 977 | 22 | 22 | Fan Coil Unit
105 | 100 | Waiting Area | 241 | 16 |  | 404 | 9 | 9 | Fan Coil Unit
112 | 100A | Conselor's Office | 15 | 1 |  | 104 | 2 | 1 | Fan Coil Unit
113 | 100G | Office | 16 | 1 |  | 123 | 2 | 1 | Fan Coil Unit
114 | 100B | Dean's Office | 16 | 1 |  | 104 | 2 | 1 | Fan Coil Unit
115 | 100F | Records | 14 | 0 |  | 101 | 2 | 0 | Fan Coil Unit
115 | - | Open Office Space | 29 | 1 |  | 332 | 7 | 1 | Fan Coil Unit
116 | 100C | Principal's Office | 30 | 2 |  | 166 | 3 | 2 | Fan Coil Unit
118 | 100D | Conference Room | 67 | 4 |  | 186 | 4 | 4 | Fan Coil Unit
119 | 101F | Kitchen Storage | 36 | 2 |  | 152 | 3 | 2 | Rooftop Unit
121 | 101E | Kitchen | 535 | 35 |  | 841 | 19 | 19 | Rooftop Unit
123 | - | Servery | 270 | 18 |  | 486 | 11 | 11 | Rooftop Unit
124 | 101B | Office | 33 | 2 |  | 91 | 2 | 2 | Rooftop Unit
126 | - | Corridor | 251 | 16 |  | 2146 | 48 | 16 | Fan Coil Unit
127 | 102 | Kindergarten Classroom | 314 | 20 |  | 1023 | 23 | 20 | Fan Coil Unit
128 | 103 | Classroom | 302 | 20 |  | 853 | 19 | 19 | Fan Coil Unit
129 | 104 | Kindergarten Classroom | 317 | 21 |  | 1022 | 23 | 21 | Fan Coil Unit
130 | 105 | Classroom | 318 | 21 |  | 851 | 19 | 19 | Fan Coil Unit
131 | 106 | Kindergarten Classroom | 321 | 21 |  | 1022 | 23 | 21 | Fan Coil Unit
132 | 107 | Classroom | 322 | 21 |  | 853 | 19 | 19 | Fan Coil Unit
133 | 108 | Special Education Classroom | 147 | 9 |  | 378 | 8 | 8 | Fan Coil Unit
134 | 109 | Classroom | 314 | 20 |  | 853 | 19 | 19 | Fan Coil Unit
135 | 110 | Classroom | 326 | 21 |  | 852 | 19 | 19 | Fan Coil Unit
136 | 111 | Classroom | 322 | 21 |  | 853 | 19 | 19 | Fan Coil Unit
137 | 112 | Classroom | 323 | 21 |  | 842 | 19 | 19 | Fan Coil Unit
138 | 113 | Classroom | 310 | 20 |  | 842 | 19 | 19 | Fan Coil Unit
139 | 114 | Classroom | 317 | 21 |  | 844 | 19 | 19 | Fan Coil Unit
140 | 115 | Classroom | 318 | 21 |  | 844 | 19 | 19 | Fan Coil Unit
141 | 116 | Classroom | 325 | 21 |  | 851 | 19 | 19 | Fan Coil Unit
142 | 117 | Classroom | 313 | 20 |  | 853 | 19 | 19 | Fan Coil Unit
143 | 118 | Special Education Classroom | 151 | 10 |  | 388 | 8 | 8 | Fan Coil Unit
145 | 119 | Library | 546 | 36 |  | 1712 | 38 | 36 | Fan Coil Unit
146 | 119B | Conference Room | 32 | 2 |  | 261 | 5 | 2 | Fan Coil Unit
147 | 119A | Work Room | 19 | 1 |  | 270 | 6 | 1 | Fan Coil Unit
148 | 120/121 | Art Classroom | 379 | 25 |  | 956 | 21 | 21 | Fan Coil Unit
149 | 120A | Art Storage Room | 50 | 3 |  | 61 | 1 | 1 | Fan Coil Unit
150 | 121/123 | Music Classroom | 200 | 13 |  | 1083 | 24 | 13 | Fan Coil Unit
152 | 123A | Music Studio | 53 | 3 |  | 237 | 5 | 3 | Fan Coil Unit
161 | - | Lobby | 208 | 13 |  | 475 | 10 | 10 | Fan Coil Unit
162 | 122 | Gym | 4453 | 296 |  | 5236 | 119 | 119 | Rooftop Unit
163 | 125A | Office | 55 | 3 |  | 161 | 3 | 3 | Rooftop Unit
164 | 125B | Storage | 35 | 2 |  | 141 | 3 | 2 | Rooftop Unit
167 | - | Small Group | 1288 | 85 |  | 963 | 21 | 21 | Fan Coil Unit
168 | - | Open Space/Corridor | 196 | 13 |  | 324 | 7 | 7 | Fan Coil Unit
201 | - | Corridor | 472 | 31 |  | 563 | 12 | 12 | Fan Coil Unit
212 | 200A | Conselor's Office | 22 | 1 |  | 104 | 2 | 1 | Fan Coil Unit
214 | 200B | Principal's Office | 33 | 2 |  | 166 | 3 | 2 | Fan Coil Unit
216 | 200C | Conference Room | 65 | 4 |  | 189 | 4 | 4 | Fan Coil Unit
217 | 200D | Small Meeting Room | 20 | 1 |  | 96 | 2 | 1 | Fan Coil Unit
218 | 200E | Small Meeting Room | 20 | 1 |  | 96 | 2 | 1 | Fan Coil Unit
219 | 200F | Records | 8 | 0 |  | 180 | 4 | 0 | Fan Coil Unit
202 | 201 | Nurse's Suite | 23 | 1 |  | 221 | 5 | 1 | Fan Coil Unit
203 | 201D | Exam Room | 12 | 0 |  | 81 | 1 | 0 | Fan Coil Unit
204 | 201A | Exam Room | 13 | 0 |  | 102 | 2 | 0 | Fan Coil Unit
205 | 200 | Waiting Area | 161 | 10 |  | 359 | 8 | 8 | Fan Coil Unit
213 | 201E | Building Storage | 44 | 2 |  | 494 | 11 | 2 | Fan Coil Unit
215 | - | Open Office | 121 | 8 |  | 1263 | 28 | 8 | Fan Coil Unit
220 | - | Corridor | 11 | 0 |  | 266 | 6 | 0 | Fan Coil Unit
221 | 201H | Faculty Lounge | 126 | 8 |  | 419 | 9 | 8 | Fan Coil Unit
226 | - | Corridor | 233 | 15 |  | 3096 | 70 | 15 | Fan Coil Unit
227 | 202 | Classroom | 421 | 28 |  | 858 | 19 | 19 | Fan Coil Unit
228 | 203 | Classroom | 446 | 29 |  | 860 | 19 | 19 | Fan Coil Unit
229 | 204 | Classroom | 427 | 28 |  | 856 | 19 | 19 | Fan Coil Unit
230 | 205 | Classroom | 416 | 27 |  | 858 | 19 | 19 | Fan Coil Unit
231 | 206 | Classroom | 426 | 28 |  | 858 | 19 | 19 | Fan Coil Unit
232 | 207 | Classroom | 417 | 27 |  | 860 | 19 | 19 | Fan Coil Unit
233 | 208 | Special Education Classroom | 195 | 13 |  | 377 | 8 | 8 | Fan Coil Unit
234 | 209 | Classroom | 438 | 29 |  | 860 | 19 | 19 | Fan Coil Unit
235 | 210 | Art Classroom | 494 | 32 |  | 1235 | 28 | 28 | Fan Coil Unit
237 | 210A | Storage | 18 | 1 |  | 48 | 1 | 1 | Fan Coil Unit
239 | 210B | Storage | 33 | 2 |  | 113 | 2 | 2 | Fan Coil Unit
236 | 211 | Classroom | 435 | 29 |  | 860 | 19 | 19 | Fan Coil Unit
241 | 212 | Classroom | 450 | 30 |  | 852 | 19 | 19 | Fan Coil Unit
238 | 213 | Classroom | 425 | 28 |  | 851 | 19 | 19 | Fan Coil Unit
243 | 214 | Classroom | 447 | 29 |  | 859 | 19 | 19 | Fan Coil Unit
240 | 215 | Classroom | 456 | 30 |  | 852 | 19 | 19 | Fan Coil Unit
244 | 216 | Small Group Classroom | 119 | 7 |  | 388 | 8 | 7 | Fan Coil Unit
242 | 217 | Pre-Eng. Classroom | 417 | 27 |  | 860 | 19 | 19 | Fan Coil Unit
245 | 219 | Makerspace | 677 | 45 |  | 165 | 3 | 3 | Fan Coil Unit
248 | 220 | Science Classroom | 1385 | 92 |  | 1289 | 29 | 29 | Fan Coil Unit
249 | 220B | Prep Room | 739 | 49 |  | 403 | 9 | 9 | Fan Coil Unit
250 | 221 | Classroom | 1356 | 90 |  | 1285 | 29 | 29 | Fan Coil Unit
256 | 221C | Storage | 0 | 0 |  | 50 | 1 | 0 | Fan Coil Unit
253 | 221C | Room | 489 | 32 |  | 632 | 14 | 14 | Fan Coil Unit
254 | 225 | Office | 50 | 3 |  | 173 | 3 | 3 | Rooftop Unit
266 | - | West Hallway | 208 | 13 |  | 779 | 17 | 13 | Fan Coil Unit

## Pratt
Sheet Last Modified: | 2021-03-31
School: | Anna B. Pratt Elementary School
Vendor: | Capital | Devine ABR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
106 | Classroom / Swing Space | 597 | 39 |  | 936 | 21 | 21 | Univent
109 | Classroom | 651 | 43 |  | 936 | 21 | 21 | Univent
110 | Classroom | 327 | 21 |  | 936 | 21 | 21 | Univent
111 | Classroom | 320 | 21 |  | 936 | 21 | 21 | Univent
112 | Classroom | 393 | 26 |  | 936 | 21 | 21 | Univent
113 | Special Education | 453 | 30 |  | 936 | 21 | 21 | Univent
114 | Classroom | 442 | 29 |  | 936 | 21 | 21 | Univent
201 | Classroom / Swing Space | 473 | 31 |  | 936 | 21 | 21 | Univent
200 / 202 | Library | 776 | 51 |  | 1848 | 42 | 42 | Univent
208 | Classroom | 367 | 24 |  | 936 | 21 | 21 | Univent
209 | Classroom | 489 | 32 |  | 936 | 21 | 21 | Univent
210 | Technology Classroom | 422 | 28 |  | 936 | 21 | 21 | Univent
211 | Classroom | 313 | 20 |  | 936 | 21 | 20 | Univent
212 | Classroom | 526 | 35 |  | 936 | 21 | 21 | Univent
213 | Classroom | 468 | 31 |  | 936 | 21 | 21 | Univent
214 | Data Room | 433 | 28 |  | 399 | 9 | 9 | Univent
301 | Music Room | 327 | 21 |  | 936 | 21 | 21 | Univent
302 | Classroom | 311 | 20 |  | 936 | 21 | 20 | Univent
308 | Classroom | 386 | 25 |  | 936 | 21 | 21 | Univent
309 | Special Education | 459 | 30 |  | 936 | 21 | 21 | Univent
310 | Special Education | 447 | 29 |  | 936 | 21 | 21 | Univent
311 | Classroom | 430 | 28 |  | 936 | 21 | 21 | Univent
312 | Classroom | 615 | 41 |  | 936 | 21 | 21 | Univent
313 | Classroom | 330 | 22 |  | 936 | 21 | 21 | Univent
314 | Classroom | 522 | 34 |  | 936 | 21 | 21 | Univent
315 | Staff Room | 361 | 24 |  | 399 | 9 | 9 | Univent
- | Main Office |  | 0 | Yes | 352 | 8 | 8
- | Principal Office |  | 0 | Yes | 228 | 5 | 5
- | AS Office |  | 0 | Yes | 192 | 4 | 4
- | Nurses Office |  | 0 | Yes | 156 | 3 | 3
- | Climate Office |  | 0 | Yes | 156 | 3 | 3
- | Counselors Office |  | 0 | Yes | 156 | 3 | 3

## Prince Hall
Sheet Last Modified: | 2021-04-23
School: | Prince Hall Elementary School
Vendor: | Devine Brothers | Retest | Gymnasium
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 380 | 25 |  | 1200 | 27 | 25 | Univent
2 | Classroom | 321 | 21 |  | 1200 | 27 | 21 | Univent
3 | Classroom | 387 | 25 |  | 1200 | 27 | 25 | Univent
4 | Classroom | 304 | 20 |  | 1200 | 27 | 20 | Univent
5 | Classroom | 313 | 20 |  | 900 | 20 | 20 | Univent
6 | Classroom | 268 | 17 | Yes | 900 | 20 | 20 | Univent
7 | Classroom | 351 | 23 |  | 836 | 19 | 19 | Univent
8 | Classroom | 334 | 22 |  | 874 | 19 | 19 | Univent
9 | Classroom | 235 | 15 | Yes | 1050 | 23 | 23 | Univent
10 | Classroom | 375 | 25 |  | 888 | 20 | 20 | Univent
11 | Classroom | 242 | 16 | Yes | 1066 | 24 | 24 | Univent
12 | Classroom | 234 | 15 | Yes | 1134 | 25 | 25 | Univent
13 | Classroom | 227 | 15 | Yes | 1100 | 25 | 25 | Univent
103 | Classroom | 601 | 40 |  | 1280 | 29 | 29 | Univent
104 | Classroom | 696 | 46 |  | 1280 | 29 | 29 | Univent
105 | Classroom | 664 | 44 |  | 1360 | 30 | 30 | Univent
106 | Classroom | 739 | 49 |  | 1280 | 29 | 29 | Univent
112 | Classroom |  | 0 | Yes | 1360 | 30 | 30
116 | Classroom | 279 | 18 |  | 400 | 9 | 9 | Univent
117 | Classroom | 322 | 21 |  | 700 | 15 | 15 | Univent
201 | Classroom | 418 | 27 |  | 1200 | 27 | 27 | Univent
202 | Classroom | 292 | 19 | Yes | 1200 | 27 | 27 | Univent
203 | Classroom | 311 | 20 |  | 1200 | 27 | 20 | Univent
204 | Classroom | 259 | 17 | Yes | 1200 | 27 | 27 | Univent
205 | Classroom | 377 | 25 |  | 900 | 20 | 20 | Univent
206 | Classroom | 338 | 22 |  | 900 | 20 | 20 | Univent
207 | Classroom | 238 | 15 |  | 836 | 19 | 15 | Univent
208 | Classroom | 312 | 20 |  | 874 | 19 | 19 | Univent
209 | Classroom | 244 | 16 | Yes | 1050 | 23 | 23 | Univent
210 | Classroom | 240 | 16 |  | 888 | 20 | 16 | Univent
211 | Classroom | 263 | 17 |  | 1066 | 24 | 17 | Univent
212 | Classroom | 332 | 22 |  | 1170 | 26 | 22 | Univent
213 | Classroom | 614 | 40 |  | 988 | 22 | 22 | Univent
- | AUDITORIUM | 1185 | 79 |  | 3363 | 76 | 76 | Air Handling Unit
- | Admin. Main Office | 56 | 3 |  | 255 | 5 | 3 | Univent
- | Admin. Office | 28 | 1 |  | 126 | 2 | 1 | Univent
- | Main Office | 301 | 20 |  | 720 | 16 | 16 | Univent
- | Principal's Office |  | 0 | Yes | 255 | 5 | 5
- | Copy Room Office | 16 | 1 |  | 98 | 2 | 1 | Univent
- | Counselor's Office | 107 | 7 |  | 416 | 9 | 7 | Univent
- | Computer Room Classroom | 380 | 25 |  | 1600 | 36 | 25 | Univent
- | IMC Classroom | 1021 | 68 |  | 4335 | 98 | 68 | Univent
- | Gym | 0 | 0 |  | 4800 | 109 | 0 | Air Handling Unit
- | Gym Locker Rooms | 335 | 22 |  | 403 | 9 | 9 | Air Handling Unit
- | Main Entrance | 68 | 4 |  | 150 | 3 | 3 | Univent
- | Multi-Purpose/Cafe | 2016 | 134 |  | 2760 | 62 | 62 | Air Handling Unit
- | Nurse's Office 1 | 50 | 3 |  | 90 | 2 | 2 | Univent
- | Nurse's Office 2 | 40 | 2 |  | 110 | 2 | 2 | Univent
- | Nurse's Office | 71 | 4 | Yes | 160 | 3 | 3 | Univent

## Randolph
Sheet Last Modified: | 2021-03-18
School: | A. Philip Randolph Career and Technical High School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
20 | Classroom | 1172 | 78 |  |  | 0 | 0 | Air Coil Unit
21 | Classroom | 1124 | 74 |  | 600 | 13 | 13 | Air Coil Unit
23 | Classroom | 1177 | 78 |  | 720 | 16 | 16 | Air Coil Unit
24 | Classroom | 889 | 59 |  | 792 | 18 | 18 | Air Coil Unit
36 | Classroom | 93 | 6 |  |  | 0 | 0 | Rooftop Unit
37 | Classroom | 176 | 11 |  | 704 | 16 | 11 | Rooftop Unit
38 | DENTAL SHOP | 236 | 15 |  | 1596 | 36 | 15 | Rooftop Unit
38 | DENTAL IMAGE ROOM | 8 | 0 |  |  | 0 | 0 | Rooftop Unit
38 | DENTAL X-RAY ROOM | 12 | 0 |  |  | 0 | 0 | Rooftop Unit
39 | Classroom | 73 | 4 |  |  | 0 | 0 | Rooftop Unit
50 | Art Room | 694 | 46 |  | 1008 | 22 | 22 | Air Coil Unit
51 | Classroom | 199 | 13 |  | 510 | 11 | 11 | Air Coil Unit
52 | Classroom | 435 | 29 |  | 420 | 9 | 9 | Air Coil Unit
53 | Classroom | 483 | 32 |  | 612 | 13 | 13 | Air Coil Unit
54 | Classroom | 784 | 52 |  | 798 | 18 | 18 | Air Coil Unit
55 | Classroom | 149 | 9 |  | 660 | 15 | 9 | Air Coil Unit
56 | Classroom | 570 | 38 |  | 1190 | 27 | 27 | Air Coil Unit
57 | Classroom | 505 | 33 |  | 522 | 11 | 11 | Air Coil Unit
71 | Room | 262 | 17 |  | 480 | 10 | 10 | Air Coil Unit
72 | Room | 289 | 19 |  | 510 | 11 | 11 | Air Coil Unit
73 | Classroom | 0 | 0 |  | 616 | 14 | 0 | Air Coil Unit
74 | Room | 0 | 0 |  | 572 | 13 | 0 | Air Coil Unit
75 | Classroom | 0 | 0 |  | 660 | 15 | 0 | Air Coil Unit
76 | Classroom | 0 | 0 |  | 600 | 13 | 0 | Air Coil Unit
94 | Room | 88 | 5 |  | 72 | 1 | 1 | Air Coil Unit
100 | Classroom | 197 | 13 |  | 396 | 9 | 9 | Air Coil Unit
- | Automotive | 80 | 5 |  |  | 0 | 0 | Air Coil Unit
- | AV storage | 96 | 6 |  |  | 0 | 0 | Air Coil Unit
- | BEHAVIORAL THERAPIST OFFICE | 26 | 1 |  |  | 0 | 0 | Rooftop Unit
- | Boys Bathroom | 0 | 0 |  |  | 0 | 0 | Air Coil Unit
- | Break Room | 168 | 11 |  |  | 0 | 0 | Air Coil Unit
- | CAFETERIA | 2027 | 135 |  | 3828 | 87 | 87 | Rooftop Unit
- | Cafeteria | 2027 | 135 |  | 704 | 16 | 16 | Air Coil Unit
- | Classrooms | 392 | 26 |  | 600 | 13 | 13 | Air Coil Unit
- | Classrooms | 5734 | 382 |  | 720 | 16 | 16 | Air Coil Unit
- | Classrooms | 4521 | 301 |  | 792 | 18 | 18 | Air Coil Unit
- | Classrooms | 0 | 0 |  | 572 | 13 | 0 | Air Coil Unit
- | COUNSELORS OFFICE | 19 | 1 |  |  | 0 | 0 | Rooftop Unit
- | Engineers Office | 238 | 15 |  |  | 0 | 0 | Air Coil Unit
- | Girls Bathroom | 0 | 0 |  | 200 | 4 | 0 | Air Coil Unit
- | Hallway | 245 | 16 |  |  | 0 | 0 | Air Coil Unit
- | IMC side area | 657 | 43 |  |  | 0 | 0 | Air Coil Unit
- | IMC area | 118 | 7 |  | 1664 | 37 | 7 | Air Coil Unit
- | INSPECTORS OFFICE | 0 | 0 |  |  | 0 | 0 | Rooftop Unit
- | IT ROOM | 40 | 2 |  |  | 0 | 0 | Rooftop Unit
- | kitchen | 1766 | 117 |  | 722 | 16 | 16 | Air Coil Unit
- | Kitchen | 3575 | 238 |  | 722 | 16 | 16 | Air Coil Unit
- | Kitchen Dining | 93 | 6 |  | 252 | 5 | 5 | Air Coil Unit
- | Library | 29 | 1 |  | 1664 | 37 | 1 | Air Coil Unit
- | MAIL ROOM | 50 | 3 |  | 384 | 8 | 3 | Rooftop Unit
- | MAIN OFFICE | 113 | 7 |  | 134 | 3 | 3 | Rooftop Unit
- | CONFERENCE ROOM | 23 | 1 |  | 247 | 5 | 1 | Rooftop Unit
Main office, classrooms | Main office, classrooms | 1328 | 88 |  | 285 | 6 | 6 | Air Coil Unit
- | Ms. SMALLEY OFFICE | 7 | 0 |  | 120 | 2 | 0 | Rooftop Unit
- | NURSES OFFICE | 156 | 10 |  | 196 | 4 | 4 | Rooftop Unit
- | office next to electrical room | 136 | 9 |  | 140 | 3 | 3 | Air Coil Unit
office diffuser s1 | office | 223 | 14 |  | 140 | 3 | 3 | Air Coil Unit
- | kitchen office | 21 | 1 |  | 320 | 7 | 1 | Air Coil Unit
- | VP office | 0 | 0 |  | 130 | 2 | 0 | Air Coil Unit
office Diffuser S6 | office | 0 | 0 |  | 192 | 4 | 0 | Air Coil Unit
office Diffuser S1 | office | 0 | 0 |  | 320 | 7 | 0 | Air Coil Unit
office diffuser s18 | office | 78 | 5 |  | 120 | 2 | 2 | Air Coil Unit
office diffuser s17 | office | 84 | 5 |  | 308 | 7 | 5 | Air Coil Unit
office diffuser s16 | office | 108 | 7 |  | 280 | 6 | 6 | Air Coil Unit
OFFICE IN BACK OF MAIN OFFICE | OFFICE IN BACK OF MAIN OFFICE | 0 | 0 |  | 110 | 2 | 0 | Rooftop Unit
OFFICE NEXT TO RM 39 | OFFICE NEXT TO RM 39 | 23 | 1 |  | 216 | 4 | 1 | Rooftop Unit
- | Paint shop | 0 | 0 |  | 320 | 7 | 0 | H2-7
- | Paint shop | 0 | 0 |  |  | 0 | 0 | H2-8
PRINCIPLE OFFICE | PRINCIPLE OFFICE | 49 | 3 |  | 16 | 0 | 0 | Rooftop Unit
security | office diffuser s4 | 180 | 12 |  |  | 0 | 0 | Air Coil Unit
- | Shop area | 408 | 27 |  |  | 0 | 0 | H2-5
- | Shop area | 1346 | 89 |  |  | 0 | 0 | H1-4
- | Shop area | 591 | 39 |  |  | 0 | 0 | H1-3
- | Shop area | 450 | 30 |  |  | 0 | 0 | H4-14
- | Shop area | 0 | 0 |  |  | 0 | 0 | H4-13
- | Shop area | 0 | 0 |  |  | 0 | 0 | H4-12
- | Shop area | 0 | 0 |  |  | 0 | 0 | H3-10
- | Shop area | 0 | 0 |  |  | 0 | 0 | H3-11
- | Shop Classrooms | 2065 | 137 |  |  | 0 | 0 | Air Coil Unit
- | SPEECH THERAPIST NEXT TO PRINCIPLE OFFICE | 60 | 4 |  |  | 0 | 0 | Rooftop Unit
- | SPEECH THERAPIST OFFICE | 20 | 1 |  |  | 0 | 0 | Rooftop Unit
storage diffuser s11 | storage | 53 | 3 |  |  | 0 | 0 | Air Coil Unit
storage diffuser s10 | storage | 192 | 12 |  |  | 0 | 0 | Air Coil Unit
storage diffuser s9 | storage | 170 | 11 |  |  | 0 | 0 | Air Coil Unit
storage diffuser s2 | storage | 120 | 8 |  |  | 0 | 0 | Air Coil Unit
storage diffuser s1 | storage | 115 | 7 |  |  | 0 | 0 | Air Coil Unit
storage diffuser S19 | storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit
storage diffuser S17 | storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit
storage diffuser S16 | storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit
Storage Diffuser S5 | Storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit
storage diffuser s6 | storage | 76 | 5 |  |  | 0 | 0 | Air Coil Unit
storage diffuser s4 | storage | 64 | 4 |  |  | 0 | 0 | Air Coil Unit
- | STORAGE ROOM IN MAIN OFFICE | 16 | 1 |  |  | 0 | 0 | Rooftop Unit
teacher lounge diffuser S19 | teachers lounge | 37 | 2 |  | 572 | 13 | 2 | Air Coil Unit
- | TOM MCLAUGHLIN OFFICE | 29 | 1 |  | 572 | 13 | 1 | Rooftop Unit
- | vending machine shop | 0 | 0 |  |  | 0 | 0 | H1-1
- | welding shop | 0 | 0 |  |  | 0 | 0 | H2-9

## Rhawnhurst
Sheet Last Modified: | 2021-04-07
School: | Rhawnhurst Elementary School
Vendor: | Devine | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 301 | 20 |  | 1485 | 33 | 20 | Univent
101 | Classroom | 341 | 22 |  | 1056 | 24 | 22 | Univent
102 | Classroom | 296 | 19 |  | 1056 | 24 | 19 | Univent
102B | Office |  | 0 | Yes | 110 | 2 | 2 | Univent
103 | Classroom | 297 | 19 |  | 1056 | 24 | 19 | Univent
104 | Classroom | 335 | 22 |  | 1056 | 24 | 22 | Univent
105 | Classroom | 307 | 20 |  | 1073 | 24 | 20 | Univent
106 | Classroom | 624 | 41 |  | 1020 | 23 | 23 | Univent
107 | Classroom | 321 | 21 |  | 1056 | 24 | 21 | Univent
108 | Classroom | 313 | 20 |  | 1056 | 24 | 20 | Univent
109 | Classroom | 302 | 20 |  | 1056 | 24 | 20 | Univent
110 | Classroom | 301 | 20 |  | 1056 | 24 | 20 | Univent
200 | Classroom | 520 | 34 |  | 1056 | 24 | 24 | Univent
201 | Classroom | 259 | 17 |  | 1056 | 24 | 17 | Univent
202 | Classroom | 306 | 20 |  | 1056 | 24 | 20 | Univent
203 | Classroom | 586 | 39 |  | 1056 | 24 | 24 | Univent
203A | Office |  | 0 | Yes | 275 | 6 | 6 | Univent
203B | Office |  | 0 | Yes | 198 | 4 | 4 | Univent
204 | Classroom | 452 | 30 |  | 1056 | 24 | 24 | Univent
Annex 301 | Classroom | 246 | 16 |  | 792 | 18 | 16 | Univent
Annex 302 | Classroom | 291 | 19 |  | 792 | 18 | 18 | Univent
Annex 303 | Classroom | 303 | 20 |  | 792 | 18 | 18 | Univent
Annex 304 | Classroom | 198 | 13 | Yes | 792 | 18 | 18 | Univent
Annex 305 | Classroom | 248 | 16 |  | 792 | 18 | 16 | Univent
Annex 306 | Classroom | 216 | 14 | Yes | 792 | 18 | 18 | Univent
- | Main Office |  | 0 | Yes | 240 | 5 | 5 | Univent
Principal | Office |  | 0 | Yes | 264 | 6 | 6 | Univent
- | Nurses Office |  | 0 | Yes | 460 | 10 | 10 | Univent
- | Special Education Office |  | 0 | Yes | 360 | 8 | 8 | Univent
- | Counselor Office |  | 0 | Yes | 241 | 5 | 5 | Univent
- | Auditorium | 2049 | 136 |  | 3431 | 77 | 77 | Air Handling Unit
- | Cafeteria | 362 | 24 |  | 2814 | 63 | 24 | Univent
- | Gym | 116 | 7 |  | 3969 | 90 | 7 | Air Handling Unit
- | Library | 140 | 9 | Yes | 1134 | 25 | 25 | Univent
- | Trailer | 286 | 19 |  | 649 | 14 | 14 | Air Handling Unit
A1 | Annex | 75 | 5 |  | 792 | 18 | 5 | Univent
A2 | Annex | 95 | 6 |  | 792 | 18 | 6 | Univent
A3 | Annex | 54 | 3 |  | 792 | 18 | 3 | Univent
A4 | Annex | 62 | 4 |  | 792 | 18 | 4 | Univent
A5 | Annex | 63 | 4 |  | 792 | 18 | 4 | Univent
A6 | Annex | 70 | 4 |  | 792 | 18 | 4 | Univent

## Rhoads, J
Sheet Last Modified: | 2021-04-15
School: | James Rhoads Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 122 | 8 |  | 552 | 12 | 8 | Univent
102 | Classroom | 87 | 5 | Yes | 968 | 22 | 22 | Univent
104 | Classroom | 136 | 9 | Yes | 968 | 22 | 22 | Univent
200 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
201 | Classroom | 190 | 12 | Yes | 805 | 18 | 18 | Univent
202 | Classroom | 237 | 15 |  | 805 | 18 | 15 | Univent
203 | Classroom | 212 | 14 | Yes | 805 | 18 | 18 | Univent
204 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent
205 | Classroom | 162 | 10 | Yes | 805 | 18 | 18 | Univent
206 | Classroom | 201 | 13 | Yes | 805 | 18 | 18 | Univent
207 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
208 | Classroom | 236 | 15 |  | 805 | 18 | 15 | Univent
209 | Classroom | 174 | 11 | Yes | 805 | 18 | 18 | Univent
210 | Classroom | 212 | 14 |  | 805 | 18 | 14 | Univent
300 | Classroom | 318 | 21 |  | 805 | 18 | 18 | Univent
301 | Classroom | 202 | 13 |  | 805 | 18 | 13 | Univent
302 | Classroom | 197 | 13 |  | 805 | 18 | 13 | Univent
303 | Classroom | 300 | 20 |  | 805 | 18 | 18 | Univent
304 | Classroom | 203 | 13 |  | 805 | 18 | 13 | Univent
305 | Classroom | 205 | 13 |  | 805 | 18 | 13 | Univent
306 | Classroom | 169 | 11 |  | 805 | 18 | 11 | Univent
307 | Classroom | 233 | 15 |  | 805 | 18 | 15 | Univent
308 | Classroom | 201 | 13 |  | 805 | 18 | 13 | Univent
309 | Classroom | 174 | 11 |  | 805 | 18 | 11 | Univent
310 | Classroom | 342 | 22 |  | 805 | 18 | 18 | Univent
400 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
401 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
402 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
403 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
404 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent
405 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent
406 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent
407 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent
408 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
409 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent
410 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
- | Main Office |  | 0 | Yes | 616 | 14 | 14
- | Principal Office |  | 0 | Yes | 300 | 6 | 6
- | Nurse Office |  | 0 | Yes | 120 | 2 | 2
- | Auditorium | 0 | 0 |  | 1800 | 40 | 0 | Air Handling Unit
- | Café/Gym | 0 | 0 |  | 6480 | 147 | 0 | Air Handling Unit
- | IMC | 0 | 0 |  | 897 | 20 | 0 | Univent

## Rhodes, EW
Sheet Last Modified: | 2021-03-08
School: | E. Washington Rhodes Elementary School
Vendor: | Goldner | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | 1ST/2ND FLR A&B POD AREAS | 0 | 0 |  | 1829 | 41 | 0 | Air Handling Unit
- | 1ST/2ND FLR C&D POD AREAS | 0 | 0 |  | 1829 | 41 | 0 | Air Handling Unit
A1 | CLASSROOM | 365 | 24 |  | 850 | 19 | 19 | Univent
A2 | CLASSROOM | 326 | 21 |  | 850 | 19 | 19 | Univent
A3 | CLASSROOM | 0 | 0 |  | 850 | 19 | 0 | Univent
A4 | CLASSROOM | 0 | 0 |  | 1085 | 24 | 0 | Univent
A5 | CLASSROOM | 289 | 19 |  | 720 | 16 | 16 | Univent
A6 | CLASSROOM | 308 | 20 |  | 890 | 20 | 20 | Univent
A7 | CLASSROOM | 0 | 0 |  | 0 | 0 | 0 | Univent
A101 | CLASSROOM | 283 | 18 |  | 850 | 19 | 18 | Univent
A102 | CLASSROOM | 369 | 24 |  | 850 | 19 | 19 | Univent
A103 | CLASSROOM | 279 | 18 |  | 816 | 18 | 18 | Univent
A104 | CLASSROOM | 238 | 15 |  | 1120 | 25 | 15 | Univent
A105 | CLASSROOM | 296 | 19 |  | 744 | 16 | 16 | Univent
A106 | CLASSROOM | 227 | 15 |  | 1100 | 25 | 15 | Univent
B1 | CLASSROOM | 275 | 18 |  | 850 | 19 | 18 | Univent
B2 | CLASSROOM | 308 | 20 |  | 850 | 19 | 19 | Univent
B3 | CLASSROOM | 338 | 22 |  | 850 | 19 | 19 | Univent
B4 | CLASSROOM | 300 | 20 |  | 1085 | 24 | 20 | Univent
B5 | CLASSROOM | 233 | 15 |  | 720 | 16 | 15 | Univent
B6 | CLASSROOM | 296 | 19 |  | 890 | 20 | 19 | Univent
B101 | CLASSROOM | 237 | 15 |  | 850 | 19 | 15 | Univent
B102 | CLASSROOM | 325 | 21 |  | 850 | 19 | 19 | Univent
B103 | CLASSROOM | 275 | 18 |  | 816 | 18 | 18 | Univent
B104 | CLASSROOM | 307 | 20 |  | 1120 | 25 | 20 | Univent
B105 | CLASSROOM | 301 | 20 |  | 744 | 16 | 16 | Univent
B106 | CLASSROOM | 297 | 19 |  | 1100 | 25 | 19 | Univent
C1 | CLASSROOM | 297 | 19 |  | 850 | 19 | 19 | Univent
C2 | CLASSROOM | 0 | 0 | Yes | 850 | 19 | 19 | Univent
C3 | CLASSROOM | 0 | 0 | Yes | 850 | 19 | 19 | Univent
C4 | CLASSROOM | 367 | 24 |  | 1085 | 24 | 24 | Univent
C5 | CLASSROOM | 368 | 24 |  | 720 | 16 | 16 | Univent
C6 | CLASSROOM | 333 | 22 |  | 890 | 20 | 20 | Univent
C7 | CLASSROOM | 293 | 19 |  | 0 | 0 | 0 | Univent
C101 | CLASSROOM | 253 | 16 |  | 850 | 19 | 16 | Univent
C102 | CLASSROOM | 404 | 26 |  | 850 | 19 | 19 | Univent
C103 | CLASSROOM | 230 | 15 |  | 816 | 18 | 15 | Univent
C104 | CLASSROOM | 353 | 23 |  | 1120 | 25 | 23 | Univent
C105 | CLASSROOM | 290 | 19 |  | 744 | 16 | 16 | Univent
C106 | CLASSROOM | 241 | 16 |  | 1100 | 25 | 16 | Univent
D1 | CLASSROOM | 274 | 18 |  | 850 | 19 | 18 | Univent
D2 | CLASSROOM | 449 | 29 |  | 850 | 19 | 19 | Univent
D3 | CLASSROOM | 314 | 20 |  | 850 | 19 | 19 | Univent
D4 | CLASSROOM | 293 | 19 |  | 1085 | 24 | 19 | Univent
D5 | CLASSROOM | 273 | 18 |  | 720 | 16 | 16 | Univent
D6 | CLASSROOM | 405 | 27 |  | 890 | 20 | 20 | Univent
D101 | CLASSROOM | 283 | 18 |  | 850 | 19 | 18 | Univent
D102 | CLASSROOM | 304 | 20 |  | 850 | 19 | 19 | Univent
D103 | CLASSROOM | 326 | 21 |  | 816 | 18 | 18 | Univent
D104 | CLASSROOM | 244 | 16 |  | 1120 | 25 | 16 | Univent
D105 | CLASSROOM | 235 | 15 |  | 744 | 16 | 15 | Univent
D106 | CLASSROOM | 0 | 0 |  | 1100 | 25 | 0 | Univent
D200 | MUSIC CLASSROOM 2 | 729 | 48 |  | 1600 | 36 | 36 | Univent
D205 | MUSIC CLASSROOM 1 | 620 | 41 |  | 1600 | 36 | 36 | Univent
E12 | SCIENCE CLASSROOM | 0 | 0 |  | 1232 | 28 | 0 | Univent
E-147 | BREAK ROOM, OFFICE AREA | 0 | 0 |  | 120 | 2 | 0 | Univent
E-148 | VICE PRINCIPAL OFFICE | 0 | 0 |  | 120 | 2 | 0 | Univent
E-149 | CONFERENCE AREA | 47 | 3 |  | 260 | 5 | 3 | Univent
E-150 | PRINCIPAL OFFICE | 36 | 2 |  | 225 | 5 | 2 | Univent
E204 | EARLY CHILDROOM ED CLASSROOM | 0 | 0 |  |  | 0 | 0 | Univent
E205 | CREATIVE WRITING CLASSROOM (LEFT) | 577 | 38 |  |  | 0 | 0 | Univent
E207 | COMPUTER LAB | 3 | 0 |  | 2070 | 47 | 0 | Univent
- | GIRLS GYM | 0 | 0 |  | 4897 | 111 | 0 | Air Handling Unit
- | BOYS GYM | 0 | 0 |  | 4897 | 111 | 0 | Air Handling Unit
- | IMC - LIBRARY | 0 | 0 |  | 3985 | 90 | 0 | Air Handling Unit
- | INDUSTRIAL ART (WOODSHOP) | 0 | 0 |  | 1564 | 35 | 0 | Air Handling Unit
- | SWIMMING POOL | 0 | 0 |  | 10200 | 231 | 0 | Air Handling Unit
- | ADMIN + HEALTH OFFICE | 0 | 0 |  | 130 | 2 | 0 | Air Handling Unit
- | ART STUDIOS | 0 | 0 |  | 3860 | 87 | 0 | Air Handling Unit
- | AUDITORIUM + STAGE | 0 | 0 |  | 12450 | 282 | 0 | Air Handling Unit
- | CLASSROOM (YMCA 2) | 0 | 0 |  | 704 | 16 | 0 | Air Handling Unit
- | CLASSROOM (YMCA OST1) | 0 | 0 |  | 544 | 12 | 0 | Air Handling Unit

## Richmond
Sheet Last Modified: | 2021-04-05
School: | Richmond Elementary School
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
3 | - |  | 0 |  | 1000 | 22 | 0 | Radiators/House fan
8 | - |  | 0 |  | 1200 | 27 | 0 | Radiators/House fan
101 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan
102 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan
102A | Nurse |  | 0 | Yes | 216 | 4 | 4 | Radiators/House fan
103 | Classroom |  | 0 | Yes | 812 | 18 | 18 | Radiators/House fan
104 | Classroom |  | 0 | Yes | 812 | 18 | 18 | Radiators/House fan
105 | Main Office |  | 0 | Yes | 416 | 9 | 9 | Radiators/House fan
106 | Classroom |  | 0 | Yes | 762 | 17 | 17 | Radiators/House fan
107 | Classroom |  | 0 | Yes | 742 | 16 | 16 | Radiators/House fan
108 | Faculty Lounge |  | 0 |  | 440 | 10 | 0 | Radiators/House fan
109 | Classroom |  | 0 | Yes | 1180 | 26 | 26 | Radiators/House fan
201 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan
202 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan
203 | Classroom |  | 0 | Yes | 960 | 21 | 21 | Radiators/House fan
203A | Counselor Office |  | 0 |  | 167 | 3 | 0 | Radiators/House fan
204 | Classroom |  | 0 | Yes | 960 | 21 | 21 | Radiators/House fan
205 | Classroom |  | 0 | Yes | 896 | 20 | 20 | Radiators/House fan
206 | - |  | 0 |  | 896 | 20 | 0 | Radiators/House fan
207 | - |  | 0 | Yes | 792 | 18 | 18 | Radiators/House fan
208 | - |  | 0 |  | 792 | 18 | 0 | Radiators/House fan
209 | - |  | 0 | Yes | 841 | 19 | 19 | Radiators/House fan
210 | - |  | 0 |  | 202 | 4 | 0 | Radiators/House fan
301 | - |  | 0 |  | 792 | 18 | 0 | Radiators/House fan
302 | Classroom |  | 0 |  | 792 | 18 | 0 | Radiators/House fan
303 | - |  | 0 |  | 840 | 19 | 0 | Radiators/House fan
303A | - |  | 0 |  | 390 | 8 | 0 | Radiators/House fan
304 | - |  | 0 |  | 900 | 20 | 0 | Radiators/House fan
305 | - |  | 0 |  | 840 | 19 | 0 | Radiators/House fan
306 | Classroom |  | 0 |  | 870 | 19 | 0 | Radiators/House fan
307 | - |  | 0 |  | 850 | 19 | 0 | Radiators/House fan
308 | - |  | 0 |  | 850 | 19 | 0 | Radiators/House fan
309 | - |  | 0 |  | 900 | 20 | 0 | Radiators/House fan
310 | - |  | 0 |  | 202 | 4 | 0 | Radiators/House fan
- | Principal's Office |  | 0 |  | 448 | 10 | 0 | Radiators/House fan
- | Gym |  | 0 |  | 2760 | 62 | 0 | Heating Ventalation Unit

## Rivera
Sheet Last Modified: | 2021-04-01
School: | Rivera (Bright Futures) Early Childhood Center
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Basement | Cafeteria | 1016 | 67 |  | 4000 | 90 | 67 | Air Handling Unit
Basement | VVT's in the small Building | 138 | 9 |  | 247 | 5 | 5 | Air Handling Unit
2nd floor | Common area vvt's(tall Building) | 131 | 8 |  | 247 | 5 | 5 | Air Handling Unit
4th for upper building | Zoned AH for 5 zone floor | 0 | 0 |  | 247 | 5 | 0 | Air Handling Unit
5th floor upper building | Zoned AH for 6 zone floor | 1 | 0 |  | 247 | 5 | 0 | Air Handling Unit
- | Zone1( group learning room) | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit
- | Zone2 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit
- | Zone3 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit
- | Zone4 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit
- | Zone5 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit
- | Zone6 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit
Zone1 | Group learning open area 1 | 804 | 53 |  | 280 | 6 | 6 | Air Handling Unit
Zone 1 | Group learning open area 2 | 0 | 0 |  | 270 | 6 | 0 | Air Handling Unit
Zone 1 | Group learning office | 0 | 0 |  | 276 | 6 | 0 | Air Handling Unit
Zone 1 | Large storage | 0 | 0 |  | 112 | 2 | 0 | Air Handling Unit
Zone 1 | Small storage | 21 | 1 |  | 80 | 1 | 1 | Air Handling Unit
Zone 2 | Office 1 | 85 | 5 |  | 80 | 1 | 1 | Air Handling Unit
Zone 2 | Office 2 | 72 | 4 |  | 80 | 1 | 1 | Air Handling Unit
Zone 2 | Office 3 | 37 | 2 |  | 80 | 1 | 1 | Air Handling Unit
Zone 2 | Spare room | 83 | 5 |  | 85 | 1 | 1 | Air Handling Unit
Zone 2 | Hallway | 0 | 0 |  | 110 | 2 | 0 | Air Handling Unit
Zone 2 | Copy room | 38 | 2 |  | 84 | 1 | 1 | Air Handling Unit
Zone 3 | Conference room vent 1 | 314 | 20 |  | 1344 | 30 | 20 | Air Handling Unit
Zone 3 | Conference room vent 2 | 0 | 0 |  | 1344 | 30 | 0 | Air Handling Unit
Zone 3 | Conference room vent 3 | 0 | 0 |  | 1344 | 30 | 0 | Air Handling Unit
Zone 4 | Admin open area 1 | 307 | 20 |  | 182 | 4 | 4 | Air Handling Unit
Zone 4 | Admin open area 2 | 0 | 0 |  | 182 | 4 | 0 | Air Handling Unit
Zone 4 | copy room | 57 | 3 |  | 84 | 1 | 1 | Air Handling Unit
Zone 4 | elevator hallway | 0 | 0 |  | 144 | 3 | 0 | Air Handling Unit
Zone 4 | admin waiting area | 0 | 0 |  | 380 | 8 | 0 | Air Handling Unit
Zone 4 | Vacant office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 4 | Vacant office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 4 | Supply Room | 0 | 0 |  | 110 | 2 | 0 | Air Handling Unit
Zone 5 | Office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 5 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 5 | Zone 5 meeting Room 1 | 42 | 2 |  | 80 | 1 | 1 | Air Handling Unit
Zone 5 | Zone 5 meeting Room 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 6 | Storage | 110 | 7 |  | 80 | 1 | 1 | Air Handling Unit
Zone 6 | Office 1 | 272 | 18 |  | 80 | 1 | 1 | Air Handling Unit
Zone 6 | Office 2 | 121 | 8 |  | 80 | 1 | 1 | Air Handling Unit
Zone 6 | Office 3 | 115 | 7 |  | 80 | 1 | 1 | Air Handling Unit
Zone 6 | Office 4 | 198 | 13 |  | 80 | 1 | 1 | Air Handling Unit
Zone 6 | Office 5 | 147 | 9 |  | 80 | 1 | 1 | Air Handling Unit
- | Zone 1 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Zone 2 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Zone 3 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Zone 4 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Zone 5 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Group learning area. Diffuser 1 | 91 | 6 |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Group learning area. Diffuser 2 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Group learning area. Diffuser 3 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Group learning area. Diffuser 4 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Group learning area. Diffuser 5 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Office 1 | 18 | 1 |  | 80 | 1 | 1 | Air Handling Unit
Zone 1 | Office 2 | 19 | 1 |  | 80 | 1 | 1 | Air Handling Unit
Zone 1 | Office 3 | 12 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 2 | Elevator lobby | 0 | 0 |  | 144 | 3 | 0 | Air Handling Unit
Zone 2 | Reception diffuser 1 | 34 | 2 |  |  | 0 | 0 | Air Handling Unit
Zone 2 | Reception diffuser 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 2 | Office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 2 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 3 | Office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 3 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 3 | Office 3 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 3 | Kitchen 1 | 0 | 0 |  | 214 | 4 | 0 | Air Handling Unit
Zone 3 | Kitchen 2 | 0 | 0 |  | 214 | 4 | 0 | Air Handling Unit
Zone 3 | Hallway 1 | 0 | 0 |  | 276 | 6 | 0 | Air Handling Unit
Zone 3 | Hallway 2 | 0 | 0 |  | 168 | 3 | 0 | Air Handling Unit
Zone 4 | Office 411 | 0 | 0 |  | 75 | 1 | 0 | Air Handling Unit
Zone 4 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 4 | Office 3 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 4 | Storage 415 | 0 | 0 |  | 39 | 0 | 0 | Air Handling Unit
Zone 4 | Hallway | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 4 | Assistant Superintendent | 0 | 0 |  | 460 | 10 | 0 | Air Handling Unit
Zone 4 | Assistant Superintendent | 0 | 0 |  | 460 | 10 | 0 | Air Handling Unit
Zone 4 | Assistant Superintendent | 0 | 0 |  | 460 | 10 | 0 | Air Handling Unit
Zone 4 | Storage 408 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 5 | Office 403 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 5 | Office 403 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 5 | Office 404 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 5 | Office | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 5 | Office | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 5 | Conference room 406 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 5 | Conference room 406 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
Zone 5 | Office 407 | 0 | 0 |  | 142 | 3 | 0 | Air Handling Unit
Zone 5 | Office 409 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit
3rd floor. VVT#11 | Commons area total | 50 | 3 |  | 247 | 5 | 3 | Air Handling Unit
- | Elevator hall | 9 | 0 |  | 400 | 9 | 0 | Air Handling Unit
- | Elevator hall | 0 | 0 |  | 602 | 13 | 0 | Air Handling Unit
- | Commons Area Diffuser | 11 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 11 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 11 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 12 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Office | 2 | 0 |  |  | 0 | 0 | Air Handling Unit
2nd floor. VVT#8 | Commons Are Total | 58 | 3 |  | 247 | 5 | 3 | Air Handling Unit
- | Elevator hall | 2 | 0 |  | 400 | 9 | 0 | Air Handling Unit
- | Commons Area Diffuser | 14 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 14 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 12 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 8 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons area office | 3 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Class bathroom | 3 | 0 |  | 75 | 1 | 0 | Air Handling Unit
- | Staff Bathroom | 2 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Elevator hall | 2 | 0 |  |  | 0 | 0 | Air Handling Unit
1st floor VVT#4 | 1st floor Commons Area Total | 46 | 3 |  | 247 | 5 | 3 | Air Handling Unit
- | elevator hall | 14 | 0 |  | 480 | 10 | 0 | Air Handling Unit
- | elevator hall | 7 | 0 |  | 700 | 15 | 0 | Air Handling Unit
- | Commons area diffuser | 7 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons area diffuser | 8 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons area diffuser | 2 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons area diffuser | 4 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Commons area office | 3 | 0 |  | 126 | 2 | 0 | Air Handling Unit
- | Class bathroom | 0 | 0 |  | 75 | 1 | 0 | Air Handling Unit
- | Staff bathroom | 2 | 0 |  | 48 | 1 | 0 | Air Handling Unit
Room110 | Classroom | 400 | 26 |  | 900 | 20 | 20 | Univent
Room 111 | Classroom | 335 | 22 |  | 900 | 20 | 20 | Univent
Room 112 | Classroom | 410 | 27 |  | 900 | 20 | 20 | Univent
Room 113 | Classroom | 375 | 25 |  | 900 | 20 | 20 | Univent
205A | Office space | 290 | 19 |  | 480 | 10 | 10 | Univent
205B | Office space | 484 | 32 |  | 613 | 13 | 13 | Univent
Room 212 | Classroom | 259 | 17 |  | 900 | 20 | 17 | Univent
Room 213 | Classroom | 502 | 33 |  | 900 | 20 | 20 | Univent
Room 214 | Classroom | 277 | 18 |  | 900 | 20 | 18 | Univent
Room 215 | Classroom | 544 | 36 |  | 900 | 20 | 20 | Univent
Room303 | Office space | 482 | 32 |  | 1414 | 32 | 32 | Univent
Room 303B | Office space | 256 | 17 |  | 360 | 8 | 8 | Univent
Room 309 | Classroom | 517 | 34 |  | 1110 | 25 | 25 | Univent
Room 310 | Classroom | 290 | 19 |  | 900 | 20 | 19 | Univent
Room 311 | Classroom | 326 | 21 |  | 900 | 20 | 20 | Univent
Room 312 | Classroom | 394 | 26 |  | 900 | 20 | 20 | Univent
VVT 9 | Total | 10 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Office | 3 | 0 |  | 144 | 3 | 0 | Air Handling Unit
- | Office | 4 | 0 |  | 144 | 3 | 0 | Air Handling Unit
- | Hallway | 4 | 0 |  | 688 | 15 | 0 | Air Handling Unit
VVT 10 | Total | 43 | 2 |  | 688 | 15 | 2 | Air Handling Unit
- | Teachers Lounge | 16 | 1 |  | 390 | 8 | 1 | Air Handling Unit
- | Bathroom | 4 | 0 |  | 48 | 1 | 0 | Air Handling Unit
- | Women's Room | 8 | 0 |  | 112 | 2 | 0 | Air Handling Unit
- | Men's Room | 3 | 0 |  | 112 | 2 | 0 | Air Handling Unit
- | Hallway | 11 | 0 |  | 688 | 15 | 0 | Air Handling Unit
VVT 6 | Total | 18 | 1 |  |  | 0 | 0 | Air Handling Unit
- | office | 6 | 0 |  | 100 | 2 | 0 | Air Handling Unit
- | Office | 5 | 0 |  | 100 | 2 | 0 | Air Handling Unit
- | Office | 5 | 0 |  | 100 | 2 | 0 | Air Handling Unit
- | Hallway | 2 | 0 |  | 688 | 15 | 0 | Air Handling Unit
VVT 7 | Total | 32 | 2 |  |  | 0 | 0 | Air Handling Unit
- | Men's room | 7 | 0 |  | 112 | 2 | 0 | Air Handling Unit
- | Women's room | 11 | 0 |  | 112 | 2 | 0 | Air Handling Unit
- | Staff bathroom | 4 | 0 |  | 52 | 1 | 0 | Air Handling Unit
- | Hallway | 4 | 0 |  | 688 | 15 | 0 | Air Handling Unit
- | Hallway | 4 | 0 |  | 688 | 15 | 0 | Air Handling Unit
VVT1 | Total | 29 | 1 |  |  | 0 | 0 | Air Handling Unit
- | kitchen | 6 | 0 |  | 288 | 6 | 0 | Air Handling Unit
- | Storage | 4 | 0 |  | 450 | 10 | 0 | Air Handling Unit
- | Men's room | 4 | 0 |  | 77 | 1 | 0 | Air Handling Unit
- | Women's room | 6 | 0 |  | 77 | 1 | 0 | Air Handling Unit
- | Unisex bathroom | 3 | 0 |  | 77 | 1 | 0 | Air Handling Unit
VVT 3 | Total | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
- | storage | 0 | 0 |  | 328 | 7 | 0 | Air Handling Unit
- | storage | 0 | 0 |  | 450 | 10 | 0 | Air Handling Unit
- | storage | 0 | 0 |  | 250 | 5 | 0 | Air Handling Unit
- | storage | 0 | 0 |  | 175 | 3 | 0 | Air Handling Unit
VVT 5 | Total | 41 | 2 |  |  | 0 | 0 | Air Handling Unit
- | hallway | 7 | 0 |  | 425 | 9 | 0 | Air Handling Unit
- | Lobby | 11 | 0 |  | 375 | 8 | 0 | Air Handling Unit
- | Guard office | 8 | 0 |  | 120 | 2 | 0 | Air Handling Unit
- | Staff lockers | 4 | 0 |  | 450 | 10 | 0 | Air Handling Unit
- | Hallway | 4 | 0 |  | 800 | 18 | 0 | Air Handling Unit
- | Hallway | 8 | 0 |  | 168 | 3 | 0 | Air Handling Unit

## Robeson
Sheet Last Modified: | 2021-03-18
School: | Paul Robeson High School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B-2 | Classroom | 0 | 0 |  | 1073 | 24 | 0 | Fan Coil Unit
100 | Classroom | 380 | 25 |  | 940 | 21 | 21 | Univent
106 | Classroom | 470 | 31 |  | 840 | 19 | 19 | Univent
108 | Classroom | 11 | 0 |  | 828 | 18 | 0 | Univent
200 | Classroom | 89 | 5 |  | 696 | 15 | 5 | Univent
202 | Classroom | 231 | 15 |  | 696 | 15 | 15 | Univent
204 | Classroom | 301 | 20 |  | 696 | 15 | 15 | Univent
205 | Classroom | 304 | 20 |  | 672 | 15 | 15 | Univent
206 | Classroom | 200 | 13 |  | 696 | 15 | 13 | Univent
207 | Classroom | 191 | 12 |  | 696 | 15 | 12 | Univent
208 | Classroom | 125 | 8 |  | 696 | 15 | 8 | Univent
209 | Classroom | 178 | 11 |  | 384 | 8 | 8 | Univent
210 | Classroom | 200 | 13 |  | 690 | 15 | 13 | Univent
211 | Classroom | 262 | 17 |  | 851 | 19 | 17 | Univent
212 | Classroom | 280 | 18 |  | 875 | 19 | 18 | Univent
213 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Univent
- | AUDITORIUM | 0 | 0 |  | 2793 | 63 | 0 | Air Handling Unit
- | Cafeteria | 862 | 57 |  | 2343 | 53 | 53 | Univent
- | GYM | 812 | 54 |  | 3478 | 79 | 54 | Air Handling Unit
- | MAIN OFFICE | 0 | 0 |  | 552 | 12 | 0 | Univent
- | Student Lounge | 64 | 4 |  | 552 | 12 | 4 | Univent

## Roosevelt
Sheet Last Modified: | 2021-05-03
School: | Roosevelt Elementary School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 1035 | 23 | 23 | House Fan
102 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan
103 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan
104 | Main Office |  | 0 | Yes | 1225 | 27 | 27 | House Fan
105 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan
106 & 106a | Classroom |  | 0 | Yes | 1298 | 29 | 29 | House Fan
107 | Parent Liason |  | 0 | Yes | 550 | 12 | 12 | House Fan
108 | Classroom |  | 0 | Yes | 814 | 18 | 18 | House Fan
109 | Classroom |  | 0 | Yes | 1104 | 25 | 25 | House Fan
110 | Classroom |  | 0 | Yes | 960 | 21 | 21 | House Fan
- | Lunchroom A |  | 0 | Yes | 2881 | 65 | 65 | House Fan
- | Lunchroom B |  | 0 | Yes | 2898 | 65 | 65 | House Fan
200A | Counselor |  | 0 | Yes | 342 | 7 | 7 | House Fan
200B | Counselor |  | 0 |  | 342 | 7 | 0 | House Fan
200C | Counselor |  | 0 | Yes | 342 | 7 | 7 | House Fan
201 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
202 | Classroom |  | 0 | Yes | 638 | 14 | 14 | House Fan
203 | Classroom |  | 0 | Yes | 748 | 17 | 17 | House Fan
205 | IMC |  | 0 | Yes | 1320 | 30 | 30 | House Fan
206A | Counselor |  | 0 | Yes | 140 | 3 | 3 | House Fan
206B | Counselor |  | 0 | Yes | 116 | 2 | 2 | House Fan
206C | Counselor |  | 0 | Yes | 115 | 2 | 2 | House Fan
206D | Counselor |  | 0 | Yes | 142 | 3 | 3 | House Fan
206E | Counselor |  | 0 | Yes | 126 | 2 | 2 | House Fan
207A | Room |  | 0 | Yes | 108 | 2 | 2 | House Fan
207B | Room |  | 0 |  | 145 | 3 | 0 | House Fan
207C | Room |  | 0 | Yes | 108 | 2 | 2 | House Fan
207D | Room |  | 0 |  | 103 | 2 | 0 | House Fan
207E | Room |  | 0 | Yes | 132 | 3 | 3 | House Fan
208 | Art Room |  | 0 | Yes | 1152 | 26 | 26 | House Fan
209 | Faculty Lounge |  | 0 | Yes | 696 | 15 | 15 | House Fan
- | Principal Office |  | 0 | Yes | 629 | 14 | 14 | House Fan
- | Nurse Suite |  | 0 | Yes | 552 | 12 | 12 | House Fan
210 | Science Lab |  | 0 | Yes | 700 | 15 | 15 | House Fan
211 | Music |  | 0 | Yes | 858 | 19 | 19 | House Fan
212 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan
213 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
214 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan
215 | Classroom |  | 0 | Yes | 572 | 13 | 13 | House Fan
216 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan
217 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
218 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
219 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan
220 | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan
221A | Classroom |  | 0 | Yes | 342 | 7 | 7 | House Fan
221B | Classroom |  | 0 |  | 342 | 7 | 0 | House Fan
221C | Classroom |  | 0 |  | 342 | 7 | 0 | House Fan
222 | Classroom |  | 0 |  | 336 | 7 | 0 | House Fan
300A | Counselor // Storage |  | 0 |  | 342 | 7 | 0 | House Fan
300B | Counselor // Storage |  | 0 |  | 342 | 7 | 0 | House Fan
300C | Counselor // Storage |  | 0 |  | 342 | 7 | 0 | House Fan
301 | Vice Principals Office |  | 0 | Yes | 628.833 | 14 | 14 | House Fan
302 | Classroom |  | 0 | Yes | 735 | 16 | 16 | House Fan
303 | Classroom |  | 0 | Yes | 789 | 17 | 17 | House Fan
304 | Classroom |  | 0 | Yes | 734 | 16 | 16 | House Fan
305 | Classroom |  | 0 | Yes | 789 | 17 | 17 | House Fan
306 | Classroom |  | 0 |  | 1170 | 26 | 0 | House Fan
307 | Classroom |  | 0 | Yes | 936 | 21 | 21 | House Fan
308 | Classroom |  | 0 | Yes | 735 | 16 | 16 | House Fan
309 | Classroom |  | 0 |  | 952 | 21 | 0 | House Fan
310 | Classroom |  | 0 | Yes | 840 | 19 | 19 | House Fan
311 | Classroom |  | 0 |  | 836 | 19 | 0 | House Fan
312 | Classroom |  | 0 |  | 792 | 18 | 0 | House Fan
313 | Classroom |  | 0 |  | 920 | 20 | 0 | House Fan
314 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan
315 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan
316 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan
317 | Classroom |  | 0 |  | 638 | 14 | 0 | House Fan
318 | Classroom |  | 0 |  | 868 | 19 | 0 | House Fan
319 | Classroom |  | 0 | Yes | 868 | 19 | 19 | House Fan
320 | Classroom |  | 0 | Yes | 868 | 19 | 19 | House Fan
324A | Counselor, School Police |  | 0 |  | 342 | 7 | 0 | House Fan
324B | Counselor, School Police |  | 0 |  | 342 | 7 | 0 | House Fan
324C | Counselor, School Police |  | 0 |  | 342 | 7 | 0 | House Fan
322 | Classroom |  | 0 | Yes | 868 | 19 | 19 | House Fan
321 | Classroom |  | 0 | Yes | 861 | 19 | 19 | House Fan

## Rowen
Sheet Last Modified: | 2021-04-26
School: | William Rowen Elementary School
Vendor: | EMCOR | EMCOR Part 2 | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium | 0 | 0 |  | 4256 | 96 | 0 | House Fan
- | Cafeteria/Gym | 0 | 0 | Yes | 5220 | 118 | 118 | Univent
- | Library | 328 | 21 |  | 1456 | 33 | 21 | Univent
101 | Classroom | 457 | 30 |  | 1128 | 25 | 25 | Univent
102 | Classroom | 545 | 36 |  | 1128 | 25 | 25 | Univent
103 | Classroom | 42 | 2 | Yes | 266 | 6 | 6 | Univent
104 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Univent
105 | Classroom | 304 | 20 |  | 816 | 18 | 18 | Univent
106 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Univent
107 | Classroom | 299 | 19 |  | 816 | 18 | 18 | Univent
108 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | Univent
109 | Classroom | 234 | 15 |  | 720 | 16 | 15 | Univent
110 | Classroom | 399 | 26 |  | 720 | 16 | 16 | Univent
111 | Classroom | 440 | 29 |  | 720 | 16 | 16 | Univent
112 | Classroom | 68 | 4 |  | 720 | 16 | 4 | Univent
113 | Classroom | 235 | 15 |  | 720 | 16 | 15 | Univent
- | Nurse's Office | 235 | 15 |  | 192 | 4 | 4 | Univent
201 | Classroom | 373 | 24 |  | 920 | 20 | 20 | Univent
202 | Classroom | 396 | 26 |  | 920 | 20 | 20 | Univent
203 | Classroom | 307 | 20 |  | 442 | 10 | 10 | Univent
204 | Classroom | 299 | 19 |  | 384 | 8 | 8 | Univent
205 | Classroom | 309 | 20 |  | 720 | 16 | 16 | Univent
206 | Classroom | 230 | 15 |  | 720 | 16 | 15 | Univent
207 | Classroom | 327 | 21 |  | 720 | 16 | 16 | Univent
208 | Classroom | 272 | 18 |  | 720 | 16 | 16 | Univent
209 | Classroom | 324 | 21 |  | 720 | 16 | 16 | Univent
210 | Classroom | 276 | 18 |  | 720 | 16 | 16 | Univent
211 | Classroom | 336 | 22 |  | 720 | 16 | 16 | Univent
212 | Classroom | 272 | 18 |  | 720 | 16 | 16 | Univent
213 | Classroom | 284 | 18 |  | 720 | 16 | 16 | Univent
214 | Classroom | 271 | 18 |  | 720 | 16 | 16 | Univent
215 | Classroom | 280 | 18 |  | 720 | 16 | 16 | Univent
216 | Classroom | 300 | 20 |  | 744 | 16 | 16 | Univent
- | Main Office |  | 0 | Yes | 552 | 12 | 12
- | Principal |  | 0 | Yes | 270 | 6 | 6

## Roxborough
Sheet Last Modified: | 2021-04-23
School: | Roxborough High School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
114 | Classroom | 0 | 0 |  | 857 | 19 | 0 | Univent
115 | Classroom | 30 | 2 |  | 870 | 19 | 2 | Univent
116 | Classroom | 45 | 3 |  | 690 | 15 | 3 | Univent
117 | Weight Room | 30 | 2 |  | 814 | 18 | 2 | Univent
118 | Classroom | 55 | 3 |  | 702 | 15 | 3 | Univent
119 | Classroom | 270 | 18 |  | 877 | 19 | 18 | Univent
120 | Classroom | 85 | 5 |  | 694 | 15 | 5 | Univent
121 | Classroom | 40 | 2 |  | 1207 | 27 | 2 | Univent
124A-1 | Classroom | 55 | 3 |  | 621 | 14 | 3 | Univent
124B-1 | Classroom | 30 | 2 |  | 672 | 15 | 2 | Univent
126 | Classroom | 0 | 0 |  | 1841 | 41 | 0 | Univent
128 | Classroom | 50 | 3 |  | 1501 | 34 | 3 | Univent
203 | Classroom |  | 0 | Yes | 682 | 15 | 15
205 | Classroom |  | 0 | Yes | 682 | 15 | 15
215 | Classroom | 0 | 0 |  | 829 | 18 | 0 | Univent
216 | Classroom | 50 | 3 |  | 834 | 18 | 3 | Univent
217 | Classroom | 0 | 0 |  | 686 | 15 | 0 | Univent
218 | Classroom | 0 | 0 |  | 724 | 16 | 0 | Univent
219 | Classroom | 55 | 3 |  | 842 | 19 | 3 | Univent
220 | Classroom | 60 | 4 |  | 616 | 14 | 4 | Univent
221 | Classroom | 35 | 2 |  | 845 | 19 | 2 | Univent
223 | Classroom | 55 | 3 |  | 1072 | 24 | 3 | Univent
224 | Classroom | 55 | 3 |  | 1010 | 22 | 3 | Univent
235 | Classroom |  | 0 | Yes | 839 | 19 | 19
309 | Classroom |  | 0 | Yes | 997 | 22 | 22
312 | Classroom |  | 0 | Yes | 1071 | 24 | 24
319 | Classroom | 40 | 2 |  | 644 | 14 | 2 | Univent
320 | Classroom | 40 | 2 |  | 721 | 16 | 2 | Univent
321 | Classroom | 55 | 3 |  | 924 | 21 | 3 | Univent
322 | Classroom | 30 | 2 |  | 723 | 16 | 2 | Univent
323 | Classroom | 60 | 4 |  | 777 | 17 | 4 | Univent
324 | Classroom | 55 | 3 |  | 942 | 21 | 3 | Univent
325 | Classroom | 45 | 3 | Yes | 325 | 7 | 7 | Univent
326 | Classroom | 55 | 3 |  | 1000 | 22 | 3 | Univent
- | Gymnasium | 740 | 49 |  | 11475 | 260 | 49 | Air Handling Unit
- | Library | 2335 | 155 |  | 2622 | 59 | 59 | Air Handling Unit
East Office | Office | 75 | 5 |  |  | 0 | 0
West Office | Office | 110 | 7 |  |  | 0 | 0 | Air Handling Unit
- | Alumni Room | 255 | 17 |  | 377 | 8 | 8 | Air Handling Unit
- | Computer Lab | 1285 | 85 |  | 870 | 19 | 19 | Air Handling Unit

## Rush
Sheet Last Modified: | 2021-03-18
School: | Arts Academy @ Benjamin Rush High School
Vendor: | Goldner | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
103 | Lab Classroom | 465 | 31 |  | 748 | 17 | 17 | Univent & Air Handling Unit
103 | Lab Classroom | 465 | 31 |  |  | 0 | 0 | Univent & Air Handling Unit
104 | GraphicArts Classroom | 928 | 61 |  | 1840 | 41 | 41 | Univent & Air Handling Unit
104 | Graphic Arts Classroom | 946 | 63 |  |  | 0 | 0 | Univent & Air Handling Unit
105 | IMC Classroom | 2959 | 197 |  |  | 0 | 0 | Air Handling Unit
105D | Student Property Office | 281 | 18 |  |  | 0 | 0 | Air Handling Unit
105E | IMC Copy Office | 960 | 64 |  |  | 0 | 0 | Air Handling Unit
105F | Cart Storage | 368 | 24 |  |  | 0 | 0 | Air Handling Unit
105G | Tech Equip Office | 255 | 17 |  |  | 0 | 0 | Air Handling Unit
105H | IMC Office | 201 | 13 |  |  | 0 | 0 | Air Handling Unit
105J | IMC Storage room | 252 | 16 |  |  | 0 | 0 | Air Handling Unit
105K | IMC Conference Rm | 312 | 20 |  |  | 0 | 0 | Air Handling Unit
106 | Art Studio Classroom | 1326 | 88 |  | 1020 | 23 | 23 | Air Handling Unit
107 | storage room | 275 | 18 |  | 280 | 6 | 6 | Air Handling Unit
122 | Art Studio Classroom | 1689 | 112 |  | 1496 | 34 | 34 | Air Handling Unit
123 | Production Studio Classroom | 2228 | 148 |  | 1254 | 28 | 28 | Air Handling Unit
126A | Boys Locker Room | 0 | 0 |  |  | 0 | 0
127A | Girls Locker Room | 0 | 0 |  |  | 0 | 0
129 | Production Booth Classroom | 842 | 56 |  | 264 | 6 | 6 | Air Handling Unit
131A | Changing Room Classroom | 238 | 15 |  | 72 | 1 | 1 | Air Handling Unit
131B | Changing Room Classroom | 175 | 11 |  | 192 | 4 | 4 | Air Handling Unit
133 | Storage Room | 428 | 28 |  | 580 | 13 | 13 | Air Handling Unit
134 | Music Classroom | 1076 | 71 |  | 748 | 17 | 17 | Air Handling Unit
135 | Music Classroom | 1097 | 73 |  | 748 | 17 | 17 | Air Handling Unit
136 | Practice Classroom | 113 | 7 |  | 36 | 0 | 0 | Air Handling Unit
137 | Practice Classroom | 116 | 7 |  | 36 | 0 | 0 | Air Handling Unit
138 | Library | 88 | 5 |  |  | 0 | 0 | Air Handling Unit
140 | Vocal Music Classroom | 3597 | 239 |  |  | 0 | 0 | Air Handling Unit
141 | Scene Shop Classroom | 994 | 66 |  |  | 0 | 0 | Univent & Air Handling Unit
142 | Vocal Theory Classroom | 347 | 23 |  | 748 | 17 | 17 | Univent & Air Handling Unit
143 | Music Theory Classroom | 963 | 64 |  | 748 | 17 | 17 | Univent & Air Handling Unit
144 | Music Tech Lab Classroom | 699 | 46 |  | 748 | 17 | 17 | Univent & Air Handling Unit
145A | Clerical Office | 362 | 24 |  | 720 | 16 | 16 | Air Handling Unit
145B | Roster Office | 161 | 10 |  | 80 | 1 | 1 | Air Handling Unit
145D | Copier Office | 219 | 14 |  | 75 | 1 | 1 | Air Handling Unit
145E | Conference Office | 341 | 22 |  | 128 | 2 | 2 | Air Handling Unit
145F | Principal Office | 328 | 21 |  | 247 | 5 | 5 | Air Handling Unit
145J | Asset Princ.Office | 114 | 7 |  | 272 | 6 | 6 | Air Handling Unit
145K | Asset Princ.Office | 67 | 4 |  | 180 | 4 | 4 | Air Handling Unit
146A | Clinic Office | 45 | 3 |  | 120 | 2 | 2 | Air Handling Unit
146B | ClinicWaitingoffice | 506 | 33 |  | 221 | 5 | 5 | Air Handling Unit
146D | Exam Room | 328 | 21 |  | 60 | 1 | 1 | Air Handling Unit
147 | Counselor Waiting Area | 450 | 30 |  | 288 | 6 | 6 | Air Handling Unit
147B | Counselor Office | 149 | 9 |  | 221 | 5 | 5 | Air Handling Unit
147D | Counselor's Office | 283 | 18 |  | 60 | 1 | 1 | Air Handling Unit
147E | Counselor Office | 157 | 10 |  | 120 | 2 | 2 | Air Handling Unit
147F | Counselor Conference Office | 311 | 20 |  | 169 | 3 | 3 | Air Handling Unit
147G | Counselor's Office | 383 | 25 |  | 180 | 4 | 4 | Air Handling Unit
148A | Camera office | 565 | 37 |  | 120 | 2 | 2 | Air Handling Unit
148B | Storage Room | 121 | 8 |  |  | 0 | 0 | Air Handling Unit
148C | Records Office | 118 | 7 |  |  | 0 | 0 | Air Handling Unit
148D | Security Office | 125 | 8 |  |  | 0 | 0 | Air Handling Unit
148E | Operations Office | 372 | 24 |  |  | 0 | 0 | Air Handling Unit
200 | General Classroom | 649 | 43 |  | 748 | 17 | 17 | Univent & Air Handling Unit
201 | General Classroom | 532 | 35 |  | 748 | 17 | 17 | Univent & Air Handling Unit
202 | General Classroom | 692 | 46 |  | 748 | 17 | 17 | Univent & Air Handling Unit
204 | General Classroom | 447 | 29 |  | 748 | 17 | 17 | Univent & Air Handling Unit
205 | General Classroom | 566 | 37 |  | 748 | 17 | 17 | Univent & Air Handling Unit
209 | Social Ed. Classroom | 779 | 51 |  | 748 | 17 | 17 | Univent & Air Handling Unit
210 | General Classroom | 662 | 44 |  | 748 | 17 | 17 | Univent & Air Handling Unit
211 | General Classroom | 562 | 37 |  | 748 | 17 | 17 | Univent & Air Handling Unit
212 | General Classroom | 423 | 28 |  | 748 | 17 | 17 | Univent & Air Handling Unit
213 | General Classroom | 597 | 39 |  | 748 | 17 | 17 | Univent & Air Handling Unit
214 | General Classroom | 868 | 57 |  | 748 | 17 | 17 | Univent & Air Handling Unit
215 | General Classroom | 442 | 29 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
216 | Physical Science Classroom | 970 | 64 |  | 1344 | 30 | 30 | Fan Coil Unit & Air Handling Unit
217 | Prep Classroom | 299 | 19 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
219 | Physics Classroom | 630 | 42 |  | 1344 | 30 | 30 | Fan Coil Unit & Air Handling Unit
220 | Storage room | 418 | 27 |  |  | 0 | 0 | Air Handling Unit
221 | General Classroom | 324 | 21 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
221B | Storage Room | 135 | 9 |  |  | 0 | 0 | Air Handling Unit
221C | Storage Room | 130 | 8 |  |  | 0 | 0 | Air Handling Unit
222 | Biology Classroom | 633 | 42 |  | 1764 | 40 | 40 | Fan Coil Unit & Air Handling Unit
223 | Prep Classroom | 322 | 21 |  | 312 | 7 | 7 | Fan Coil Unit & Air Handling Unit
224 | Chemistry Classroom | 616 | 41 |  | 1716 | 39 | 39 | Fan Coil Unit & Air Handling Unit
224A | Storage Room | 135 | 9 |  |  | 0 | 0 | Air Handling Unit
225 | Instructional Room | 483 | 32 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
234 | Lab Classroom | 1107 | 73 |  | 850 | 19 | 19 | Fan Coil Unit & Air Handling Unit
235 | Lab Classroom | 595 | 39 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
235 | Lab Classroom | 465 | 31 |  |  | 0 | 0 | Univent & Air Handling Unit
236 | Multipurpose Classroom | 636 | 42 |  | 1156 | 26 | 26 | Fan Coil Unit & Air Handling Unit
237 | Foreign Language Classroom | 613 | 40 |  | 1156 | 26 | 26 | Fan Coil Unit & Air Handling Unit
240 | Commercial Art Classroom | 845 | 56 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
241 | General Classroom | 664 | 44 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
242 | Instructional Room | 551 | 36 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
243 | General Classroom | 518 | 34 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
244 | General Classroom | 737 | 49 |  | 748 | 17 | 17 | Univent & Air Handling Unit
245 | General Classroom | 586 | 39 |  | 748 | 17 | 17 | Univent & Air Handling Unit
246 | General Classroom | 719 | 47 |  | 748 | 17 | 17 | Univent & Air Handling Unit
247 | General Classroom | 705 | 47 |  | 748 | 17 | 17 | Univent & Air Handling Unit
248 | General Classroom | 909 | 60 |  | 748 | 17 | 17 | Univent & Air Handling Unit
249 | General Classroom | 779 | 51 |  | 748 | 17 | 17 | Univent & Air Handling Unit
251 | General Classroom | 671 | 44 |  | 748 | 17 | 17 | Univent & Air Handling Unit
252 | General Classroom | 876 | 58 |  | 748 | 17 | 17 | Univent & Air Handling Unit
253 | General Classroom | 608 | 40 |  | 748 | 17 | 17 | Univent & Air Handling Unit
254 | General Classroom | 633 | 42 |  | 748 | 17 | 17 | Univent & Air Handling Unit
255 | General Classroom | 738 | 49 |  | 748 | 17 | 17 | Univent & Air Handling Unit
256 | General Classroom | 684 | 45 |  | 748 | 17 | 17 | Univent & Air Handling Unit
- | Auditorium | 18527 | 1235 |  |  | 0 | 0 | Air Handling Unit
- | Cafeteria | 10458 | 697 |  |  | 0 | 0 | Air Handling Unit
- | Studios Area and Assoc. Corridors, fresh air vent in rooms | 18369 | 1224 |  |  | 0 | 0 | Air Handling Unit
- | Instrumental Music Area | 14678 | 978 |  |  | 0 | 0 | Air Handling Unit
- | Gym | 8904 | 593 |  |  | 0 | 0 | Air Handling Unit
- | ICM Classroom Area | 11044 | 736 |  |  | 0 | 0 | Air Handling Unit

## Saul
Sheet Last Modified: | 2021-04-27
School: | Walter Biddle Saul High School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
A1 | A1 | 732 | 48 |  | 864 | 19 | 19 | Air Handling Unit
A1/A2 | Storage | 288 | 19 |  | 255 | 5 | 5 | Air Handling Unit
A2 | A2 | 703 | 46 |  | 864 | 19 | 19 | Air Handling Unit
A3 | A3 | 395 | 26 |  | 792 | 18 | 18 | Univent
A5 | A5 | 1123 | 74 |  | 740 | 16 | 16 | Univent
A21 | A21 | 0 | 0 |  | 570 | 12 | 0 | Air Handling Unit
A22 | A22 | 487 | 32 |  | 620 | 14 | 14 | Univent
A23 | A23 | 699 | 46 |  | 888 | 20 | 20 | Univent
A24 | A24 | 1147 | 76 |  | 888 | 20 | 20 | Univent
A25 | A25 | 878 | 58 |  | 888 | 20 | 20 | Univent
A26 | A26 | 449 | 29 |  | 888 | 20 | 20 | Univent
A29 | A29 |  | 0 | Yes | 864 | 19 | 19
1 | 1 | 240 | 16 |  | 864 | 19 | 19 | Univent
2 | 2 | 70 | 4 |  | 551 | 12 | 12 | Univent
3 | 3 | 900 | 60 |  | 1134 | 25 | 25 | Univent
4 | 4 | 0 | 0 |  | 896 | 20 | 0 | Univent
100 | 100 | 215 | 14 |  | 620 | 14 | 14 | Univent
102 | 102 | 342 | 22 |  | 620 | 14 | 14 | Univent
103 | 103 | 206 | 13 |  | 780 | 17 | 17 | Univent
104 | 104 | 265 | 17 |  | 640 | 14 | 14 | Univent
200 | 200 | 258 | 17 |  | 620 | 14 | 14 | Univent
201 | 201 | 244 | 16 |  | 620 | 14 | 14 | Univent
202 | 202 | 251 | 16 |  | 620 | 14 | 14 | Univent
203 | 203 | 173 | 11 |  | 620 | 14 | 14 | Univent
204 | 204 | 226 | 15 |  | 620 | 14 | 14 | Univent
205 | 205 | 468 | 31 |  | 660 | 15 | 15 | Univent
206 | 206 | 560 | 37 |  | 110 | 2 | 2 | Univent
208 | 208 | 232 | 15 |  | 600 | 13 | 13 | Univent
210 | 210 | 244 | 16 |  | 465 | 10 | 10 | Univent
Food Science | Laboratory |  | 0 |  | 560 | 12 | 12
- | Nurse | 316 | 21 |  | 260 | 5 | 5 | Univent
- | Staff Lounge | 0 | 0 |  | 384 | 8 | 0 | Univent

## Sayre
Sheet Last Modified: | 2021-05-03
School: | William L. Sayre High School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 518 | 34 |  | 720 | 16 | 16 | Univent
102 | Lounge | 229 | 15 |  | 408 | 9 | 9 | Univent
103 | Music | 327 | 21 |  | 1260 | 28 | 28 | Univent
104 | Office | 0 | 0 |  | 360 | 8 | 0 | Univent
105 | Classroom | 375 | 25 |  | 1504 | 34 | 34 | Univent
106 | Classroom | 389 | 25 |  | 768 | 17 | 17 | Univent
107 | Classroom | 517 | 34 |  | 1408 | 32 | 32 | Univent
108 | Classroom | 0 | 0 |  | 768 | 17 | 0 | Univent
109 | Classroom | 0 | 0 | Yes | 1120 | 25 | 25 | Univent
110 | Classroom | 351 | 23 |  | 768 | 17 | 17 | Univent
111 | Classroom | 638 | 42 |  | 1363 | 30 | 30 | Univent
115 | Classroom | 369 | 24 |  | 896 | 20 | 20 | Univent
117 | Classroom | 0 | 0 | Yes | 756 | 17 | 17 | Univent
119 | Classroom | 192 | 12 |  | 868 | 19 | 19 | Univent
131 | Classroom | 402 | 26 |  | 729 | 16 | 16 | Univent
133 | Office | 357 | 23 |  | 288 | 6 | 6 | Univent
135 | Boy's Infirmary | 287 | 19 |  | 132 | 3 | 3 | Univent
137 | Girl's Infirmary | 142 | 9 |  | 285 | 6 | 6 | Univent
139 | Classroom | 202 | 13 |  | 1024 | 23 | 23 | Univent
141 | Classroom | 384 | 25 |  | 1188 | 27 | 27 | Univent
200 | Youth Court | 693 | 46 |  | 744 | 16 | 16 | Univent
200 | Classroom | 410 | 27 |  | 592 | 13 | 13 | Univent
203 | Classroom | 808 | 53 |  | 1504 | 34 | 34 | Univent
204 | Classroom | 294 | 19 |  | 744 | 16 | 16 | Univent
205 | Classroom | 762 | 50 |  | 1504 | 34 | 34 | Univent
206 | Classroom | 473 | 31 |  | 696 | 15 | 15 | Univent
207 | Classroom | 702 | 46 |  | 1280 | 29 | 29 | Univent
208 | Classroom | 548 | 36 |  | 744 | 16 | 16 | Univent
210 | Classroom | 246 | 16 |  | 744 | 16 | 16 | Univent
211 | Classroom | 835 | 55 |  | 1344 | 30 | 30 | Univent
212 | Classroom | 367 | 24 |  | 744 | 16 | 16 | Univent
215 | Classroom | 0 | 0 |  | 621 | 14 | 0 | Univent
216 | Classroom | 731 | 48 |  | 864 | 19 | 19 | Univent
217 | Classroom | 81 | 5 |  | 990 | 22 | 22 | Univent
219 | Classroom | 0 | 0 |  | 1008 | 22 | 0 | Univent
220 | Classroom | 301 | 20 |  | 744 | 16 | 16 | Univent
221 | Classroom | 92 | 6 |  | 987 | 22 | 22 | Univent
222 | Classroom | 623 | 41 |  | 744 | 16 | 16 | Univent
223 | Classroom | 0 | 0 |  | 902 | 20 | 0 | Univent
224 | Classroom | 419 | 27 |  | 744 | 16 | 16 | Univent
225 | Classroom | 264 | 17 |  | 725 | 16 | 16 | Univent
226 | Classroom | 0 | 0 |  | 744 | 16 | 0 | Univent
228 | Classroom | 202 | 13 |  | 840 | 19 | 19 | Univent
229 | Classroom | 401 | 26 |  | 1458 | 33 | 33 | Univent
230 | Classroom | 797 | 53 |  | 792 | 18 | 18 | Univent
231 | Classroom | 509 | 33 |  | 999 | 22 | 22 | Univent
232 | Classroom | 1571 | 104 |  | 960 | 21 | 21 | Univent
234 | Classroom | 1041 | 69 |  | 816 | 18 | 18 | Univent
235 | Classroom | 778 | 51 |  | 1400 | 31 | 31 | Univent
236 | Classroom | 809 | 53 |  | 744 | 16 | 16 | Univent
240 | Classroom | 683 | 45 |  | 696 | 15 | 15 | Univent
242 | Classroom | 274 | 18 |  | 912 | 20 | 20 | Univent
244 | Classroom | 0 | 0 |  | 768 | 17 | 0 | Univent
246 | Classroom | 415 | 27 |  | 936 | 21 | 21 | Univent
248 | Classroom | 0 | 0 |  | 666 | 15 | 0 | Univent
- | Auditorium | 0 | 0 |  | 10250 | 232 | 0 | House Fan
- | Cafeteria | 0 | 0 |  | 10540 | 239 | 0 | House Fan
- | Counseling Office | 234 | 15 |  | 187 | 4 | 4 | Univent
- | Girls Gym | 0 | 0 | Yes | 7630 | 173 | 173 | House Fan
- | Boys Gym | 0 | 0 | Yes | 7630 | 173 | 173 | House Fan
- | Handball Court | 0 | 0 |  | 800 | 18 | 0 | Air Handling Unit
- | Library | 0 | 0 |  | 3432 | 78 | 0 | Univent
- | IMC Computer | 0 | 0 |  | 744 | 16 | 0 | Univent
- | Kitchen Cooler room | 0 | 0 |  | 182 | 4 | 0 | Univent
- | Locker room | 0 | 0 |  | 180 | 4 | 0 | Air Handling Unit & Univent
- | Boys Locker Rm | 0 | 0 |  | 7470 | 169 | 0 | Whole House Return Air Fan & Air Handling Unit
- | Girls Locker Rm | 0 | 0 |  | 7470 | 169 | 0 | Whole House Return Air Fan & Air Handling Unit
- | Main Office | 153 | 10 |  | 1128 | 25 | 25 | Univent
- | Office | 0 | 0 |  | 198 | 4 | 0 | Univent
- | Rec Room | 0 | 0 |  | 9780 | 222 | 0 | House Fan

## School of the Future
Sheet Last Modified: | 2021-03-18
School: | High School of the Future
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium | 4278 | 285 |  | 4935 | 112 | 112 | Air Handling Unit
10 | Mens Room | 139 | 9 |  | 205 | 4 | 4 | Air Handling Unit
12 | Womens Room | 88 | 5 |  | 215 | 4 | 4 | Air Handling Unit
14 | Storage | 26 | 1 |  | 275 | 6 | 6 | Air Handling Unit
16 | IDF | 15 | 1 |  | 165 | 3 | 3 | Air Handling Unit
17 | Electrical room | 40 | 2 |  | 75 | 1 | 1 | Air Handling Unit
19 | Music Library | 30 | 2 |  | 120 | 2 | 2 | Air Handling Unit
21 | Instrument stroage | 96 | 6 |  | 370 | 8 | 8 | Air Handling Unit
22 | Uniform Room | 49 | 3 |  | 100 | 2 | 2 | Air Handling Unit
23 | Practice room | 41 | 2 |  | 100 | 2 | 2 | Air Handling Unit
24 | Practice room | 42 | 2 |  | 100 | 2 | 2 | Air Handling Unit
25 | Practice room | 43 | 2 |  | 100 | 2 | 2 | Air Handling Unit
26 | Vocal Music Room | 184 | 12 |  | 1400 | 31 | 31 | Air Handling Unit
27 | Practice Room | 27 | 1 |  | 100 | 2 | 2 | Air Handling Unit
28 | Practice Room | 36 | 2 |  | 100 | 2 | 2 | Air Handling Unit
29 | Practice Room | 41 | 2 |  | 100 | 2 | 2 | Air Handling Unit
30 | Dressing Room | 45 | 3 |  | 1300 | 29 | 29 | Air Handling Unit
31 | Music Intrrument room | 966 | 64 |  | 1800 | 40 | 40 | Air Handling Unit
32 | Dressing Room | 104 | 6 |  | 900 | 20 | 20 | Air Handling Unit
33 | Dressing Room | 45 | 3 |  | 300 | 6 | 6 | Air Handling Unit
34 | Scene shop | 537 | 35 |  | 1200 | 27 | 27 | Air Handling Unit
58 | Kitchen |  | 0 |  |  | 0 | 0 | Air Handling Unit
101 | Vestibule | 102 | 6 |  | 555 | 12 | 12 | Air Handling Unit
103 | Camera Room | 49 | 3 |  | 100 | 2 | 2 | Air Handling Unit
104 | Security Room | 59 | 3 |  | 200 | 4 | 4 | Air Handling Unit
105 | Corridor |  | 0 |  | 50 | 1 | 1 | Air Handling Unit
106 | Electric room | 63 | 4 |  | 135 | 3 | 3 | Air Handling Unit
107 | Equipment room | 55 | 3 |  | 205 | 4 | 4 | Air Handling Unit
110 | waiting room | 101 | 6 |  | 200 | 4 | 4 | Air Handling Unit
112 | clerical office | 315 | 21 |  | 635 | 14 | 14 | Air Handling Unit
113 | work/ conf room | 97 | 6 |  | 200 | 4 | 4 | Air Handling Unit
114 | Admin conf room | 81 | 5 |  | 200 | 4 | 4 | Air Handling Unit
115 | Principal office | 80 | 5 |  | 255 | 5 | 5 | Air Handling Unit
115A | Principal bathroom | 8 | 0 |  | 60 | 1 | 1 | Air Handling Unit
117 | Operations office | 24 | 1 |  | 120 | 2 | 2 | Air Handling Unit
118 | vault room | 25 | 1 |  | 200 | 4 | 4 | Air Handling Unit
119 | supply room | 12 | 0 |  | 120 | 2 | 2 | Air Handling Unit
121 | Nurse | 38 | 2 |  | 95 | 2 | 2 | Air Handling Unit
121 | Waiting room | 17 | 1 |  | 95 | 2 | 2 | Air Handling Unit
123 | Nurse office | 14 | 0 |  |  | 0 | 0 | Air Handling Unit
125 | Exam room B | 14 | 0 |  | 100 | 2 | 2 | Air Handling Unit
125 | Exam room A | 13 | 0 |  | 100 | 2 | 2 | Air Handling Unit
130 | Parent volunteer room | 13 | 0 |  | 480 | 10 | 10 | Air Handling Unit
130 | Parent volunteer room | 13 | 0 |  | 480 | 10 | 10 | Air Handling Unit
131 | Plasma screen room | 9 | 0 |  | 45 | 1 | 1 | Air Handling Unit
131 | Janitor closet |  | 0 |  | 30 | 0 | 0 | Air Handling Unit
132 | Womens room | 25 | 1 |  | 220 | 5 | 5 | Air Handling Unit
132 | Womens Room | 20 | 1 |  | 220 | 5 | 5 | Air Handling Unit
132 | Womens room |  | 0 |  | 220 | 5 | 5 | Air Handling Unit
132 | Womens room |  | 0 |  | 220 | 5 | 5 | Air Handling Unit
133 | Mens room | 49 | 3 |  | 245 | 5 | 5 | Air Handling Unit
133 | Mens room | 38 | 2 |  | 245 | 5 | 5 | Air Handling Unit
135 | Mens Room |  | 0 |  | 245 | 5 | 5 | Air Handling Unit
135 | Mens Room |  | 0 |  | 245 | 5 | 5 | Air Handling Unit
139 | Mens locker | 14 | 0 |  | 375 | 8 | 8 | Air Handling Unit
139 | Mens Locker | 14 | 0 |  | 375 | 8 | 8 | Air Handling Unit
139 | Mens Locker | 15 | 1 |  | 375 | 8 | 8 | Air Handling Unit
139 | Mens Locker | 15 | 1 |  | 375 | 8 | 8 | Air Handling Unit
139 | Mens Locker room |  | 0 |  | 375 | 8 | 8 | Air Handling Unit
139 | Mens locaker room |  | 0 |  | 375 | 8 | 8 | Air Handling Unit
140 | office | 48 | 3 |  | 300 | 6 | 6 | Air Handling Unit
140 | office |  | 0 |  | 300 | 6 | 6 | Air Handling Unit
141 | toilet room | 9 | 0 |  | 90 | 2 | 2 | Air Handling Unit
141 | toilet room |  | 0 |  | 90 | 2 | 2 | Air Handling Unit
142 | Training room | 20 | 1 |  | 375 | 8 | 8 | Air Handling Unit
142 | Training room | 22 | 1 |  | 375 | 8 | 8 | Air Handling Unit
142 | training room |  | 0 |  | 375 | 8 | 8 | Air Handling Unit
143 | Womens Locker | 14 | 0 |  | 750 | 17 | 14 | Air Handling Unit
143 | Womens Locker | 14 | 0 |  | 750 | 17 | 14 | Air Handling Unit
143 | Womens Locker | 15 | 1 |  | 750 | 17 | 15 | Air Handling Unit
143 | Womens LOcker | 16 | 1 |  | 750 | 17 | 16 | Air Handling Unit
143 | Womens locker room |  | 0 |  | 750 | 17 | 17 | Air Handling Unit
143 | Womens locker room |  | 0 |  | 750 | 17 | 17 | Air Handling Unit
144 | Office | 44 | 2 |  | 300 | 6 | 6 | Air Handling Unit
144 | office |  | 0 |  | 300 | 6 | 6 | Air Handling Unit
145 | Toilet Room | 9 | 0 |  | 65 | 1 | 1 | Air Handling Unit
145 | toilet room |  | 0 |  | 65 | 1 | 1 | Air Handling Unit
146 | Corridor | 6 | 0 |  | 150 | 3 | 3 | Air Handling Unit
146 | corridor |  | 0 |  | 150 | 3 | 3 | Air Handling Unit
147 | Fitness center | 44 | 2 |  | 1545 | 35 | 35 | Air Handling Unit
147 | Fitness center | 62 | 4 |  | 1545 | 35 | 35 | Air Handling Unit
147 | Fitness center | 47 | 3 |  | 1545 | 35 | 35 | Air Handling Unit
147 | Fitness center |  | 0 |  | 1545 | 35 | 35 | Air Handling Unit
147 | Fitness center |  | 0 |  | 1545 | 35 | 35 | Air Handling Unit
147 | Fitness center |  | 0 |  | 1545 | 35 | 35 | Air Handling Unit
148 | Visitor locker room | 39 | 2 |  | 485 | 11 | 11 | Air Handling Unit
148 | Visitor locker room | 44 | 2 |  | 485 | 11 | 11 | Air Handling Unit
148 | visitor locaker room |  | 0 |  | 485 | 11 | 11 | Air Handling Unit
148 | Visitor locaker room |  | 0 |  | 485 | 11 | 11 | Air Handling Unit
148 | visitor locker room |  | 0 |  | 485 | 11 | 11 | Air Handling Unit
149 | IDF | 15 | 1 |  | 50 | 1 | 1 | Air Handling Unit
149 | IDF |  | 0 |  | 50 | 1 | 1 | Air Handling Unit
150 | work shop |  | 0 |  | 155 | 3 | 3 | Air Handling Unit
151 | Custodial office |  | 0 |  | 155 | 3 | 3 | Air Handling Unit
152 | Corridor | 34 | 2 |  | 2055 | 46 | 34 | Air Handling Unit
152 | Corridor | 28 | 1 |  | 2055 | 46 | 28 | Air Handling Unit
152 | Corridor | 28 | 1 |  | 2055 | 46 | 28 | Air Handling Unit
155 | Corridor |  | 0 |  | 145 | 3 | 3 | Air Handling Unit
156 | Locker room |  | 0 |  | 60 | 1 | 1 | Air Handling Unit
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit
158 | Dishwashing |  | 0 |  | 390 | 8 | 8 | Air Handling Unit
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit
160 | Dishwashing |  | 0 |  | 390 | 8 | 8 | Air Handling Unit
161 | Serving |  | 0 |  | 695 | 15 | 15 | Air Handling Unit
161 | Serving |  | 0 |  | 695 | 15 | 15 | Air Handling Unit
161 | Serving |  | 0 |  | 695 | 15 | 15 | Air Handling Unit
162 | Kitchen office |  | 0 |  | 80 | 1 | 1 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit
164 | Faculty dining |  | 0 |  | 610 | 13 | 13 | Air Handling Unit
164 | Faculty dining |  | 0 |  | 610 | 13 | 13 | Air Handling Unit
166 | Mens Room | 71 | 4 |  | 220 | 5 | 5 | Air Handling Unit
167 | Womens Room | 50 | 3 |  | 245 | 5 | 5 | Air Handling Unit
170 | Special Education | 24 | 1 |  | 1205 | 27 | 24 | Air Handling Unit
170 | Special Education | 21 | 1 |  | 1205 | 27 | 21 | Air Handling Unit
170 | Special Education | 31 | 2 |  | 1205 | 27 | 27 | Air Handling Unit
170 | Special Education | 30 | 2 |  | 1205 | 27 | 27 | Air Handling Unit
173 | Driver education lab | 70 | 4 |  | 1200 | 27 | 27 | Air Handling Unit
173 | Driver education lab | 70 | 4 |  | 1200 | 27 | 27 | Air Handling Unit
173 | Driver education lab | 69 | 4 |  | 1200 | 27 | 27 | Air Handling Unit
173 | Driver education lab | 65 | 4 |  | 1200 | 27 | 27 | Air Handling Unit
174 | Science Prep | 59 | 3 |  | 200 | 4 | 4 | Air Handling Unit
175 | Science Lab | 55 | 3 |  | 1505 | 34 | 34 | Air Handling Unit
175 | Science LAB | 54 | 3 |  | 1505 | 34 | 34 | Air Handling Unit
175 | science lab | 47 | 3 |  | 1505 | 34 | 34 | Air Handling Unit
175 | science lab | 41 | 2 |  | 1505 | 34 | 34 | Air Handling Unit
175 | science lab | 59 | 3 |  | 1505 | 34 | 34 | Air Handling Unit
175 | science lab | 63 | 4 |  | 1505 | 34 | 34 | Air Handling Unit
177 | table storage | 0 | 0 |  | 610 | 13 | 0 | Air Handling Unit
177 | table storage | 0 | 0 |  | 610 | 13 | 0 | Air Handling Unit
178 | teacher storage | 0 | 0 |  | 125 | 2 | 0 | Air Handling Unit
179 | services room | 0 | 0 |  | 160 | 3 | 0 | Air Handling Unit
180 | IDF closet | 0 | 0 |  | 155 | 3 | 0 | Air Handling Unit
181 | School store | 0 | 0 |  | 200 | 4 | 0 | Air Handling Unit
183 | Computer lab |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
183 | Computer lab | 374 | 24 |  | 900 | 20 | 20 | Air Handling Unit
183 | Computer lab | 362 | 24 |  | 900 | 20 | 20 | Air Handling Unit
183 | Computer lab | 477 | 31 |  | 900 | 20 | 20 | Air Handling Unit
183 | Computer lab | 477 | 31 |  | 900 | 20 | 20 | Air Handling Unit
184 | Interactive learning center | 667 | 44 |  | 2800 | 63 | 63 | Air Handling Unit
184 | Interactive learning center | 473 | 31 |  | 2800 | 63 | 63 | Air Handling Unit
184 | Interactive learning center | 570 | 38 |  | 2800 | 63 | 63 | Air Handling Unit
184 | Interactive learning center | 536 | 35 |  | 2800 | 63 | 63 | Air Handling Unit
184 | Interactive learning center | 417 | 27 |  | 2800 | 63 | 63 | Air Handling Unit
185 | Individual reading | 37 | 2 |  | 390 | 8 | 8 | Air Handling Unit
185 | Individual reading | 32 | 2 |  | 390 | 8 | 8 | Air Handling Unit
185 | Individual reading | 27 | 1 |  | 390 | 8 | 8 | Air Handling Unit
185 | Individual reading | 31 | 2 |  | 390 | 8 | 8 | Air Handling Unit
186 | Literacy Nook | 35 | 2 |  | 900 | 20 | 20 | Air Handling Unit
186 | Literacy Nook | 28 | 1 |  | 900 | 20 | 20 | Air Handling Unit
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit
186 | Literacy Nook | 30 | 2 |  | 900 | 20 | 20 | Air Handling Unit
186 | Literacy Nook | 14 | 0 |  | 900 | 20 | 14 | Air Handling Unit
187 | Copy Room | 111 | 7 |  | 250 | 5 | 5 | Air Handling Unit
187 | Copy Room | 86 | 5 |  | 250 | 5 | 5 | Air Handling Unit
188 | Conference room | 87 | 5 |  | 200 | 4 | 4 | Air Handling Unit
188 | Conferenceroom | 90 | 6 |  | 200 | 4 | 4 | Air Handling Unit
189 | Visitor room | 165 | 11 |  | 605 | 13 | 13 | Air Handling Unit
189 | Visitor room | 202 | 13 |  | 605 | 13 | 13 | Air Handling Unit
189 | Visitor room | 177 | 11 |  | 605 | 13 | 13 | Air Handling Unit
190 | ILC office | 120 | 8 |  | 135 | 3 | 3 | Air Handling Unit
191 | storage | 112 | 7 |  | 170 | 3 | 3 | Air Handling Unit
192 |  | 1210 |  |  |  |  | 1210 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit
201 | Computer tech |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit
201 | Computer tech |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit
201 | Computer tech |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit
203 | Teachers Copy center |  | 0 |  | 300 | 6 | 6 | Air Handling Unit
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit
205 | Storage |  | 0 |  | 150 | 3 | 3 | Air Handling Unit
207 | Clerical |  | 0 |  | 100 | 2 | 2 | Air Handling Unit
207 | Clerical |  | 0 |  | 100 | 2 | 2 | Air Handling Unit
208 | Office |  | 0 |  | 120 | 2 | 2 | Air Handling Unit
209 | Roster Room |  | 0 |  | 120 | 2 | 2 | Air Handling Unit
210 |  |  |  |  | 200 |  | 0 | Air Handling Unit
211 |  |  |  |  | 200 |  | 0 | Air Handling Unit
212 | Staff Room |  | 0 |  | 120 | 2 | 2 | Air Handling Unit
213 | Staff Room |  | 0 |  | 120 | 2 | 2 | Air Handling Unit
214 | Assistant Principle office |  | 0 |  | 120 | 2 | 2 | Air Handling Unit
215 |  |  |  |  | 120 |  | 0 | Air Handling Unit
216 | Rest Room |  | 0 |  | 50 | 1 | 1 | Air Handling Unit
217 | Records |  | 0 |  | 300 | 6 | 6 | Air Handling Unit
218 |  |  |  |  | 120 |  | 0 | Air Handling Unit
219 | PE Director |  | 0 |  | 150 | 3 | 3 | Air Handling Unit
220 |  |  |  |  | 150 |  | 0 | Air Handling Unit
221 |  |  |  |  | 120 |  | 0 | Air Handling Unit
222 |  |  |  |  | 120 |  | 0 | Air Handling Unit
223 | Counselor office |  | 0 |  | 120 | 2 | 2 | Air Handling Unit
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
225 |  |  |  |  | 450 |  | 0 | Air Handling Unit
225 |  |  |  |  | 450 |  | 0 | Air Handling Unit
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit
227 | General classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
227 | General Classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
227 | General Classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
227 | General Classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
228 | Art Storage |  | 0 |  | 200 | 4 | 4 | Air Handling Unit
229 | [6 empty] | 0 | Air Handling Unit
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit
231A | [6 empty] | 0 | Air Handling Unit
231A | [6 empty] | 0 | Air Handling Unit
231B | Special education |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
231B | Special education |  | 0 |  | 900 | 20 | 20 | Air Handling Unit
237 | Mens Room | 57 | 3 |  | 250 | 5 | 5 | Air Handling Unit
240 | Womens Room | 76 | 5 |  | 255 | 5 | 5 | Air Handling Unit
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit
242 | chemistry classroom | 53 | 3 |  | 1500 | 34 | 34 | Air Handling Unit
242 | chemistry classroom | 47 | 3 |  | 1500 | 34 | 34 | Air Handling Unit
242 | chemistry classroom | 51 | 3 |  | 1500 | 34 | 34 | Air Handling Unit
242 | chemistry classroom | 56 | 3 |  | 1500 | 34 | 34 | Air Handling Unit
242 | chemistry classroom | 56 | 3 |  | 1500 | 34 | 34 | Air Handling Unit
242 | chemistry classroom | 41 | 2 |  | 1500 | 34 | 34 | Air Handling Unit
243 | Storage | 84 | 5 |  | 200 | 4 | 4 | Air Handling Unit
244 | Planning | 72 | 4 |  | 290 | 6 | 6 | Air Handling Unit
245 | Biology class | 97 | 6 |  | 245 | 5 | 5 | Air Handling Unit
245 | Biology class | 97 | 6 |  | 1290 | 29 | 29 | Air Handling Unit
245 | Biology class | 78 | 5 |  | 1290 | 29 | 29 | Air Handling Unit
245 | Biology class | 83 | 5 |  | 1290 | 29 | 29 | Air Handling Unit
245 | Biology class | 93 | 6 |  | 1290 | 29 | 29 | Air Handling Unit
245 | Biology class | 51 | 3 |  | 1290 | 29 | 29 | Air Handling Unit
246 | General classroom | 67 | 4 |  | 900 | 20 | 20 | Air Handling Unit
246 | General classroom | 50 | 3 |  | 900 | 20 | 20 | Air Handling Unit
246 | General classroom | 66 | 4 |  | 900 | 20 | 20 | Air Handling Unit
246 | General classroom | 63 | 4 |  | 900 | 20 | 20 | Air Handling Unit
247 | General classroom | 68 | 4 |  | 900 | 20 | 20 | Air Handling Unit
247 | General classroom | 72 | 4 |  | 900 | 20 | 20 | Air Handling Unit
247 | General classroom | 69 | 4 |  | 900 | 20 | 20 | Air Handling Unit
247 | General classroom | 81 | 5 |  | 900 | 20 | 20 | Air Handling Unit
248 | N/A | 107 | 7 |  | 135 | 3 | 3 | Air Handling Unit
249 | General classroom | 59 | 3 |  | 745 | 16 | 16 | Air Handling Unit
249 | General classroom | 62 | 4 |  | 745 | 16 | 16 | Air Handling Unit
249 | General classroom | 90 | 6 |  | 745 | 16 | 16 | Air Handling Unit
249 | General classroom | 77 | 5 |  | 745 | 16 | 16 | Air Handling Unit
250 | General classroom | 68 | 4 |  | 795 | 18 | 18 | Air Handling Unit
250 | General classroom | 60 | 4 |  | 795 | 18 | 18 | Air Handling Unit
250 | General classroom | 80 | 5 |  | 795 | 18 | 18 | Air Handling Unit
250 | General classroom | 83 | 5 |  | 795 | 18 | 18 | Air Handling Unit
251 | N/A | 173 | 11 |  |  | 0 | 0 | Air Handling Unit
252 | General classroom | 57 | 3 |  | 800 | 18 | 18 | Air Handling Unit
252 | General classroom | 56 | 3 |  | 800 | 18 | 18 | Air Handling Unit
252 | General classroom | 88 | 5 |  | 800 | 18 | 18 | Air Handling Unit
252 | General classroom | 79 | 5 |  | 800 | 18 | 18 | Air Handling Unit
253 | Corridor | 26 | 1 |  | 6010 | 136 | 26 | Air Handling Unit
253 | Corridor | 25 | 1 |  | 6010 | 136 | 25 | Air Handling Unit
253 | Corridor | 28 | 1 |  | 6010 | 136 | 28 | Air Handling Unit
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit
302 | SPR |  | 0 |  | 135 | 3 | 3 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit
305 | SPR |  | 0 |  | 135 | 3 | 3 | Air Handling Unit
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit
308 | Teacher storage |  | 0 |  | 90 | 2 | 2 | Air Handling Unit
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit
315 | Electrical room | 27 | 1 |  | 120 | 2 | 2 | Air Handling Unit
316 | IDF closet | 29 | 1 |  | 170 | 3 | 3 | Air Handling Unit
317 | Deans Office | 32 | 2 |  | 140 | 3 | 3 | Air Handling Unit
318 | Mens room | 107 | 7 |  | 245 | 5 | 5 | Air Handling Unit
321 | Womens Room | 110 | 7 |  | 250 | 5 | 5 | Air Handling Unit
322 | General classroom | 102 | 6 |  | 815 | 18 | 18 | Air Handling Unit
322 | General classroom | 105 | 7 |  | 815 | 18 | 18 | Air Handling Unit
322 | General classroom | 65 | 4 |  | 815 | 18 | 18 | Air Handling Unit
322 | General classroom | 73 | 4 |  | 815 | 18 | 18 | Air Handling Unit
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit
324 | Science Prep | 54 | 3 |  | 200 | 4 | 4 | Air Handling Unit
324 | Science Prep | 53 | 3 |  | 200 | 4 | 4 | Air Handling Unit
325 | Physics classroom | 16 | 1 |  | 1505 | 34 | 16 | Air Handling Unit
325 | Physics classroom | 116 | 7 |  | 1505 | 34 | 34 | Air Handling Unit
325 | Physics classroom | 14 | 0 |  | 1505 | 34 | 14 | Air Handling Unit
325 | Physics classroom | 13 | 0 |  | 1505 | 34 | 13 | Air Handling Unit
325 | Physics classroom | 13 | 0 |  | 1505 | 34 | 13 | Air Handling Unit
325 | Physics classroom | 14 | 0 |  | 1505 | 34 | 14 | Air Handling Unit
326 | General classroom | 86 | 5 |  | 825 | 18 | 18 | Air Handling Unit
326 | General classroom | 85 | 5 |  | 825 | 18 | 18 | Air Handling Unit
326 | General classroom | 99 | 6 |  | 825 | 18 | 18 | Air Handling Unit
326 | General classroom | 47 | 3 |  | 825 | 18 | 18 | Air Handling Unit
327 | General classroom | 64 | 4 |  | 795 | 18 | 18 | Air Handling Unit
327 | General classroom | 58 | 3 |  | 795 | 18 | 18 | Air Handling Unit
327 | General classroom | 62 | 4 |  | 795 | 18 | 18 | Air Handling Unit
327 | General classroom | 43 | 2 |  | 795 | 18 | 18 | Air Handling Unit
328 | N/A | 159 | 10 |  | 135 | 3 | 3 | Air Handling Unit
329 | General classroom | 64 | 4 |  | 800 | 18 | 18 | Air Handling Unit
329 | General classroom | 59 | 3 |  | 800 | 18 | 18 | Air Handling Unit
329 | General classroom | 65 | 4 |  | 135 | 3 | 3 | Air Handling Unit
329 | General classroom | 68 | 4 |  | 800 | 18 | 18 | Air Handling Unit
330 | General classroom | 70 | 4 |  | 795 | 18 | 18 | Air Handling Unit
330 | General classroom | 64 | 4 |  | 795 | 18 | 18 | Air Handling Unit
330 | General classroom | 74 | 4 |  | 795 | 18 | 18 | Air Handling Unit
330 | General classroom | 81 | 5 |  | 795 | 18 | 18 | Air Handling Unit
331 | General classroom | 62 | 4 |  | 135 | 3 | 3 | Air Handling Unit
331 | General classroom | 69 | 4 |  | 135 | 3 | 3 | Air Handling Unit
331 | General classroom | 73 | 4 |  | 135 | 3 | 3 | Air Handling Unit
331 | General classroom | 73 | 4 |  | 135 | 3 | 3 | Air Handling Unit
333 | Corridor | 79 | 5 |  | 5535 | 125 | 79 | Air Handling Unit
333 | Corridor | 66 | 4 |  | 5535 | 125 | 66 | Air Handling Unit
333 | Corridor | 81 | 5 |  | 5535 | 125 | 81 | Air Handling Unit
360 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
360 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
360 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Corridor | 9 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Vending machines |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Corridor | 28 | 1 |  |  | 0 | 0 | Air Handling Unit
- | Corridor | 11 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Kitchen storage |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Gymnasium | 5058 | 337 |  |  | 0 | 0 | Air Handling Unit
- | Storage |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Fitness center |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Fitness center |  | 0 |  |  | 0 | 0 | Air Handling Unit

## Sharswood
Sheet Last Modified: | 2021-04-22
School: | George W. Sharswood Elementary School |  |  | House fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Building Engineer | 0 | 0 |  | 1288 | 29 | 0 | House Fan
- | Cafeteria | 0 | 0 | Yes | 2000 | 45 | 45 | House Fan
- | Kitchen Storage | 0 | 0 |  | 121 | 2 | 0 | House Fan
- | Art Room | 1817 | 121 |  | 1242 | 28 | 28 | House Fan
B9A & B9B | Classroom | 2017 | 134 |  | 1242 | 28 | 28 | House Fan
- | Gym | 2219 | 147 |  | 2160 | 49 | 49 | House Fan
- | Main Office | 0 | 0 | Yes | 552 | 12 | 12 | House Fan
- | Nurse Office | 0 | 0 | Yes | 550 | 12 | 12 | House Fan
- | Nurse Exam | 0 | 0 | Yes | 299 | 6 | 6 | House Fan
- | Principal's Office | 0 | 0 | Yes | 288 | 6 | 6 | House Fan
101 | Classroom | 1018 | 67 |  | 550 | 12 | 12 | House Fan
102 | Classroom | 932 | 62 |  | 550 | 12 | 12 | House Fan
103 | Classroom | 484 | 32 |  | 550 | 12 | 12 | House Fan
104 | Classroom |  | 0 | Yes | 276 | 6 | 6 | House Fan
105 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | House Fan
106 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | House Fan
107 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | House Fan
108 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | House Fan
109 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan
114 | Classroom | 0 | 0 | Yes | 748 | 17 | 17 | House Fan
- | Auditorium | 0 | 0 |  | 2350 | 53 | 0 | House Fan
216 | Music Rm | 0 | 0 | Yes | 1500 | 34 | 34 | House Fan
- | Teacher's Lounge | 0 | 0 |  | 440 | 10 | 0 | House Fan
217 | Classroom | 0 | 0 | Yes | 644 | 14 | 14 | House Fan
219 | Classroom | 0 | 0 | Yes | 744 | 16 | 16 | House Fan
223 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan
224 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | House Fan
225 | Classroom | 695 | 46 |  | 684 | 15 | 15 | House Fan
226 | Classroom | 881 | 58 |  | 684 | 15 | 15 | House Fan
227 | Classroom | 429 | 28 |  | 684 | 15 | 15 | House Fan
228 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan
329 | Classroom | 281 | 18 |  | 696 | 15 | 15 | House Fan
329A | Office | 0 | 0 | Yes | 120 | 2 | 2 | House Fan
330 | Classroom | 811 | 54 |  | 696 | 15 | 15 | House Fan
331 | Classroom | 276 | 18 |  | 696 | 15 | 15 | House Fan
332 | Classroom | 0 | 0 | Yes | 576 | 13 | 13 | House Fan
333 | Classroom | 0 | 0 | Yes | 775 | 17 | 17 | House Fan
334 | Classroom | 0 | 0 | Yes | 783 | 17 | 17 | House Fan
335 | Classroom | 0 | 0 | Yes | 783 | 17 | 17 | House Fan
336 | Classroom | 0 | 0 | Yes | 783 | 17 | 17 | House Fan
337 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan
338 | Classroom | 0 | 0 | Yes | 552 | 12 | 12 | House Fan
339 | Classroom | 368 | 24 |  | 672 | 15 | 15 | House Fan
340 | Classroom | 326 | 21 |  | 576 | 13 | 13 | House Fan
341 | Classroom | 156 | 10 |  | 576 | 13 | 10 | House Fan
341A | Classroom | 0 | 0 |  | 120 | 2 | 0 | House Fan
342A | Classroom | 0 | 0 |  | 288 | 6 | 0 | House Fan
342B | Classroom | 0 | 0 | Yes | 432 | 9 | 9 | House Fan

## Shawmont
Sheet Last Modified: | 2021-04-26
School: | Shawmont Elementary-Middle School
Vendor: | EMCOR Fluidics | Retest | 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | CLASS | 0 | 0 | Yes | 1033 | 23 | 23 | Univent
103 | CLASS | 323 | 21 |  | 687 | 15 | 15 | Univent
104 | CLASS | 337 | 22 |  | 568 | 12 | 12 | Univent
105 | Office | 0 | 0 | Yes | 359 | 8 | 8
106 | CLASS | 336 | 22 |  | 687 | 15 | 15 | Univent
107 | CLASS | 327 | 21 |  | 705 | 16 | 16 | Univent
108 | CLASS | 308 | 20 |  | 750 | 17 | 17 | Univent
201 | CLASS | 312 | 20 |  | 670 | 15 | 15 | Univent
202 | CLASS | 323 | 21 |  | 536 | 12 | 12 | Univent
203 | CLASS | 372 | 24 |  | 794 | 18 | 18 | Univent
204 | CLASS | 273 | 18 |  | 794 | 18 | 18 | Univent
205 | Therapy | 340 | 22 |  | 370 | 8 | 8 | Univent
206 | CLASS | 325 | 21 |  | 670 | 15 | 15 | Univent
207 | CLASS | 222 | 14 | Yes | 675 | 15 | 15 | Univent
208 | CLASS | 272 | 18 |  | 675 | 15 | 15 | Univent
209 | CLASS | 252 | 16 |  | 670 | 15 | 15 | Univent
300 | CLASS | 281 | 18 |  | 503 | 11 | 11 | Univent
301 | CLASS | 312 | 20 |  | 690 | 15 | 15 | Univent
302 | CLASS | 287 | 19 |  | 704 | 16 | 16 | Univent
303 | CLASS | 276 | 18 |  | 695 | 15 | 15 | Univent
304 | CLASS | 371 | 24 |  | 797 | 18 | 18 | Univent
305 | Office | 96 | 6 | Yes | 448 | 10 | 10 | Univent
305-A | Classroom | 313 | 20 |  | 814 | 18 | 18 | Univent
306 | CLASS | 296 | 19 |  | 675 | 15 | 15 | Univent
307 | CLASS | 279 | 18 |  | 675 | 15 | 15 | Univent
308 | CLASS | 0 | 0 | Yes | 695 | 15 | 15 | Univent
309 | CLASS | 370 | 24 |  | 690 | 15 | 15 | Univent
310 | CLASS | 275 | 18 | Yes | 1103 | 25 | 25 | Univent
311 | CLASS | 292 | 19 |  | 935 | 21 | 19 | Univent
312 | CLASS | 0 | 0 | Yes | 1039 | 23 | 23 | Univent
313 | CLASS | 0 | 0 | Yes | 1036 | 23 | 23 | Univent
314 | CLASS | 433 | 28 |  | 1012 | 23 | 23 | Univent
315 | CLASS | 388 | 25 |  | 1184 | 26 | 25 | Univent
- | AUDITORIUM | 1331 | 88 |  | 3193 | 72 | 72 | Air Handling Unit
- | BAND RM | 0 | 0 | Yes | 934 | 21 | 21 | Univent
- | COMPUTER LAB | 0 | 0 | Yes | 1103 | 25 | 25 | Univent
- | GYM | 5749 | 383 | Yes | 2610 | 59 | 59 | Air Handling Unit
- | LIBRARY | 750 | 50 |  | 1804 | 41 | 41 | Univent
B-1 | Strings Room | 343 | 22 |  | 641 | 14 | 14 | Univent
B-2 | Music Room | 0 | 0 | Yes | 518 | 11 | 11 | Univent
B-3 | Band Room | 396 | 26 |  | 153 | 3 | 3 | Univent
B-4 | Band Room | 281 | 18 |  | 940 | 21 | 18 | Univent
B-6 | Classroom | 395 | 26 |  | 803 | 18 | 18 | Univent
- | Cafeteria | 1132 | 75 |  | 4090 | 92 | 75 | Univent
- | Staff Lounge | 0 | 0 | Yes | 364 | 8 | 8 | Univent
- | Nurse |  | 0 | Yes | 287 | 6 | 6
- | Principal's Office |  | 0 | Yes | 210 | 4 | 4
- | Main Office |  | 0 | Yes | 379 | 8 | 8

## Sheppard
Sheet Last Modified: | 2021-04-06
School: | Isaac A. Sheppard Elementary School
Vendor: | EMCOR Fluidics | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 661 | 44 |  | 768 | 17 | 17 | House Fan
101 | Classroom | 894 | 59 |  | 682 | 15 | 15 | House Fan
102 | Classroom | 910 | 60 |  | 682 | 15 | 15 | House Fan
103 | Classroom | 578 | 38 |  | 682 | 15 | 15 | House Fan
200 | Classroom | 665 | 44 |  | 704 | 16 | 16 | House Fan
201 | Classroom | 595 | 39 |  | 704 | 16 | 16 | House Fan
202 | Classroom | 1004 | 66 |  | 682 | 15 | 15 | House Fan
203 | Classroom | 951 | 63 |  | 682 | 15 | 15 | House Fan
204 | Classroom | 949 | 63 |  | 682 | 15 | 15 | House Fan
205 | Classroom | 661 | 44 |  | 682 | 15 | 15 | House Fan
206 | Classroom | 844 | 56 |  | 704 | 16 | 16 | House Fan
300 | Classroom | 840 | 56 |  | 875 | 19 | 19 | House Fan
301 | Classroom | 717 | 47 |  | 875 | 19 | 19 | House Fan
302 | Classroom | 963 | 64 |  | 836 | 19 | 19 | House Fan
303 | Classroom | 762 | 50 |  | 836 | 19 | 19 | House Fan
304 | Classroom | 998 | 66 |  | 704 | 16 | 16 | House Fan
305 | Classroom | 847 | 56 |  | 704 | 16 | 16 | House Fan
306 | Classroom | 636 | 42 |  | 704 | 16 | 16 | House Fan
- | Auditorium | 1843 | 122 |  | 1176 | 26 | 26 | House Fan
Main Office | Office |  | 0 | Yes | 255 | 5 | 5 | Air Purifier
Nurse Office | Office |  | 0 | Yes | 122 | 2 | 2 | Air Purifier
Principal Office | Office |  | 0 | Yes | 183 | 4 | 4 | Air Purifier
- | Library | 1317 | 87 |  | 851 | 19 | 19 | House Fan
- | Lunch Room/Cafeteria | 1498 | 99 |  | 1311 | 29 | 29 | House Fan
- | Server Room | 0 | 0 |  | 0 | 0 | 0 | Minisplit Air Handling Unit

## Sheridan
Sheet Last Modified: | 2021-04-07
School: | Philip Sheridan Elementary School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Room | 0 | 0 | Yes | 768 | 17 | 17 | House Fan
102 | Room | 1116 | 74 |  | 768 | 17 | 17 | House Fan
103 | Room | 921 | 61 |  | 768 | 17 | 17 | House Fan
104 | Room | 749 | 49 |  | 720 | 16 | 16 | House Fan
105 | Room | 693 | 46 |  | 720 | 16 | 16 | House Fan
106 | Classroom | 1006 | 67 |  | 768 | 17 | 17 | House Fan
107 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan
108 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan
109 | Classroom | 861 | 57 |  | 768 | 17 | 17 | House Fan
110 | Classroom | 376 | 25 |  | 768 | 17 | 17 | House Fan
Main Office | Office |  | 0 | Yes | 448 | 10 | 10 | House Fan
110 | Principal office | 597 | 39 |  | 216 | 4 | 4 | House Fan
111 | Nurse | 0 | 0 | Yes | 312 | 7 | 7 | House Fan
201 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan
202 | Classroom | 877 | 58 |  | 768 | 17 | 17 | House Fan
203 | Classroom | 981 | 65 |  | 720 | 16 | 16 | House Fan
204 | Classroom | 760 | 50 |  | 720 | 16 | 16 | House Fan
205 | Classroom | 737 | 49 |  | 720 | 16 | 16 | House Fan
206 | Classroom | 999 | 66 |  | 768 | 17 | 17 | House Fan
207 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan
208 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan
209 | Classroom | 1162 | 77 |  | 768 | 17 | 17 | House Fan
209 1/2 | Office |  | 0 | Yes | 220 | 5 | 5 | House Fan
210 | Classroom | 926 | 61 |  | 768 | 17 | 17 | House Fan
210 1/2 | Office |  | 0 |  | 220 | 5 | 0 | House Fan
211 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan
301 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan
302 | Classroom | 1253 | 83 |  | 768 | 17 | 17 | House Fan
303 | Classroom | 1038 | 69 |  | 720 | 16 | 16 | House Fan
304 | Classroom | 746 | 49 |  | 720 | 16 | 16 | House Fan
305 | Classroom | 811 | 54 |  | 720 | 16 | 16 | House Fan
306 | Classroom | 1007 | 67 |  | 768 | 17 | 17 | House Fan
307 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan
308 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan
309 | Classroom | 894 | 59 |  | 768 | 17 | 17 | House Fan
310 | Classroom | 1334 | 88 |  | 768 | 17 | 17 | House Fan
311 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan
- | Basement East Side |  | 0 |  | 567 | 12 | 0 | House Fan
- | Basement West Side |  | 0 |  | 567 | 12 | 0 | House Fan

## SLA @ Beeber
Sheet Last Modified: | 2021-04-19
School: | SLA @ Beeber
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom |  | 0 |  | 1200 | 27 | 0
101 | Classroom |  | 0 |  | 1150 | 26 | 0
102 | Classroom |  | 0 |  | 925 | 21 | 0
102A | Classroom |  | 0 |  | 720 | 16 | 0
103 | Classroom |  | 0 |  | 1636 | 37 | 0
104 | Classroom |  | 0 |  | 875 | 19 | 0
105 | Classroom |  | 0 |  | 909 | 20 | 0
106 | Classroom |  | 0 | Yes | 966 | 21 | 21
106A | Classroom |  | 0 | Yes | 610 | 13 | 13
107 | Classroom |  | 0 |  | 912 | 20 | 0
107A | Classroom |  | 0 |  | 720 | 16 | 0
107B | Classroom |  | 0 |  | 360 | 8 | 0
108 | Classroom |  | 0 |  | 912 | 20 | 0
109 | Classroom |  | 0 |  | 700 | 15 | 0
200 | Classroom |  | 0 | Yes | 638 | 14 | 14
201 | Office |  | 0 | Yes | 187 | 4 | 4
202 | Classroom |  | 0 | Yes | 1128 | 25 | 25
203 | Classroom |  | 0 |  | 1128 | 25 | 0
203A | Classroom |  | 0 | Yes | 720 | 16 | 16
203B | Classroom |  | 0 | Yes | 360 | 8 | 8
204 | Classroom |  | 0 | Yes | 664 | 15 | 15
204A | Nurse office |  | 0 |  | 187 | 4 | 0
205 | Office |  | 0 | Yes | 360 | 8 | 8
206-208 | Office |  | 0 |  | 996 | 22 | 0
- | Main Office |  | 0 | Yes | 335 | 7 | 7
- | Principal Office |  | 0 |  | 660 | 15 | 0
Secretary | Office |  | 0 | Yes |  | 0 | 0
Conference Room | Conference Room |  | 0 | Yes |  | 0 | 0
Cafeteria | Cafeteria |  | 0 |  | 7014 | 159 | 0
209-210 | Library |  | 0 | Yes | 1872 | 42 | 42
211 | Classroom |  | 0 |  | 984 | 22 | 0
212 | Classroom |  | 0 |  | 720 | 16 | 0
213-214 | Classroom |  | 0 |  | 1518 | 34 | 0
214A-B | Classroom |  | 0 |  | 1021 | 23 | 0
215 | Office |  | 0 |  | 187 | 4 | 0
216 | Classroom |  | 0 |  | 638 | 14 | 0
217 | Classroom |  | 0 |  | 816 | 18 | 0
218 | Classroom |  | 0 | Yes | 744 | 16 | 16
219 | Classroom |  | 0 | Yes | 768 | 17 | 17
220 | Classroom |  | 0 | Yes | 768 | 17 | 17
221 | Classroom |  | 0 | Yes | 768 | 17 | 17
222 | Classroom |  | 0 | Yes | 816 | 18 | 18
223 | Classroom |  | 0 | Yes |  | 0 | 0
224 | Classroom |  | 0 | Yes |  | 0 | 0
316 | Office |  | 0 |  | 187 | 4 | 0
317 | Classroom |  | 0 |  | 665 | 15 | 0
318 | Classroom |  | 0 |  | 836 | 19 | 0
319-320 | Classroom |  | 0 |  | 1488 | 33 | 0
321 | Classroom |  | 0 |  | 749 | 17 | 0
322 | Classroom |  | 0 |  | 766 | 17 | 0
323 | Classroom |  | 0 |  | 808 | 18 | 0
324 | Classroom |  | 0 |  | 668 | 15 | 0
300 | Office |  | 0 |  | 187 | 4 | 0
301-303 | Classroom |  | 0 | Yes | 2072 | 47 | 47
302 | Classroom |  | 0 | Yes | 720 | 16 | 16
303A-B | Classroom |  | 0 | Yes | 1072 | 24 | 24
304 | Classroom |  | 0 | Yes | 1009 | 22 | 22
305 | Classroom |  | 0 |  | 989 | 22 | 0
306 | Classroom |  | 0 |  | 1001 | 22 | 0
307 | Classroom |  | 0 |  | 1361 | 30 | 0
308 | Office |  | 0 |  | 200 | 4 | 0
309-310 | Classroom |  | 0 | Yes | 2085 | 47 | 47
311 | Office |  | 0 | Yes | 651 | 14 | 14
312 | Office |  | 0 |  | 300 | 6 | 0
313-315 | Classroom |  | 0 |  | 2227 | 50 | 0
314A | Classroom |  | 0 |  | 1126 | 25 | 0

## Solis-Cohen
Sheet Last Modified: | 2021-04-23
School: | Solis-Cohen Elementary School
Vendor: | Chadwick | Main Exhaust | Main Exhaust Part 2
School: | Solis-Cohen Elementary School- Little School House
Vendor: | Chadwick | Chadwick Part 2 | Chadwick Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Solis-Cohen Main Building
- | Main Office |  | 0 |  | 120 | 2 | 0 | N/A
1 | classroom |  | 0 |  | 914.25 | 20 | 0 | N/A
2 | classroom |  | 0 |  | 914 | 20 | 0 | N/A
3 | Classroom |  | 0 |  | 914 | 20 | 0 | N/A
4 | classroom |  | 0 |  | 914 | 20 | 0 | N/A
5 | classroom |  | 0 |  | 914 | 20 | 0 | N/A
6 | classroom |  | 0 |  | 731 | 16 | 0 | N/A
7 | classroom |  | 0 |  | 731 | 16 | 0 | N/A
8 | classroom |  | 0 |  | 731 | 16 | 0 | N/A
9 | classroom |  | 0 |  | 731 | 16 | 0 | N/A
9A | classroom |  | 0 |  | 731 | 16 | 0 | N/A
10 | classroom |  | 0 |  | 731 | 16 | 0 | N/A
11 | classroom |  | 0 |  | 731 | 16 | 0 | N/A
12 | classroom |  | 0 |  | 731 | 16 | 0 | N/A
13 | classroom |  | 0 |  | 731 | 16 | 0 | N/A
14 | classroom |  | 0 |  | 731 | 16 | 0 | N/A
26 | Classroom |  | 0 |  | 914 | 20 | 0 | N/A
27 | Classroom |  | 0 |  | 914 | 20 | 0 | N/A
- | Esol Room |  | 0 |  | 806 | 18 | 0 | N/A
- | Nurses Office |  | 0 |  | 1116 | 25 | 0 | N/A
- | Gym |  | 0 |  | 5355 | 121 | 0 | N/A
- | Cafeteria |  | 0 |  | 2660 | 60 | 0 | N/A
- | Auditorium |  | 0 |  | 5036 | 114 | 0 | N/A
- | Counselors Office A |  | 0 |  | 352 | 8 | 0 | N/A
- | Counselors Office B |  | 0 |  | 352 | 8 | 0 | N/A
Solis-Cohen LSH
100B | Lobby | 88 | 5 |  | 196 | 4 | 4 | Air Handling Unit
101A | Reception Office | 30 | 2 |  | 256 | 5 | 2 | Air Handling Unit
101B | Clerical Office | 56 | 3 |  | 336 | 7 | 3 | Air Handling Unit
101C | Asst. Principals Office | 32 | 2 |  | 598 | 13 | 2 | Air Handling Unit
101D | Nurses Office | 32 | 2 |  | 256 | 5 | 2 | Air Handling Unit
102 | Classroom | 287 | 19 |  | 858 | 19 | 19 | Univent
103 | Classroom | 276 | 18 |  | 858 | 19 | 18 | Univent
104 | Classroom | 276 | 18 |  | 858 | 19 | 18 | Univent
105 | Classroom | 292 | 19 |  | 858 | 19 | 19 | Univent
106 | Classroom | 280 | 18 |  | 858 | 19 | 18 | Univent
107 | Classroom | 274 | 18 |  | 858 | 19 | 18 | Univent
108 | Classroom | 275 | 18 |  | 858 | 19 | 18 | Univent
110 | Faculty Dining | 45 | 3 |  | 640 | 14 | 3 | Air Handling Unit
121 | Classroom | 282 | 18 |  | 1092 | 24 | 18 | Univent
122 | Classroom | 289 | 19 |  | 1092 | 24 | 19 | Univent
123 | Classroom | 290 | 19 |  | 1092 | 24 | 19 | Univent
124 | Classroom | 292 | 19 |  | 1092 | 24 | 19 | Univent
125 | Classroom | 320 | 21 |  | 598 | 13 | 13 | Univent
126 | Classroom | 287 | 19 |  | 1092 | 24 | 19 | Univent
- | Lunch Room |  | 0 | Yes | 2160 | 49 | 49 | Air Handling Unit

## South Phila HS
Sheet Last Modified: | 2021-04-30
School: | South Philly HS
Vendor: | Meehan (Auditoriums) | EMCOR (School) | Chadwick Retest
Vendor: | EMCOR (Gym) | EMCOR Retest 2 | EMCOR Retest 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Pre Engineering Shop Class A | 0 | 0 |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | Pre Engineering Shop Class B | 281 | 18 |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | Computer Lab | 296 | 19 |  |  | 0 | 0 | Nesbitt Unit Ventilator
004A | Engineering Tech. | 308 | 20 |  | 1716 | 39 | 20 | Nesbitt Unit Ventilator
004B | Engineering Tech. | 0 | 0 |  | 880 | 20 | 0 | Nesbitt Unit Ventilator
004C | Engineering Tech. | 313 | 20 |  | 2640 | 60 | 20 | Nesbitt Unit Ventilator
- | Cafeteria | 7225 | 481 |  | 11200 | 254 | 254 | Nesbitt Unit Ventilator
- | Cafeteria | 5887 | 392 |  |  | 0 | 0 | Air Handling Unit
- | Culinary Kitchen Hood MAU | 0 | 0 |  |  | 0 | 0 | Make-up Air Unit
- | Cafeteria Kitchen Hood | 4929 | 328 |  |  | 0 | 0 | Cafeteria Kitchen Hood
005A | Room | 0 | 0 |  | 2204 | 50 | 0 | Nesbitt Unit Ventilator
005B | Room | 0 | 0 |  | 984 | 22 | 0 | Nesbitt Unit Ventilator
- | General Office A | 461 | 30 |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | General Office B | 394 | 26 |  |  | 0 | 0 | Nesbitt Unit Ventilator
100 | Room | 384 | 25 |  | 1100 | 25 | 25 | Nesbitt Unit Ventilator
101 | Room | 345 | 23 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator
104 | Room | 276 | 18 |  | 620 | 14 | 14 | Nesbitt Unit Ventilator
105A | Room | 0 | 0 |  | 2709 | 61 | 0 | Nesbitt Unit Ventilator
105B | Room | 207 | 13 |  | 260 | 5 | 5 | Nesbitt Unit Ventilator
106 | Room | 400 | 26 |  | 667 | 15 | 15 | Nesbitt Unit Ventilator
108A | Room | 0 | 0 |  | 2280 | 51 | 0 | Nesbitt Unit Ventilator
108B | Room | 386 | 25 |  | 528 | 12 | 12 | Nesbitt Unit Ventilator
108C | Room | 417 | 27 |  | 276 | 6 | 6 | Nesbitt Unit Ventilator
109 | Room | 0 | 0 |  | 812 | 18 | 0 | Nesbitt Unit Ventilator
- | Studio 1 | 308 | 20 |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | Studio 2 | 419 | 27 |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | Community Closet | 352 | 23 |  | 899 | 20 | 20 | Nesbitt Unit Ventilator
200 | Room | 371 | 24 |  | 840 | 19 | 19
201 | Room | 363 | 24 |  | 1008 | 22 | 22 | Nesbitt Unit Ventilator
202 | Room | 465 | 31 |  | 1247 | 28 | 28 | Nesbitt Unit Ventilator
203 | Room | 278 | 18 |  | 579 | 13 | 13 | Nesbitt Unit Ventilator
204 | Room | 549 | 36 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator
205A | Room | 0 | 0 |  | 86.25 | 1 | 0 | Nesbitt Unit Ventilator
205B | Room | 415 | 27 |  | 150 | 3 | 3 | Nesbitt Unit Ventilator
206 | Room | 479 | 31 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator
207 | Room | 426 | 28 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator
208 | Room | 373 | 24 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator
209 | Room | 419 | 27 |  | 242 | 5 | 5 | Nesbitt Unit Ventilator
210 | Room | 297 | 19 |  | 900 | 20 | 19 | Nesbitt Unit Ventilator
211 | Room | 320 | 21 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator
214A | Music Room | 350 | 23 |  | 2142 | 48 | 23 | Nesbitt Unit Ventilator
214B | Music Room | 323 | 21 |  | 170 | 3 | 3 | Nesbitt Unit Ventilator
217A | Room | 382 | 25 |  | 2560 | 58 | 25 | Nesbitt Unit Ventilator
217B | Room | 411 | 27 |  | 1312 | 29 | 27 | Nesbitt Unit Ventilator
219A | Room | 367 | 24 |  | 899 | 20 | 20 | Nesbitt Unit Ventilator
220 | Room | 380 | 25 |  | 667 | 15 | 15 | Nesbitt Unit Ventilator
221A | Room | 320 | 21 |  | 1984 | 45 | 21 | Nesbitt Unit Ventilator
221B | Room | 279 | 18 |  | 127.5 | 2 | 2 | Nesbitt Unit Ventilator
222A | Room | 329 | 21 |  | 1705 | 38 | 21 | Nesbitt Unit Ventilator
222B | Room | 286 | 19 |  | 110.5 | 2 | 2 | Nesbitt Unit Ventilator
223A | Room | 259 | 17 |  | 1519 | 34 | 17 | Nesbitt Unit Ventilator
223B | Room | 217 | 14 |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | Culinary Arts A | 0 | 0 |  | 130.5 | 2 | 0 | Nesbitt Unit Ventilator
- | Culinary Arts B | 0 | 0 |  | 215 | 4 | 0 | Nesbitt Unit Ventilator
300A | Room | 0 | 0 |  | 112 | 2 | 0 | Nesbitt Unit Ventilator
300B | Room | 367 | 24 |  | 149 | 3 | 3 | Nesbitt Unit Ventilator
301 | Room | 416 | 27 |  | 1207 | 27 | 27 | Nesbitt Unit Ventilator
302 | Room | 393 | 26 |  | 1167 | 26 | 26 | Nesbitt Unit Ventilator
303 | Room | 338 | 22 |  | 875 | 19 | 19 | Nesbitt Unit Ventilator
304A | Room | 413 | 27 |  | 193 | 4 | 4 | Nesbitt Unit Ventilator
304B | Room | 427 | 28 |  | 1027 | 23 | 23 | Nesbitt Unit Ventilator
305A | Room | 371 | 24 |  | 259 | 5 | 5 | Nesbitt Unit Ventilator
305B | Room | 365 | 24 |  | 140 | 3 | 3 | Nesbitt Unit Ventilator
306A | Room | 358 | 23 |  | 193 | 4 | 4 | Nesbitt Unit Ventilator
306B | Room | 310 | 20 |  | 948 | 21 | 20 | Nesbitt Unit Ventilator
307A | Room | 298 | 19 |  | 959 | 21 | 19 | Nesbitt Unit Ventilator
308 | Library A | 322 | 21 |  | 6124 | 139 | 21 | Nesbitt Unit Ventilator
308 | Library B | 429 | 28 |  |  | 0 | 0 | Nesbitt Unit Ventilator
308 | Library C | 381 | 25 |  |  | 0 | 0 | Nesbitt Unit Ventilator
308 | Library Office | 361 | 24 |  | 84 | 1 | 1 | Nesbitt Unit Ventilator
308 | Library Archive Room | 0 | 0 |  | 360 | 8 | 0 | Nesbitt Unit Ventilator
311A | Room | 347 | 23 |  | 973 | 22 | 22 | Nesbitt Unit Ventilator
311B | Room | 374 | 24 |  | 1054 | 23 | 23 | Nesbitt Unit Ventilator
313B | Room | 0 | 0 |  | 526 | 11 | 0 | Nesbitt Unit Ventilator
316 | Room | 686 | 45 |  | 722 | 16 | 16 | Nesbitt Unit Ventilator
400A | Room | 314 | 20 |  | 203 | 4 | 4 | Nesbitt Unit Ventilator
400B | Room | 208 | 13 |  | 1092 | 24 | 13 | Nesbitt Unit Ventilator
401A | Room | 342 | 22 |  | 878 | 19 | 19 | Nesbitt Unit Ventilator
401B | Room | 318 | 21 |  |  | 0 | 0 | Nesbitt Unit Ventilator
402A | Room | 0 | 0 |  | 894 | 20 | 0 | Nesbitt Unit Ventilator
402B | Room | 296 | 19 |  |  | 0 | 0 | Nesbitt Unit Ventilator
403A | Room | 0 | 0 |  | 994 | 22 | 0 | Nesbitt Unit Ventilator
403B | Room | 307 | 20 |  | 458 | 10 | 10
404A | Room | 0 | 0 |  | 952 | 21 | 0 | Nesbitt Unit Ventilator
404B | Room | 297 | 19 |  |  | 0 | 0 | Nesbitt Unit Ventilator
405A | Room | 306 | 20 |  | 893 | 20 | 20 | Nesbitt Unit Ventilator
405B | Room | 0 | 0 |  |  | 0 | 0 | Nesbitt Unit Ventilator
406 | Room | 339 | 22 |  | 708 | 16 | 16 | Nesbitt Unit Ventilator
407 | Room | 298 | 19 |  | 715 | 16 | 16 | Nesbitt Unit Ventilator
408 | Room | 321 | 21 |  | 708 | 16 | 16 | Nesbitt Unit Ventilator
409 | Room | 278 | 18 |  | 675 | 15 | 15 | Nesbitt Unit Ventilator
410 | Room | 288 | 19 |  | 694 | 15 | 15 | Nesbitt Unit Ventilator
411 | Room | 333 | 22 |  | 707 | 16 | 16 | Nesbitt Unit Ventilator
412 | Room | 276 | 18 |  | 701 | 15 | 15 | Nesbitt Unit Ventilator
412A | Room | 222 | 14 |  | 471 | 10 | 10 | Nesbitt Unit Ventilator
413 | Room | 284 | 18 |  | 711 | 16 | 16 | Nesbitt Unit Ventilator
414 | Room | 0 | 0 |  | 580 | 13 | 0 | Nesbitt Unit Ventilator
415 | Room | 416 | 27 |  | 691 | 15 | 15 | Nesbitt Unit Ventilator
416 | Room | 337 | 22 |  | 660 | 15 | 15 | Nesbitt Unit Ventilator
417 | Room | 349 | 23 |  | 694 | 15 | 15 | Nesbitt Unit Ventilator
418 | Room | 343 | 22 |  | 698 | 15 | 15 | Nesbitt Unit Ventilator
418A | Room | 277 | 18 |  | 341 | 7 | 7 | Nesbitt Unit Ventilator
419A | Room | 0 | 0 |  | 1126 | 25 | 0 | Nesbitt Unit Ventilator
419B | Room | 0 | 0 |  | 135 | 3 | 0 | Nesbitt Unit Ventilator
420A | Room | 322 | 21 |  | 1082 | 24 | 21 | Nesbitt Unit Ventilator
420B | Room | 337 | 22 |  | 85 | 1 | 1 | Nesbitt Unit Ventilator
421 | Room | 328 | 21 |  | 673 | 15 | 15 | Nesbitt Unit Ventilator
422 | Room | 343 | 22 |  | 673 | 15 | 15 | Nesbitt Unit Ventilator
423 | Room | 322 | 21 |  | 673 | 15 | 15 | Nesbitt Unit Ventilator
424 | Room | 272 | 18 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator
425 | Room | 310 | 20 |  | 706 | 16 | 16 | Nesbitt Unit Ventilator
426 | Room | 285 | 19 |  | 681 | 15 | 15 | Nesbitt Unit Ventilator
427 | Room | 295 | 19 |  | 670 | 15 | 15 | Nesbitt Unit Ventilator
428 | Room | 400 | 26 |  | 681 | 15 | 15 | Nesbitt Unit Ventilator
429 | Room | 309 | 20 |  | 716 | 16 | 16 | Nesbitt Unit Ventilator
432 | Room | 972 | 64 |  | 664 | 15 | 15 | Nesbitt Unit Ventilator
433 | Room | 401 | 26 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator
434 | Room | 544 | 36 |  | 677 | 15 | 15 | Nesbitt Unit Ventilator
435 | Room | 503 | 33 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator
500 | Classroom | 0 | 0 |  | 937 | 21 | 0 | Nesbitt Unit Ventilator
500A | Classroom | 0 | 0 |  | 36 | 0 | 0 | Univent
500B | Classroom | 158 | 10 |  |  | 0 | 0 | Univent
501 A | Classroom | 0 | 0 |  | 845 | 19 | 0 | Univent
501 B | Classroom | 351 | 23 |  |  | 0 | 0 | Univent
502 A | Classroom | 208 | 13 |  | 969 | 22 | 13 | Univent
502 B | Classroom | 266 | 17 |  |  | 0 | 0 | Univent
503 A | Classroom | 157 | 10 |  | 1035 | 23 | 10 | Univent
503 B | Classroom | 67 | 4 |  | 200 | 4 | 4 | Univent
504 A | Classroom | 330 | 22 |  | 982 | 22 | 22 | Univent
504 B | Classroom | 160 | 10 |  |  | 0 | 0 | Univent
505 A | Classroom |  | 0 |  | 942 | 21 | 0 | Univent
505 B | Classroom |  | 0 |  |  | 0 | 0 | Univent
506 | Classroom | 320 | 21 |  | 690 | 15 | 15 | Univent
507 | Classroom | 212 | 14 |  | 690 | 15 | 14 | Univent
508 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent
509 | Classroom | 192 | 12 |  | 690 | 15 | 12 | Univent
510 A | Classroom | 183 | 12 |  | 990 | 22 | 12 | Univent
510 B | Classroom | 353 | 23 |  | 102 | 2 | 2 | Univent
511 | Classroom | 286 | 19 |  | 690 | 15 | 15 | Univent
512 | Classroom | 159 | 10 |  | 690 | 15 | 10 | Univent
513 | Classroom | 183 | 12 |  | 690 | 15 | 12 | Univent
514 | Classroom | 182 | 12 |  | 690 | 15 | 12 | Univent
515 | Classroom | 205 | 13 |  | 690 | 15 | 13 | Univent
516 | Classroom | 65 | 4 |  | 713 | 16 | 4 | Univent
517 | Classroom | 334 | 22 |  | 552 | 12 | 12 | Univent
518 | Classroom | 0 | 0 |  | 713 | 16 | 0 | Univent
519 | Classroom | 177 | 11 |  | 616 | 14 | 11 | Univent
520 | Classroom | 196 | 13 |  | 616 | 14 | 13 | Univent
521 | Classroom | 155 | 10 |  | 616 | 14 | 10 | Univent
522 | Classroom | 0 | 0 |  | 616 | 14 | 0 | Univent
523 | Classroom | 153 | 10 |  | 705 | 16 | 10 | Univent
524 | Classroom | 63 | 4 |  | 690 | 15 | 4 | Univent
525 | Classroom | 76 | 5 |  | 690 | 15 | 5 | Univent
526 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent
527 | Classroom | 167 | 11 |  | 690 | 15 | 11 | Univent
528 | Classroom | 223 | 14 |  | 690 | 15 | 14 | Univent
529 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent
530 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent
531 | Classroom | 4 | 0 |  | 690 | 15 | 0 | Univent
532 | Classroom | 0 | 0 |  | 705 | 16 | 0 | Univent
533 | Classroom | 163 | 10 |  | 705 | 16 | 10 | Univent
534 | Classroom | 0 | 0 |  | 705 | 16 | 0 | Univent
535 | Classroom | 380 | 25 |  | 705 | 16 | 16 | Univent
- | Auditorium | 10918 | 727 |  | 11536 | 262 | 262 | Nesbitt Unit Ventilator
- | Gym | 24019 | 1601 |  | 20384 | 463 | 463 | Air Handling Unit

## Southwark
Sheet Last Modified: | 2021-05-03
School: | Southwark Elementary School
Vendor: | Devine | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B4 | Office | 0 | 0 | Yes | 952 | 21 | 21 | House Fan
B5 | Music Room | 1241 | 82 |  | 1800 | 40 | 40 | House Fan
B20 | Basement | 584 | 38 |  | 960 | 21 | 21 | House Fan
B21 | Basement | 515 | 34 |  | 1728 | 39 | 34 | House Fan
102 | First Floor | 532 | 35 |  | 528 | 12 | 12 | House Fan
103 | First Floor | 268 | 17 |  | 660 | 15 | 15 | House Fan
107 | First Floor | 739 | 49 |  | 704 | 16 | 16 | House Fan
112 | Classroom | 579 | 38 |  | 864 | 19 | 19 | House Fan
113 | First Floor | 679 | 45 |  | 704 | 16 | 16 | House Fan
114 | Classroom | 716 | 47 |  | 864 | 19 | 19 | House Fan
115 | First Floor | 417 | 27 |  | 792 | 18 | 18 | House Fan
116 | Classroom | 575 | 38 |  | 864 | 19 | 19 | House Fan
117 | Classroom |  | 0 | Yes | 414 | 9 | 9 | House Fan
201 | Second Floor | 772 | 51 |  | 748 | 17 | 17 | House Fan
202 | Classroom | 486 | 32 |  | 864 | 19 | 19 | House Fan
203 | Classroom | 297 | 19 |  | 704 | 16 | 16 | House Fan
204 | Library |  | 0 | Yes | 696 | 15 | 15 | House Fan
205 | Library |  | 0 | Yes | 696 | 15 | 15 | House Fan
206 | Second Floor | 615 | 41 |  | 704 | 16 | 16 | House Fan
207 | Classroom | 633 | 42 |  | 864 | 19 | 19 | House Fan
208 | Second Floor | 332 | 22 |  | 792 | 18 | 18 | House Fan
209 | Classroom | 990 | 66 |  | 864 | 19 | 19 | House Fan
210 | Second Floor | 236 | 15 |  | 660 | 15 | 15 | House Fan
211 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan
212 | Classroom | 1033 | 68 |  | 864 | 19 | 19 | House Fan
213 | Second Floor | 675 | 45 |  | 792 | 18 | 18 | House Fan
214 | Classroom | 453 | 30 |  | 864 | 19 | 19 | House Fan
215 | Second Floor | 532 | 35 |  | 748 | 17 | 17 | House Fan
216 | Classroom | 562 | 37 |  | 864 | 19 | 19 | House Fan
217 | Room |  | 0 | Yes | 272 | 6 | 6 | House Fan
300 | Classroom |  | 0 | Yes | 480 | 10 | 10 | House Fan
301 | Classroom |  | 0 | Yes | 800 | 18 | 18 | House Fan
302 | Third Floor | 415 | 27 |  | 748 | 17 | 17 | House Fan
303 | Classroom | 291 | 19 |  | 864 | 19 | 19 | House Fan
304 | Room |  | 0 | Yes | 336 | 7 | 7 | House Fan
305 | Third Floor | 589 | 39 |  | 704 | 16 | 16 | House Fan
306 | Classroom | 276 | 18 |  | 864 | 19 | 18 | House Fan
307 | Classroom |  | 0 | Yes | 480 | 10 | 10 | House Fan
308 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
309 | Third Floor | 98 | 6 | Yes | 704 | 16 | 16 | House Fan
310 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
311 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
312 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
313 | Third Floor | 66 | 4 | Yes | 704 | 16 | 16 | House Fan
314 | Classroom |  | 0 | Yes | 800 | 18 | 18 | House Fan
315 | Classroom | 214 | 14 | Yes | 864 | 19 | 19 | House Fan
316 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan
- | Auditorium | 1586 | 105 |  | 1584 | 36 | 36 | House Fan
- | Boy's Bathroom | 541 | 36 |  | 792 | 18 | 18 | House Fan
- | Girl's Bathroom | 582 | 38 |  | 704 | 16 | 16 | House Fan
- | Music Room | 1241 | 82 |  | 1496 | 34 | 34 | House Fan
- | Nurses | 1184 | 78 |  | 150 | 3 | 3 | House Fan
- | Gym | 1915 | 127 |  | 1560 | 35 | 35 | House Fan
- | Main Office | 0 | 0 | Yes | 416 | 9 | 9 | House Fan
- | Principal's Office |  | 0 | Yes | 294 | 6 | 6 | House Fan
- | Cafeteria |  | 0 | Yes | 1890 | 42 | 42 | House Fan

## Spring Garden
Sheet Last Modified: | 2021-04-26
School: | Spring Garden
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 475 | 10 | 10
102 | Classroom |  | 0 | Yes | 494 | 11 | 11
103 | Classroom |  | 0 | Yes | 494 | 11 | 11
104A | storage |  | 0 |  | 50 | 1 | 0
104B | office |  | 0 | Yes | 80 | 1 | 1
104C | office |  | 0 | Yes | 110 | 2 | 2
104D | office |  | 0 | Yes | 99 | 2 | 2
105A | Classroom |  | 0 | Yes | 483 | 10 | 10
105B | Classroom |  | 0 | Yes | 420 | 9 | 9
201 | Classroom |  | 0 | Yes | 494 | 11 | 11
202 | Classroom |  | 0 | Yes | 494 | 11 | 11
203 | Classroom |  | 0 | Yes | 494 | 11 | 11
204 | Classroom |  | 0 | Yes | 494 | 11 | 11
205 | Classroom |  | 0 | Yes | 494 | 11 | 11
206 | Classroom |  | 0 | Yes | 483 | 10 | 10
207 | Classroom |  | 0 | Yes | 572 | 13 | 13
301 | Classroom |  | 0 | Yes | 741 | 16 | 16
303 | Classroom |  | 0 | Yes | 532 | 12 | 12
304 | Classroom |  | 0 | Yes | 578 | 13 | 13
305 | Classroom |  | 0 | Yes | 720 | 16 | 16
306 | Classroom |  | 0 | Yes | 494 | 11 | 11
307 | Classroom |  | 0 | Yes | 608 | 13 | 13
308 | IMC |  | 0 | Yes | 874 | 19 | 19
310 | Classroom |  | 0 | Yes | 380 | 8 | 8
- | Auditorium |  | 0 | Yes | 2265 | 51 | 51
- | Gym |  | 0 | Yes | 1800 | 40 | 40
- | Lunchroom |  | 0 | Yes | 1520 | 34 | 34
- | Main office |  | 0 | Yes | 231 | 5 | 5
- | Nurses Office |  | 0 | Yes | 189 | 4 | 4
- | Principal Office |  | 0 | Yes | 210 | 4 | 4
- | Staff lounge |  | 0 | Yes | 168 | 3 | 3
- | Teachers lounge |  | 0 | Yes | 195 | 4 | 4

## Spruance
Sheet Last Modified: | 2021-04-19
School: | Gilbert Spruance Elementary School
Vendor: | EMCOR
School: | Gilbert Spruance Little School House
Vendor: | EMCOR |  | Chadwick
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Spruance Main Building
100 | Room | 108 | 7 |  | 728 | 16 | 7 | Unit Ventilator
101 & 101B | Room | 208 | 13 |  | 1180 | 26 | 13 | Unit Ventilator
102 | Room | 112 | 7 |  | 756 | 17 | 7 | Unit Ventilator
Outside 102 | Hallway | 0 | 0 |  | 370 | 8 | 0 | Unit Ventilator
103 | Room | 188 | 12 |  | 756 | 17 | 12 | Unit Ventilator
104 | Room | 101 | 6 |  | 756 | 17 | 6 | Unit Ventilator
105 | Room | 83 | 5 |  | 756 | 17 | 5 | Unit Ventilator
106 | Room | 106 | 7 |  | 756 | 17 | 7 | Unit Ventilator
107 | Room | 119 | 7 | Yes | 756 | 17 | 17 | Unit Ventilator
108 | Room | 115 | 7 |  | 756 | 17 | 7 | Unit Ventilator
109 | Room | 160 | 10 |  | 756 | 17 | 10 | Unit Ventilator
110 | Room | 97 | 6 |  | 756 | 17 | 6 | Unit Ventilator
111 | Room | 145 | 9 |  | 996 | 22 | 9 | Unit Ventilator
112 | Room | 208 | 13 |  | 996 | 22 | 13 | Unit Ventilator
113 | Room | 110 | 7 |  | 996 | 22 | 7 | Unit Ventilator
Outside of 113 | Hallway | 0 | 0 |  | 3700 | 84 | 0 | Unit Ventilator
114 | Room | 240 | 16 |  | 996 | 22 | 16 | Unit Ventilator
115 | Room | 150 | 10 |  | 996 | 22 | 10 | Unit Ventilator
116 | Room | 334 | 22 |  | 719 | 16 | 16 | Unit Ventilator
117 | Room | 240 | 16 |  | 736 | 16 | 16 | Unit Ventilator
118 | Room | 145 | 9 |  | 1075 | 24 | 9 | Unit Ventilator
118A | Room | 183 | 12 |  | 486 | 11 | 11 | Unit Ventilator
119 | Room | 241 | 16 |  | 736 | 16 | 16 | Unit Ventilator
120 | Room | 225 | 15 |  | 1062 | 24 | 15 | Unit Ventilator
122 | Room | 248 | 16 |  | 851 | 19 | 16 | Unit Ventilator
124 | Room | 58 | 3 | Yes | 756 | 17 | 17 | Unit Ventilator
- | Auditorium/Gym | 0 | 0 |  | 4620 | 105 | 0 | Unit Ventilator
- | Adjustment Room | 73 | 4 |  | 435 | 9 | 4 | Unit Ventilator
200 | Room | 148 | 9 |  | 756 | 17 | 9 | Unit Ventilator
201 | Room | 136 | 9 |  | 756 | 17 | 9 | Unit Ventilator
202 | Room | 179 | 11 |  | 690 | 15 | 11 | Unit Ventilator
Outside of 202 | Hallway | 0 | 0 |  | 3700 | 84 | 0 | Unit Ventilator
203 | Room | 134 | 8 |  | 756 | 17 | 8 | Unit Ventilator
204 | Room | 114 | 7 |  | 756 | 17 | 7 | Unit Ventilator
205 | Room | 97 | 6 |  | 756 | 17 | 6 | Unit Ventilator
206 | Room | 83 | 5 |  | 756 | 17 | 5 | Unit Ventilator
207 | Room | 102 | 6 |  | 756 | 17 | 6 | Unit Ventilator
208 | Room | 139 | 9 |  | 756 | 17 | 9 | Unit Ventilator
209 | Room | 121 | 8 |  | 756 | 17 | 8 | Unit Ventilator
210 | Room | 90 | 6 |  | 756 | 17 | 6 | Unit Ventilator
211 | Room | 199 | 13 |  | 756 | 17 | 13 | Unit Ventilator
212 | Room | 134 | 8 |  | 756 | 17 | 8 | Unit Ventilator
213A | Room | 103 | 6 |  | 420 | 9 | 6 | Unit Ventilator
Outside of Room 213A | Hallway | 0 | 0 |  | 756 | 17 | 0 | Unit Ventilator
213B | Room | 267 | 17 |  | 548 | 12 | 12 | Unit Ventilator
214 | Room | 114 | 7 |  | 755 | 17 | 7 | Unit Ventilator
214A | Room | 0 | 0 |  | 756 | 17 | 0 | Unit Ventilator
215 | Room | 53 | 3 |  | 756 | 17 | 3 | Unit Ventilator
216 | Room | 122 | 8 |  | 756 | 17 | 8 | Unit Ventilator
217 | Room | 83 | 5 |  | 756 | 17 | 5 | Unit Ventilator
Outside of Room 217 | Hallway | 0 | 0 |  | 1850 | 42 | 0 | Unit Ventilator
218 | Room | 139 | 9 |  | 718 | 16 | 9 | Unit Ventilator
220 | Room | 131 | 8 |  | 724 | 16 | 8 | Unit Ventilator
- | Cafeteria | 263 | 17 | Yes | 4550 | 103 | 103 | Unit Ventilator
- | Main Office | 315 | 21 |  | 456 | 10 | 10
- | Principal | 240.25 | 16 |  | 241 | 5 | 5
- | Nurse | 374 | 24 |  | 374 | 8 | 8
- | Main Entrance Lobby | 1498 | 99 |  | 1498 | 34 | 34 | Unit Ventilator
Little School House
1 | Room | 1072 | 71 |  | 1056 | 24 | 24 | Air Handling Unit
2 | Room | 938 | 62 |  | 1056 | 24 | 24 | Air Handling Unit
3 | Room | 741 | 49 |  | 1056 | 24 | 24 | Air Handling Unit
4 | Room | 1188 | 79 |  | 1056 | 24 | 24 | Air Handling Unit
5 | Room | 682 | 45 |  | 1056 | 24 | 24 | Air Handling Unit
6 | Room | 713 | 47 |  | 1056 | 24 | 24 | Air Handling Unit
7 | Room | 554 | 36 |  | 1056 | 24 | 24 | Air Handling Unit
8 | Room | 690 | 46 |  | 1056 | 24 | 24 | Air Handling Unit
9 | Room | 1558 | 103 |  | 1056 | 24 | 24 | Air Handling Unit
10 | Room | 853 | 56 |  | 1056 | 24 | 24 | Air Handling Unit
11 | Room | 1512 | 100 |  | 1056 | 24 | 24 | Air Handling Unit
12 | Room | 946 | 63 |  | 1056 | 24 | 24 | Air Handling Unit
- | CLI Office | 159 | 10 |  | 120 | 2 | 2 | Air Handling Unit
- | Entrance/Lobby | 0 | 0 |  | 210 | 4 | 0 | Air Handling Unit
- | Hallway | 0 | 0 |  | 1950 | 44 | 0 | Air Handling Unit
- | Main Office | 165 | 11 |  | 315 | 7 | 7 | Air Handling Unit
- | Office | 158 | 10 |  | 126 | 2 | 2 | Air Handling Unit
- | Storage | 0 | 0 |  | 215 | 4 | 0 | Air Handling Unit
- | Teachers Lounge | 331 | 22 |  | 72 | 1 | 1 | Air Handling Unit
- | Therapy Room | 0 | 0 |  | 72 | 1 | 0 | Air Handling Unit
- | Girl's RR | 0 | 0 |  | 272 | 6 | 0 | Air Handling Unit
- | Boy's RR | 0 | 0 |  | 272 | 6 | 0 | Air Handling Unit
- | Men's RR | 0 | 0 |  | 77 | 1 | 0 | Air Handling Unit
- | Women's RR | 0 | 0 |  | 131 | 2 | 0 | Air Handling Unit
- | Multi-purpose Room | 2808 | 187 |  | 1998 | 45 | 45 | Fan Coil Unit

## Stanton, EM
Sheet Last Modified: | 2021-04-29
School: | Edwin M. Stanton Elementary School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Main Office | 0 | 0 | Yes | 375 | 8 | 8 | House Fan
101 | Classroom | 829 | 55 |  | 870 | 19 | 19 | House Fan
102 | Classroom | 598 | 39 |  | 870 | 19 | 19 | House Fan
103 | Classroom | 630 | 42 |  | 899 | 20 | 20 | House Fan
104 | Classroom | 635 | 42 |  | 864 | 19 | 19 | House Fan
105 | Classroom | 639 | 42 |  | 870 | 19 | 19 | House Fan
106 | Classroom | 764 | 50 |  | 870 | 19 | 19 | House Fan
107 | Classroom | 836 | 55 |  | 1450 | 32 | 32 | House Fan
201 | Classroom | 697 | 46 |  | 870 | 19 | 19 | House Fan
202 | Classroom | 500 | 33 |  | 870 | 19 | 19 | House Fan
203 | Classroom | 526 | 35 |  | 870 | 19 | 19 | House Fan
204 | Classroom | 527 | 35 |  | 870 | 19 | 19 | House Fan
205 | Library | 907 | 60 |  | 1363 | 30 | 30 | House Fan
206 | Classroom | 531 | 35 |  | 870 | 19 | 19 | House Fan
207 | Classroom | 706 | 47 |  | 870 | 19 | 19 | House Fan
208 | Classroom | 806 | 53 |  | 870 | 19 | 19 | House Fan
301 | Gym | 61 | 4 |  | 870 | 19 | 4 | House Fan
302 | Gym | 432 | 28 |  | 870 | 19 | 19 | House Fan
302 | Classroom | 560 | 37 |  | 870 | 19 | 19 | House Fan
304 | Classroom | 715 | 47 |  | 870 | 19 | 19 | House Fan
305 | Classroom | 833 | 55 |  | 1316 | 29 | 29 | House Fan
306 | Classroom | 525 | 35 |  | 870 | 19 | 19 | House Fan
307 | Classroom | 988 | 65 |  | 870 | 19 | 19 | House Fan
308 | Classroom | 230 | 15 |  | 870 | 19 | 15 | House Fan
Counselor | Office |  | 0 | Yes | 240 | 5 | 5 | House Fan
- | Cafeteria | 0 | 0 | Yes | 2400 | 54 | 54 | House Fan
- | Nurse Office | 0 | 0 | Yes | 200 | 4 | 4 | House Fan
- | Principal Office | 0 | 0 | Yes | 256 | 5 | 5 | House Fan

## Stearne
Sheet Last Modified: | 2021-04-15
School: | Allen M. Stearne Elementary School
Vendor: | EMCOR | EMCOR Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | classroom | 529 | 35 |  | 730 | 16 | 16 | Perimeter Heater
100A | First Floor | 30 | 2 |  | 222 | 5 | 2 | Perimeter Heater
101 | classroom | 316 | 21 |  | 1197 | 27 | 21 | Perimeter Heater
102 | classroom | 452 | 30 |  | 753 | 17 | 17 | Perimeter Heater
102A | First Floor | 284 | 18 |  | 401 | 9 | 9 | Perimeter Heater
103 | classroom | 569 | 37 |  | 1175 | 26 | 26 | Perimeter Heater
104 | classroom | 224 | 14 |  | 716 | 16 | 14 | Perimeter Heater
105 | Classroom |  | 0 |  | 319 | 7 | 0 | Perimeter Heater
106 | classroom | 189 | 12 |  | 730 | 16 | 12 | Perimeter Heater
108A | First Floor | 276 | 18 |  | 810 | 18 | 18 | Perimeter Heater
108B | First Floor | 59 | 3 |  | 129 | 2 | 2 | Perimeter Heater
108C | First Floor | 109 | 7 |  | 146 | 3 | 3 | Perimeter Heater
108D | First Floor | 54 | 3 |  | 86 | 1 | 1 | Perimeter Heater
108E | First Floor | 87 | 5 |  | 75 | 1 | 1 | Perimeter Heater
108F | First Floor | 62 | 4 |  | 94 | 2 | 2 | Perimeter Heater
200 | classroom | 274 | 18 |  | 740 | 16 | 16 | Perimeter Heater
201 | classroom | 322 | 21 |  | 717 | 16 | 16 | Perimeter Heater
202 | classroom | 313 | 20 |  | 705 | 16 | 16 | Perimeter Heater
203 | classroom | 337 | 22 |  | 739 | 16 | 16 | Perimeter Heater
204 | classroom | 329 | 21 |  | 737 | 16 | 16 | Perimeter Heater
205 | classroom | 325 | 21 |  | 756 | 17 | 17 | Perimeter Heater
206 | classroom | 334 | 22 |  | 745 | 16 | 16 | Perimeter Heater
207 | classroom | 0 | 0 | Yes | 386 | 8 | 8 | Perimeter Heater
208 | classroom | 328 | 21 |  | 882 | 20 | 20 | Perimeter Heater
209 | classroom | 109 | 7 | Yes | 639 | 14 | 14 | Perimeter Heater
209A | classroom | 80 | 5 |  | 152 | 3 | 3 | Perimeter Heater
209B | classroom | 0 | 0 |  | 125 | 2 | 0 | Perimeter Heater
210 | classroom | 549 | 36 |  | 1185 | 26 | 26 | Perimeter Heater
211 | classroom | 845 | 56 |  | 728 | 16 | 16 | Perimeter Heater
212 | classroom | 116 | 7 |  | 434 | 9 | 7 | Perimeter Heater
213 | classroom | 131 | 8 |  | 224 | 5 | 5 | Perimeter Heater
300 | classroom | 532 | 35 |  | 763 | 17 | 17 | Perimeter Heater
300A | classroom | 395 | 26 |  | 224 | 5 | 5 | Perimeter Heater
301 | classroom | 350 | 23 |  | 755 | 17 | 17 | Perimeter Heater
302 | classroom | 289 | 19 |  | 746 | 16 | 16 | Perimeter Heater
303 | classroom | 447 | 29 |  | 722 | 16 | 16 | Perimeter Heater
304 | classroom | 434 | 28 |  | 745 | 16 | 16 | Perimeter Heater
305 | classroom | 360 | 24 |  | 747 | 16 | 16 | Perimeter Heater
306 | classroom | 534 | 35 |  | 715 | 16 | 16 | Perimeter Heater
307 | Classroom |  | 0 |  | 790 | 17 | 0 | Perimeter Heater
308 | classroom | 278 | 18 |  | 717 | 16 | 16 | Perimeter Heater
- | Auditorium | 0 | 0 |  | 2919 | 66 | 0 | AHU
- | Cafeteria/Gym | 0 | 0 | Yes | 3719 | 84 | 84 | AHU
- | Dean's Office (Temple) | 72 | 4 |  | 106 | 2 | 2 | Perimter Heater
- | Health Office | 274 | 18 |  | 294 | 6 | 6 | Perimter Heater
- | Office | 300 | 20 |  | 984 | 22 | 20 | Perimter Heater
- | Principal | 187 | 12 |  | 321 | 7 | 7 | Perimter Heater

## Steel
Sheet Last Modified: | 2021-04-27
School: | Edward Steel Elementary School
Vendor: | EMCORE Fluidics | Exhaust Report
| 2-15-2021 Retest | 2-22-21 Retest | 4-12-21 Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Storeroom | 0 | 0 | Yes | 323 | 7 | 7 | Air Coil Unit
101A - C | Office | 0 | 0 | Yes | 356 | 8 | 8 | Air Coil Unit
102 | Main Office- open office | 0 | 0 | Yes | 512 | 11 | 11 | Air Coil Unit
102 | Main Office- admin ofc | 0 | 0 |  | 121 | 2 | 0 | Air Coil Unit
102 | Main Office- asst principals ofc | 0 | 0 | Yes | 121 | 2 | 2 | Air Coil Unit
102 | Main Office- principals ofc | 0 | 0 | Yes | 143 | 3 | 3 | Air Coil Unit
102 | Main Office- conf rm | 0 | 0 | Yes | 204 | 4 | 4 | Air Coil Unit
103 | Lounge | 0 | 0 | Yes | 676 | 15 | 15 | Air Coil Unit
104 | counselors ofc | 0 | 0 | Yes | 385 | 8 | 8 | Air Coil Unit
105 | Classroom | 46 | 3 | Yes | 660 | 15 | 15 | Air Handling Unit
106 | data room | 0 | 0 | Yes | 1364 | 31 | 31 | Air Coil Unit
107 | Classroom | 363 | 24 | Yes | 1364 | 31 | 31 | Air Handling Unit
109 | Classroom | 257 | 17 | Yes | 1364 | 31 | 31 | Air Handling Unit
110 | nurse str | 0 | 0 | Yes | 886 | 20 | 20 | Air Coil Unit
- | Nurse Waiting Area |  | 0 | Yes | 208 | 4 | 4
111 | Classroom | 450 | 30 | Yes | 1364 | 31 | 31 | Air Handling Unit
113 | Classroom | 338 | 22 | Yes | 1364 | 31 | 31 | Air Handling Unit
- | AUDITORIUM | 475 | 31 | Yes | 2482 | 56 | 56 | Air Coil Unit
- | CAFETERIA | 0 | 0 | Yes | 3478 | 79 | 79 | Air Coil Unit
- | Cafeteria Office |  | 0 | Yes | 300 | 6 | 6
- | IMC | 2021 | 134 |  | 3283 | 74 | 74 | Air Coil Unit
201 | Classroom | 163 | 10 | Yes | 1330 | 30 | 30 | Air Handling Unit
202 | Classroom | 250 | 16 | Yes | 1330 | 30 | 30 | Air Handling Unit
203 | Classroom | 188 | 12 | Yes | 1147 | 26 | 26 | Air Handling Unit
204 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
205 | Classroom | 194 | 12 | Yes | 1147 | 26 | 26 | Air Handling Unit
206 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
207 | Classroom | 144 | 9 | Yes | 1147 | 26 | 26 | Air Handling Unit
208 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
209 | Classroom | 186 | 12 | Yes | 1147 | 26 | 26 | Air Handling Unit
210 | Classroom | 196 | 13 | Yes | 1147 | 26 | 26 | Air Coil Unit
211 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
212 | Classroom | 287 | 19 | Yes | 1130 | 25 | 25 | Air Coil Unit
213 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Coil Unit
214 | Classroom |  | 0 | Yes | 870 | 19 | 19 | Air Coil Unit
215 | Office | 0 | 0 | Yes | 345 | 7 | 7 | Air Coil Unit
216 | Classroom | 0 | 0 | Yes | 588 | 13 | 13 | Air Coil Unit
219 | Classroom |  | 0 | Yes | 462 | 10 | 10 | Air Coil Unit
220 | team office | 0 | 0 | Yes | 462 | 10 | 10 | Air Coil Unit
301 | Classroom | 0 | 0 | Yes | 1330 | 30 | 30 | Air Coil Unit
302 | Classroom | 0 | 0 | Yes | 1330 | 30 | 30 | Air Coil Unit
303 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
304 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
305 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
306 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
307 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
308 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
309 | Classroom | 0 | 0 | Yes | 1155 | 26 | 26 | Air Coil Unit
310 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit
311 | Classroom | 0 | 0 | Yes | 1330 | 30 | 30 | Air Coil Unit
312 | Classroom | 482 | 32 |  | 1330 | 30 | 30 | Air Coil Unit
313 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Coil Unit
314 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Coil Unit
315 | Staff Lounge |  | 0 | Yes | 330 | 7 | 7 | Air Coil Unit
319 | Classroom |  | 0 | Yes | 462 | 10 | 10 | Air Coil Unit
320 | team office |  | 0 | Yes | 462 | 10 | 10 | Air Coil Unit
- | imc office | 105 | 7 | Yes | 3283 | 74 | 74 | Air Coil Unit
- | imc storage | 70 | 4 |  | 255 | 5 | 4 | Air Coil Unit
- | material production | 210 | 14 | Yes | 625 | 14 | 14 | Air Coil Unit
- | open library | 1180 | 78 |  | 3360 | 76 | 76 | Air Coil Unit
- | Gym Office |  | 0 | Yes | 168 | 3 | 3
- | Gym | 7824 | 521 |  | 4860 | 110 | 110

## Stoddart-Fleisher
Sheet Last Modified: | 2021-03-18
School: | Parkway Center City Middle College @ Stoddart Fleisher
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | kitchen |  | 0 |  | 837 | 19 | 0
- | lunchroom |  | 0 |  | 3822 | 86 | 0
- | art room |  | 0 |  | 782 | 17 | 0
506 | art room |  | 0 |  | 851 | 19 | 0
505B | office |  | 0 |  | 528 | 12 | 0
505 | classroom |  | 0 |  | 1078 | 24 | 0
504 | classroom |  | 0 |  | 1144 | 26 | 0
503A | office |  | 0 |  | 96 | 2 | 0
503B | shop |  | 0 |  | 252 | 5 | 0
- | teacher's lounge |  | 0 |  | 621 | 14 | 0
502 | classroom |  | 0 |  | 552 | 12 | 0
501 | classroom |  | 0 |  | 640 | 14 | 0
411 | classroom |  | 0 |  | 770 | 17 | 0
410 | classroom |  | 0 |  | 805 | 18 | 0
409 | classroom |  | 0 |  | 713 | 16 | 0
408 | classroom |  | 0 |  | 716 | 16 | 0
407 | classroom |  | 0 |  | 748 | 17 | 0
406 | classroom |  | 0 |  | 704 | 16 | 0
405B | counselor |  | 0 |  | 135 | 3 | 0
405A | VP office |  | 0 |  | 506 | 11 | 0
404 | classroom |  | 0 |  | 644 | 14 | 0
403 | classroom |  | 0 |  | 621 | 14 | 0
402 | classroom |  | 0 |  | 598 | 13 | 0
401 | classroom |  | 0 |  | 640 | 14 | 0
310 | classroom |  | 0 |  | 704 | 16 | 0
309 | weight room |  | 0 |  | 920 | 20 | 0
308 | classroom |  | 0 |  | 897 | 20 | 0
307 | classroom |  | 0 |  | 858 | 19 | 0
306 | storage room |  | 0 |  | 682 | 15 | 0
305 | classroom |  | 0 |  | 660 | 15 | 0
304 | classroom |  | 0 |  | 726 | 16 | 0
303A | office |  | 0 |  | 161 | 3 | 0
303 | classroom |  | 0 |  | 713 | 16 | 0
302 | classroom |  | 0 |  | 682 | 15 | 0
301A | computer office |  | 0 |  | 184 | 4 | 0
301 | classroom |  | 0 |  | 640 | 14 | 0
- | Boys locker room |  | 0 |  | 360 | 8 | 0
- | Gym |  | 0 |  | 3300 | 75 | 0
- | Girls Locker room |  | 0 |  | 324 | 7 | 0
- | Nurses office |  | 0 |  | 240 | 5 | 0
- | Exam Room |  | 0 |  | 150 | 3 | 0
208 | classroom |  | 0 |  | 598 | 13 | 0
207 | classroom |  | 0 |  | 598 | 13 | 0
206 | classroom |  | 0 |  | 644 | 14 | 0
205 | Library |  | 0 |  | 1081 | 24 | 0
- | Main Office Area |  | 0 |  | 285 | 6 | 0
- | Main Office Waiting area |  | 0 |  | 150 | 3 | 0
- | Principal's office |  | 0 |  | 280 | 6 | 0
204 | classroom |  | 0 |  | 616 | 14 | 0
203 | classroom |  | 0 |  | 621 | 14 | 0
202 | classroom |  | 0 |  | 598 | 13 | 0
201 | counselor's Sitting area |  | 0 |  | 200 | 4 | 0
201A | counselor's A |  | 0 |  | 96 | 2 | 0
201B | counselor's B |  | 0 |  | 132 | 3 | 0
201C | counselor's C |  | 0 |  | 121 | 2 | 0
201D | counsel's D |  | 0 |  | 121 | 2 | 0
105 | conferance room |  | 0 |  | 598 | 13 | 0
104A | classroom |  | 0 |  | 247 | 5 | 0
104B | office |  | 0 |  | 117 | 2 | 0
104C | office |  | 0 |  | 112 | 2 | 0
104D | office |  | 0 |  | 90 | 2 | 0
104E | office |  | 0 |  | 99 | 2 | 0
- | Regional office |  | 0 |  | No Access | 0 | 0
- | Data room |  | 0 |  | 484 | 11 | 0
102A | classroom |  | 0 |  | 693 | 15 | 0
102C | office |  | 0 |  | 195 | 4 | 0
102E | classroom |  | 0 |  | 513 | 11 | 0
102D | office |  | 0 |  | 635 | 14 | 0
102B | office |  | 0 |  | 195 | 4 | 0
101 | counselor |  | 0 |  | 306 | 6 | 0
- | Auditorium |  | 0 |  | 4539 | 103 | 0

## Strawberry Mansion Hill
Sheet Last Modified: | 2021-03-18
School: | Strawberry Mansion High School
School: | Leslie P. Hill Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Strawberry Mansion
101 | Music Rm. | 0 | 0 |  | 1288 | 29 | 0 | Heating Unit Ventilator
102 | Classroom | 542 | 36 |  | 768 | 17 | 17 | Univent
103 | Music Rm. | 78 | 5 |  | 1288 | 29 | 5 | Heating Unit Ventilator
104 | Classroom | 427 | 28 |  | 888 | 20 | 20 | Univent
108 | Classroom | 0 | 0 |  | 888 | 20 | 0 | Univent
109A & 109B | Classroom | 620 | 41 |  | 1288 | 29 | 29 | Heating Unit Ventilator
110 | Classroom | 695 | 46 |  | 888 | 20 | 20 | Univent
111 | Classroom | 444 | 29 |  | 288 | 6 | 6 | Univent
112 | Classroom | 0 | 0 |  | 888 | 20 | 0 | Univent
200 | Classroom | 0 | 0 |  | 1056 | 24 | 0 | Univent
201 | Classroom | 416 | 27 |  | 805 | 18 | 18 | Univent
202 | Classroom | 357 | 23 |  | 1152 | 26 | 23 | Univent
203 | Classroom | 607 | 40 |  | 782 | 17 | 17 | Univent
206 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
207 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
208 | Classroom | 512 | 34 |  | 1104 | 25 | 25 | Univent
209 | Computer Lab | 859 | 57 |  | 1012 | 23 | 23 | Air Handling Unit
212 | Classroom | 382 | 25 |  | 851 | 19 | 19 | Univent
214 | Classroom | 301 | 20 |  | 851 | 19 | 19 | Univent
216 | Classroom | 350 | 23 |  | 851 | 19 | 19 | Univent
217 | Classroom | 516 | 34 |  | 1012 | 23 | 23 | Univent
219 | Classroom | 0 | 0 |  | 960 | 21 | 0 | Univent
220 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
222 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
224 | Classroom | 0 | 0 |  | 782 | 17 | 0 | Univent
300 | Classroom | 464 | 30 |  | 782 | 17 | 17 | Univent
301 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
302 | Classroom | 401 | 26 |  | 782 | 17 | 17 | Univent
303 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent
304 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
306 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
307 | Classroom | 442 | 29 |  | 851 | 19 | 19 | Univent
308 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
309 | Classroom | 335 | 22 |  | 851 | 19 | 19 | Univent
310 | Classroom | 430 | 28 |  | 851 | 19 | 19 | Univent
311 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
312 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
314 | Classroom | 446 | 29 |  | 851 | 19 | 19 | Univent
315 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
316 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
317 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
319 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
320 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
322 | Classroom | 459 | 30 |  | 851 | 19 | 19 | Univent
323 | Classroom | 601 | 40 |  | 851 | 19 | 19 | Univent
324 | Classroom | 466 | 31 |  | 782 | 17 | 17 | Univent
325 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
400A&B | Classroom | 0 | 0 |  | 598 | 13 | 0 | Univent
401A | Classroom | 488 | 32 |  | 345 | 7 | 7 | Univent
402 | Classroom | 465 | 31 |  | 1288 | 29 | 29 | Univent
403 | Classroom | 250 | 16 |  | 299 | 6 | 6 | Univent
404 | Classroom | 434 | 28 |  | 1196 | 27 | 27 | Univent
405 | Classroom | 503 | 33 |  | 987 | 22 | 22 | Univent
406 | Classroom | 239 | 15 |  | 666 | 15 | 15 | Univent
407 | Classroom | 236 | 15 |  | 375 | 8 | 8 | Univent
408 | Classroom | 456 | 30 |  | 851 | 19 | 19 | Univent
409 | Classroom | 0 | 0 |  | 1288 | 29 | 0 | Univent
410 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
412 | Classroom | 431 | 28 |  | 851 | 19 | 19 | Univent
413 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
414 | Classroom | 467 | 31 |  | 851 | 19 | 19 | Univent
415 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
417 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
418 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
420 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
421 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
422 | Classroom | 0 | 0 |  | 782 | 17 | 0 | Univent
423 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent
500 | Classroom | 280 | 18 |  | 800 | 18 | 18 | Univent
500B | Classroom | 264 | 17 |  | 375 | 8 | 8 | Univent
502 | Classroom | 442 | 29 |  | 300 | 6 | 6 | Univent
505 | Classroom | 0 | 0 |  | 1300 | 29 | 0 | Univent
506 | Classroom | 0 | 0 |  | 925 | 21 | 0 | Univent
507 | Classroom | 0 | 0 |  | 425 | 9 | 0 | Univent
508 | Classroom | 487 | 32 |  | 1250 | 28 | 28 | Univent
509 | Classroom | 0 | 0 |  | 1100 | 25 | 0 | Univent
513 | Classroom | 489 | 32 |  | 325 | 7 | 7 | Univent
516 | Classroom | 0 | 0 |  | 1326.78 | 30 | 0 | Univent
517 | Classroom | 0 | 0 |  | 1161.96 | 26 | 0 | Univent
518 | Classroom | 0 | 0 |  | 1375.48 | 31 | 0 | Univent
519 | Classroom | 292 | 19 |  | 569.92 | 12 | 12 | Univent
520 | Classroom | 683 | 45 |  | 1446.72 | 32 | 32 | Univent
522 | Classroom | 0 | 0 |  | 1471.38 | 33 | 0 | Univent
- | Library | 1247 | 83 |  | 1863 | 42 | 42 | Air Handling Unit
- | Culinary Arts area | 1077 | 71 |  | 6536 | 148 | 71 | Air Handling Unit
- | Book Strg. Rm. Security office | 0 | 0 |  | 1732.629 | 39 | 0 | Air Handling Unit
- | DOS office | 0 | 0 |  |  | 0 | 0 | Univent
- | EST office | 513 | 34 |  |  | 0 | 0 | Univent
| Serves unknown | 0 | 0 |  |  | 0 | 0 | Heating Unit Ventilator
- | Auditorium | 7054 | 470 |  | 9936 | 225 | 225 | Heating Unit Ventilator
- | Cafeteria | 1912 | 127 |  | 10725 | 243 | 127 | Heating Unit Ventilator
- | Aud. Stage | 2999 | 199 |  | 2668 | 60 | 60 | Heating Unit Ventilator
- | Unknown location and what it serves |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator
- | Maintenance office, Lobby | 317 | 21 |  |  | 0 | 0 | Heating Unit Ventilator
- | Girls Locker Room | 1759 | 117 |  |  | 0 | 0 | Heating Unit Ventilator
- | Girls Gym | 885 | 59 |  | 5808 | 132 | 59 | Heating Unit Ventilator
- | Boys Locker Room | 126 | 8 |  |  | 0 | 0 | Heating Unit Ventilator
- | Boys Gym | 6081 | 405 |  | 5808 | 132 | 132 | Heating Unit Ventilator
- | Unknown location and what it serves |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator
- | Music Prac. Rms. & Office | 607 | 40 |  |  | 0 | 0 | Heating Unit Ventilator
- | Nurses area, Admin areas | 796 | 53 |  |  | 0 | 0 | Heating Unit Ventilator
- | Unknown |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator
- | Unknown |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator
LP Hill Building
1 | Office | 0 | 0 |  | 870.365 | 19 | 0 | Vertical ACU
4 | Office | 0 | 0 |  | 409.462 | 9 | 0 | Vertical Air Coil Unit and Univent
5 | Classroom | 0 | 0 |  |  | 0 | 0 | Vertical Air Coil Unit and Univent
7 | Classroom | 0 | 0 |  |  | 0 | 0 | Vertical Air Coil Unit and Univent
7 | Conference Rm. | 0 | 0 |  | 1111.66 | 25 | 0 | Vertical Air Coil Unit and Univent
10 | Storage Room | 0 | 0 |  | 454.88 | 10 | 0 | Vertical Air Coil Unit
12 | Truency Court | 0 | 0 |  | 988.792 | 22 | 0 | Vertical Air Coil Unit
14 | Truency Court | 0 | 0 |  | 715.596 | 16 | 0 | Univent
15 | General Room | 0 | 0 |  | 734.479 | 16 | 0 | Vertical Air Coil Unit and Univent
100 | Classroom | 0 | 0 |  | 982.127 | 22 | 0 | Vertical Air Coil Unit and Univent
101 | Classroom | 0 | 0 |  | 1041.52 | 23 | 0 | Vertical Air Coil Unit and Univent
102 | Classroom | 0 | 0 |  | 973.903 | 22 | 0 | Univent
103 | Classroom | 0 | 0 |  | 1054.8 | 23 | 0 | Vertical Air Coil Unit and Univent
104 | Classroom | 0 | 0 |  | 1022.271 | 23 | 0 | Univent
105 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Univent
106 | Classroom | 160 | 10 |  | 933.66 | 21 | 10 | Univent
107 | Classroom | 15 | 1 |  | 1492.29 | 33 | 1 | Univent
108 | Classroom | 224 | 14 |  | 1492.29 | 33 | 14 | Univent
200 | Office | 0 | 0 |  | 917.724 | 20 | 0 | Univent
202 | Office | 294 | 19 |  | 1034 | 23 | 19 | Univent
203 | Office | 0 | 0 |  | 833.94 | 18 | 0 | Univent
204 | Office | 50 | 3 |  | 1034 | 23 | 3 | Univent
205 | Office | 0 | 0 |  | 1033.59 | 23 | 0 | Univent
206 | Office | 0 | 0 |  | 951.5 | 21 | 0 | Univent
207 | Office | 31 | 2 |  | 1033.59 | 23 | 2 | Univent
209 | Office | 119 | 7 |  | 1031.06 | 23 | 7 | Univent
210 | Office | 0 | 0 |  | 1009.73 | 22 | 0 | Univent
212 | Office | 169 | 11 |  | 882.972 | 20 | 11 | Univent
213 | Office | 0 | 0 |  | 940.62 | 21 | 0 | Univent
214 | Waiting area | 0 | 0 |  | 912.502 | 20 | 0 | Univent
215 | Waiting area | 0 | 0 |  | 1025.81 | 23 | 0 | Univent
300 | Classroom | 216 | 14 |  | 922.898 | 20 | 14 | Univent
301 | Classroom | 0 | 0 |  | 921.33 | 20 | 0 | Univent
302 | Classroom | 0 | 0 |  | 1010.47 | 22 | 0 | Univent
303 | Classroom | 0 | 0 |  | 912.38 | 20 | 0 | Univent
304 | Classroom | 0 | 0 |  | 986.631 | 22 | 0 | Univent
305 | Classroom | 25 | 1 |  | 618.57 | 14 | 1 | Univent
306 | Classroom | 0 | 0 |  | 932.119 | 21 | 0 | Univent
307 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
309 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
310 | Classroom | 280 | 18 |  | 1009.5 | 22 | 18 | Univent
312 | Classroom | 0 | 0 |  | 992.166 | 22 | 0 | Univent
313 | Classroom | 0 | 0 |  | 978.97 | 22 | 0 | Univent
314 | Classroom | 0 | 0 |  | 911.255 | 20 | 0 | Univent
315 | Classroom |  | 0 |  | 863.91 | 19 | 0 | Univent
400 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
401 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
402 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
403 | Classroom | 194 | 12 |  |  | 0 | 0 | Univent
404 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
405 | Classroom | 92 | 6 |  |  | 0 | 0 | Univent
406 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
407 | Classroom | 131 | 8 |  |  | 0 | 0 | Univent
409 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
410 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
411/413 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
412 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
414 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
415 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent
- | Faculty Rm. | 0 | 0 |  |  | 0 | 0 | Univent
- | Main office | 0 | 0 |  | 1107.41 | 25 | 0 | Univent
- | Princ. Office | 682 | 45 |  | 355.756 | 8 | 8 | Univent

## Sullivan
Sheet Last Modified: | 2021-04-27
School: | James J. Sullivan Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B7 | Classroom |  | 0 | Yes | 610 | 13 | 13 | House Fan
B2 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
- | Library |  | 0 | Yes | 968 | 22 | 22 | House Fan
B9 | Classroom |  | 0 |  | 506 | 11 | 0 | House Fan
- | Kitchen |  | 0 |  | 704 | 16 | 0 | House Fan
101 | Classroom |  | 0 | Yes | 920 | 20 | 20 | House Fan
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
103 | Classroom |  | 0 |  | 736 | 16 | 0 | House Fan
104 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
105 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
106 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
107 | Classroom |  | 0 | Yes | 275 | 6 | 6
107a | office |  | 0 | Yes | 115 | 2 | 2 | House Fan
107b | office |  | 0 | Yes | 115 | 2 | 2 | House Fan
107c | office |  | 0 | Yes | 115 | 2 | 2 | House Fan
108 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
109 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan
110 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
- | Main Office |  | 0 | Yes | 336 | 7 | 7 | House Fan
- | Principal's Office |  | 0 | Yes | 210 | 4 | 4 | House Fan
201 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
203 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
204 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
205 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
206 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
207 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
208 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
209 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
210 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
211 | Classroom |  | 0 | Yes | 192 | 4 | 4 | House Fan
214 | Classroom |  | 0 | Yes | 384 | 8 | 8 | House Fan
215 | Office |  | 0 | Yes | 195 | 4 | 4 | House Fan
- | Nurses Office |  | 0 | Yes | 264 | 6 | 6 | House Fan
300 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan
301 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
302 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
303 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
304 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
305 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
306 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
307 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan
307B | Classroom |  | 0 | Yes | 119 | 2 | 2
308 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
309 | Computer Room |  | 0 |  | 690 | 15 | 0 | House Fan
310 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan
311 | Office |  | 0 | Yes | 192 | 4 | 4 | House Fan
- | Cafe/Gym |  | 0 | Yes | 3432 | 78 | 78 | Hydroxyl Unit

## Sulzberger
Sheet Last Modified: | 2021-04-27
School: | Parkway West High School @ Sulzberger
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | - |  | 0 |  | 483 | 10 | 0
101 | - |  | 0 |  | 575 | 13 | 0
102 | - |  | 0 |  | 851 | 19 | 0
106 | - |  | 0 |  | 920 | 20 | 0
107 | - |  | 0 | Yes | 943 | 21 | 21
108 | - |  | 0 | Yes | 874 | 19 | 19
109 | - |  | 0 |  | 920 | 20 | 0
201 | - |  | 0 |  | 682 | 15 | 0
202 | - |  | 0 |  | 660 | 15 | 0
203 | - |  | 0 | Yes | 528 | 12 | 12
203A | - |  | 0 | Yes | 660 | 15 | 15
204 | Nurses Office |  | 0 | Yes | 460 | 10 | 10
205 | - |  | 0 | Yes | 660 | 15 | 15
206 | Counselors Office |  | 0 | Yes | 690 | 15 | 15
Principal | Office |  | 0 | Yes | 322 | 7 | 7
208 | Main Office |  | 0 | Yes | 825 | 18 | 18
210 | - |  | 0 |  | 836 | 19 | 0
211 | - |  | 0 | Yes | 864 | 19 | 19
212 | - |  | 0 | Yes | 660 | 15 | 15
212A | - |  | 0 | Yes | 660 | 15 | 15
213 | - |  | 0 | Yes | 682 | 15 | 15
215 | - |  | 0 |  | 816 | 18 | 0
216 | - |  | 0 | Yes | 748 | 17 | 17
217 | - |  | 0 | Yes | 736 | 16 | 16
218 | - |  | 0 | Yes | 704 | 16 | 16
219 | - |  | 0 | Yes | 704 | 16 | 16
220 | - |  | 0 | Yes | 704 | 16 | 16
221 | - |  | 0 |  | 805 | 18 | 0
222 | - |  | 0 |  | 690 | 15 | 0
301-302 | - |  | 0 | Yes | 1012 | 23 | 23
303 | - |  | 0 | Yes | 1176 | 26 | 26
304 | - |  | 0 | Yes | 966 | 21 | 21
305 | - |  | 0 |  | 858 | 19 | 0
306 | - |  | 0 | Yes | 770 | 17 | 17
307 | - |  | 0 |  | 770 | 17 | 0
308 | - |  | 0 | Yes | 900 | 20 | 20
309 | - |  | 0 |  | 880 | 20 | 0
310 | - |  | 0 |  | 880 | 20 | 0
311 | - |  | 0 |  | 924 | 21 | 0
312 | - |  | 0 | Yes | 682 | 15 | 15
313 | - |  | 0 | Yes | 660 | 15 | 15
314 | - |  | 0 | Yes | 682 | 15 | 15
315 | - |  | 0 |  | 330 | 7 | 0
316 | - |  | 0 | Yes | 660 | 15 | 15
317 | - |  | 0 |  | 748 | 17 | 0
318 | - |  | 0 | Yes | 736 | 16 | 16
319 | - |  | 0 | Yes | 616 | 14 | 14
320 | - |  | 0 | Yes | 616 | 14 | 14
321 | - |  | 0 |  | 704 | 16 | 0
322 | - |  | 0 | Yes | 748 | 17 | 17
323 | - |  | 0 |  | 638 | 14 | 0
- | 3rd Flr. Computer Lab |  | 0 |  | 1035 | 23 | 0
- | Auditorium |  | 0 |  | 3390 | 77 | 0
- | North Caf. |  | 0 |  | 2680 | 60 | 0
- | South Caf. |  | 0 | Yes | 2720 | 61 | 61
- | South Gym |  | 0 |  | 4186 | 95 | 0

## Swenson
Sheet Last Modified: | 2021-04-30
School: | Swenson Arts & Technology High School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
49 | Classroom |  | 0 | Yes | 308 | 7 | 7
50 | Classroom |  | 0 |  | 308 | 7 | 0
51 | Classroom |  | 0 | Yes | 308 | 7 | 7
53 | Classroom |  | 0 | Yes | 616 | 14 | 14
4 | Classroom |  | 0 | Yes | 532 | 12 | 12
5 | Classroom |  | 0 | Yes | 528 | 12 | 12
6 | Classroom |  | 0 |  | 132 | 3 | 0
100 | Classroom | 242.1 | 16 |  | 1278 | 29 | 16 | Rooftop Unit
101 | Classroom | 142.9 | 9 |  | 228 | 5 | 5 | Rooftop Unit
102 | Classroom | 76.4 | 5 |  | 149 | 3 | 3 | Rooftop Unit
103 | Classroom | 82.1 | 5 |  | 151 | 3 | 3 | Rooftop Unit
104 | Classroom | 115.5 | 7 |  | 144 | 3 | 3 | Rooftop Unit
105 | Classroom | 39.9 | 2 |  | 110 | 2 | 2 | Rooftop Unit
105 | Classroom | 55.1 | 3 |  | 200 | 4 | 3 | Rooftop Unit
106 | Classroom | 75.2 | 5 |  | 178 | 4 | 4 | Rooftop Unit
109 | Classroom | 92.7 | 6 |  | 306 | 6 | 6 | Rooftop Unit
110 | Classroom | 69.5 | 4 |  | 159 | 3 | 3 | Rooftop Unit
111 | Classroom | 42.2 | 2 |  | 146 | 3 | 2 | Rooftop Unit
112 | Classroom | 23.9 | 1 |  | 100 | 2 | 1 | Rooftop Unit
113 | Classroom | 20.9 | 1 | Yes | 105 | 2 | 2 | Rooftop Unit
114 | Classroom | 135.3 | 9 |  | 602 | 13 | 9 | Rooftop Unit
128 | Classroom | 611.7 | 40 |  | 1275 | 28 | 28 | Rooftop Unit
129 | Classroom | 39.4 | 2 |  | 144 | 3 | 2 | Rooftop Unit
130 | Classroom | 535.8 | 35 |  | 960 | 21 | 21 | Rooftop Unit
138 | Classroom | 305 | 20 | Yes | 1125 | 25 | 25 | Rooftop Unit
140 | Classroom | 675.3 | 45 |  | 1085 | 24 | 24 | Rooftop Unit
144 | Classroom | 1497.2 | 99 |  | 1734 | 39 | 39 | Rooftop Unit
146 | Classroom | 649.7 | 43 |  | 700 | 15 | 15 | Rooftop Unit
150 | Classroom | 618 | 41 |  | 308 | 7 | 7 | Rooftop Unit
164 | Classroom | 304.9 | 20 |  | 899 | 20 | 20 | Rooftop Unit
170 | Classroom | 187.6 | 12 |  | 351 | 7 | 7 | Rooftop Unit
171 | Classroom | 526.4 | 35 |  | 1461 | 33 | 33 | Rooftop Unit
172 | Classroom |  | 0 | Yes | 126 | 2 | 2
176 | Classroom |  | 0 | Yes | 452 | 10 | 10
180 | Classroom | 93 | 6 |  | 209 | 4 | 4 | Rooftop Unit
182 | Classroom | 251.3 | 16 | Yes | 1059 | 24 | 24 | Rooftop Unit
184 | Classroom | 227.5 | 15 | Yes | 1628 | 37 | 37 | Rooftop Unit
195 | Classroom | 438.5 | 29 |  | 1566 | 35 | 29 | Rooftop Unit
196 | Classroom | 67.5 | 4 |  | 272 | 6 | 4 | Rooftop Unit
200 | Classroom | 344 | 22 |  | 1624 | 36 | 22 | Rooftop Unit
201 & 201A | Classroom | 211.4 | 14 | Yes | 660 | 15 | 15 | Rooftop Unit
202 | Classroom | 180.6 | 12 | Yes | 836 | 19 | 19 | Rooftop Unit
203 | Classroom | 189.5 | 12 |  | 760 | 17 | 12 | Rooftop Unit
204 | Classroom |  | 0 | Yes | 1584 | 36 | 36 | Rooftop Unit
205 | Classroom | 327.8 | 21 | Yes | 1925 | 43 | 43 | Rooftop Unit
207 | Classroom | 993.8 | 66 |  | 2300 | 52 | 52 | Rooftop Unit
210 | Classroom | 1277.8 | 85 |  | 1020 | 23 | 23 | Rooftop Unit
213 | Classroom |  | 0 | Yes | 748 | 17 | 17 | Rooftop Unit
214 | Classroom |  | 0 | Yes | 126 | 2 | 2
216 | Classroom | 409.7 | 27 |  | 1597 | 36 | 27 | Rooftop Unit
216 | Classroom | 1577.8 | 105 |  | 1597 | 36 | 36 | Rooftop Unit
227 | Classroom | 225 | 15 | Yes | 840 | 19 | 19 | Rooftop Unit
228 | Classroom | 135.2 | 9 | Yes | 930 | 21 | 21 | Rooftop Unit
229 | Classroom | 173.8 | 11 | Yes | 1008 | 22 | 22 | Rooftop Unit
230/231 | Classroom | 87.4 | 5 | Yes | 522 | 11 | 11 | Rooftop Unit
231 | Classroom | 42.8 | 2 |  | 100 | 2 | 2 | Rooftop Unit
232 | Classroom |  | 0 | Yes | 968 | 22 | 22
232B | Classroom | 46 | 3 | Yes | 348 | 7 | 7 | Rooftop Unit
234 | Classroom | 191.5 | 12 | Yes | 900 | 20 | 20 | Rooftop Unit
236 | Classroom | 293 | 19 |  | 1240 | 28 | 19 | Rooftop Unit
237 | Classroom | 185.8 | 12 | Yes | 969 | 22 | 22 | Rooftop Unit
238 | Classroom | 442.3 | 29 |  | 888 | 20 | 20 | Rooftop Unit
245 | Classroom | 281.3 | 18 |  | 675 | 15 | 15 | Rooftop Unit
247 | Classroom | 140 | 9 |  | 448 | 10 | 9 | Rooftop Unit
249 & 249 A-B | Classroom | 520.2 | 34 |  | 414 | 9 | 9 | Rooftop Unit
250 | Classroom | 302.6 | 20 |  | 900 | 20 | 20 | Rooftop Unit
253 | Classroom | 655.2 | 43 |  | 186 | 4 | 4 | Rooftop Unit
257 | Classroom | 341.2 | 22 |  | 756 | 17 | 17 | Rooftop Unit
258 | Classroom | 356.6 | 23 |  | 1050 | 23 | 23 | Rooftop Unit
259 | Classroom | 242.1 | 16 |  | 1225 | 27 | 16 | Rooftop Unit
260 and 260 A-C | Classroom | 579.4 | 38 |  | 561 | 12 | 12 | Rooftop Unit
261 | Classroom | 375.4 | 25 |  | 1050 | 23 | 23 | Rooftop Unit
262 | Classroom | 678.3 | 45 |  | 2373 | 53 | 45 | Rooftop Unit
263 | Classroom |  | 0 | Yes | 2373 | 53 | 53
264 | Classroom | 333.1 | 22 |  | 870 | 19 | 19 | Rooftop Unit
265 | Classroom | 306.8 | 20 |  | 928 | 21 | 20 | Rooftop Unit
1750b | Room | 108.4 | 7 |  | 374 | 8 | 7 | Rooftop Unit
1775A | - |  | 0 | Yes | 528 | 12 | 12
- | Baking Room | 524.7 | 34 |  | 1981 | 45 | 34 | Rooftop Unit
- | Dark Room | 59.1 | 3 |  | 104 | 2 | 2 | Rooftop Unit
- | Corridor | 108.8 | 7 |  | 355 | 8 | 7 | Rooftop Unit
- | Hallway | 640.2 | 42 |  | 730 | 16 | 16 | Rooftop Unit
- | Corridor | 53.5 | 3 |  | 162 | 3 | 3 | Rooftop Unit
- | Corridor | 53.2 | 3 |  | 152 | 3 | 3 | Rooftop Unit
- | Corridor | 167 | 11 |  | 286 | 6 | 6 | Rooftop Unit
- | Corridor | 70.2 | 4 |  | 344 | 7 | 4 | Rooftop Unit
- | Hallway Diffuser s31 | 24.9 | 1 |  | 258 | 5 | 1 | Rooftop Unit
- | Kitchen | 1391 | 92 |  | 205 | 4 | 4 | Rooftop Unit
- | Nurse's Office/Medical | 165.3 | 11 |  | 591 | 13 | 11 | Rooftop Unit
- | Office | 35 | 2 |  | 287 | 6 | 2 | Rooftop Unit
- | Office | 76.7 | 5 |  | 1435 | 32 | 5 | Rooftop Unit
- | Office | 53.9 | 3 |  | 157 | 3 | 3 | Rooftop Unit
- | Office | 597.9 | 39 |  | 94 | 2 | 2 | Rooftop Unit
- | Classroom | 313 | 20 |  | 1769 | 40 | 20 | Rooftop Unit
S1 | Classroom | 309 | 20 |  | 336 | 7 | 7 | Rooftop Unit
S2 | Classroom | 318.4 | 21 |  | 336 | 7 | 7 | Rooftop Unit
S3 | Classroom | 51.8 | 3 |  | 336 | 7 | 3 | Rooftop Unit
S3 | Office | 231.7 | 15 |  | 306 | 6 | 6 | Rooftop Unit
S4 | Office | 14.4 | 0 |  | 20 | 0 | 0 | Rooftop Unit
S5 | Storage | 32.8 | 2 |  | 270 | 6 | 2 | Rooftop Unit
S6 | School Police | 206.6 | 13 |  | 515 | 11 | 11 | Rooftop Unit
S8 | Classroom | 104.2 | 6 |  | 560 | 12 | 6 | Rooftop Unit
- | School Store | 386.2 | 25 |  | 455 | 10 | 10 | Rooftop Unit
- | Second Floor Hallway | 95 | 6 |  | 1846 | 41 | 6 | Rooftop Unit
- | Storage | 32.7 | 2 |  | 590 | 13 | 2 | Rooftop Unit
- | Storage | 107.1 | 7 |  | 35 | 0 | 0 | Rooftop Unit
- | Storage | 72.6 | 4 |  | 134 | 3 | 3 | Rooftop Unit
- | Storage | 44 | 2 |  | 94 | 2 | 2 | Rooftop Unit
- | Storage | 45.1 | 3 |  | 91 | 2 | 2 | Rooftop Unit
- | Storage/Closet | 236.8 | 15 |  | 50 | 1 | 1 | Rooftop Unit

## Taggart
Sheet Last Modified: | 2021-04-23
School: | John H. Taggart Elementary-Middle School
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 |  | 638 | 14 | 0
102-A | Classroom |  | 0 |  | 372 | 8 | 0
102-B | Classroom |  | 0 |  | 230 | 5 | 0
103 | Classroom |  | 0 |  | 506 | 11 | 0
104 | Classroom |  | 0 | Yes | 594 | 13 | 13
107 | Classroom |  | 0 | Yes | 682 | 15 | 15
108 | Nurse's Office |  | 0 | Yes | 176 | 4 | 4
- | 2nd Floor Dean of Student's Office |  | 0 |  | 144 | 3 | 0
200 | Classroom |  | 0 | Yes | 667 | 15 | 15
201 | Classroom |  | 0 | Yes | 667 | 15 | 15
202 | Classroom |  | 0 | Yes | 667 | 15 | 15
203 | Classroom |  | 0 |  | 136 | 3 | 0
204 | Computer Lab |  | 0 | Yes | 924 | 21 | 21
205 | Classroom |  | 0 |  | 414 | 9 | 0
206 | Classroom |  | 0 | Yes | 736 | 16 | 16
207 | Classroom |  | 0 | Yes | 667 | 15 | 15
208 | Classroom |  | 0 | Yes | 638 | 14 | 14
209 | Classroom |  | 0 | Yes | 638 | 14 | 14
- | 3rd Floor Men's Room |  | 0 |  | 56 | 1 | 0
300 | Classroom |  | 0 | Yes | 638 | 14 | 14
301 | Classroom |  | 0 | Yes | 667 | 15 | 15
302 | Classroom |  | 0 | Yes | 667 | 15 | 15
303 | Classroom |  | 0 | Yes | 616 | 14 | 14
304 | Classroom |  | 0 | Yes | 594 | 13 | 13
305-306 | Library |  | 0 | Yes | 1320 | 30 | 30
307 | Classroom |  | 0 | Yes | 638 | 14 | 14
308 | Classroom |  | 0 | Yes | 660 | 15 | 15
309 | Classroom |  | 0 |  | 638 | 14 | 0
400 | Classroom |  | 0 | Yes | 667 | 15 | 15
401 | Classroom |  | 0 | Yes | 667 | 15 | 15
402 | Classroom |  | 0 | Yes | 667 | 15 | 15
403 | Classroom |  | 0 | Yes | 638 | 14 | 14
404 | Classroom |  | 0 | Yes | 667 | 15 | 15
405 | Classroom |  | 0 | Yes | 667 | 15 | 15
406 | Classroom |  | 0 | Yes | 667 | 15 | 15
407 | Classroom |  | 0 | Yes | 667 | 15 | 15
408 | Classroom |  | 0 | Yes | 638 | 14 | 14
409 | Classroom |  | 0 | Yes | 667 | 15 | 15
410 | Classroom |  | 0 | Yes | 638 | 14 | 14
500 | Classroom |  | 0 | Yes | 132 | 3 | 3
- | Gym |  | 0 | Yes | 3555 | 80 | 80 | Hydroxyl Unit
- | Building Engineer's Office |  | 0 |  | 286 | 6 | 0
- | Main Office |  | 0 | Yes | 286 | 6 | 6
- | Principal's Office |  | 0 | Yes | 154 | 3 | 3
- | Teacher's Lounge |  | 0 |  | 322 | 7 | 0

## Taylor
Sheet Last Modified: | 2021-03-18
School: | Bayard Taylor Elementary School
Vendor: | EMCOR Main Building Test 10-29-20
Vendor: | Devine Main Building Retest 2-7-21
School: | Bayard Taylor Annex (Our Lady of Pompeii)
Vendor: | EMCOR | EMCOR Retest 2-18-21
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Taylor Main Building
B1 | Classroom | 210 | 14 |  | 780 | 17 | 14 | Univent
B1B and B1B North & South. | B1 and B1 North & South. | 325 | 21 |  | 760 | 17 | 17 | Univent
B2A & B2B | Classroom | 0 | 0 |  | 600 | 13 | 0 | Univent
B4 | Classroom | 299 | 19 |  | 1444 | 32 | 19 | Univent
B5 | Classroom | 316 | 21 |  | 1410 | 32 | 21 | Univent
101 | Classroom | 362 | 24 |  | 1159 | 26 | 24 | Univent
102 | Classroom |  | 0 | Yes | 1148 | 26 | 26 | Univent
103 | Classroom | 328 | 21 |  | 1149 | 26 | 21 | Univent
104 | Classroom | 387 | 25 |  | 1107 | 25 | 25 | Univent
105 | Classroom | 387 | 25 |  | 1394 | 31 | 25 | Univent
201 | Classroom | 342 | 22 |  | 1101 | 25 | 22 | Univent
202 | Classroom | 423 | 28 |  | 1097 | 24 | 24 | Univent
203 | Classroom |  | 0 | Yes | 1163 | 26 | 26 | Univent
204 | Classroom | 444 | 29 |  | 1099 | 24 | 24 | Univent
205 | Classroom | 470 | 31 |  | 1098 | 24 | 24 | Univent
206 | Classroom | 408 | 27 |  | 1052 | 23 | 23 | Univent
301 | Classroom |  | 0 | Yes | 1066 | 24 | 24 | Univent
302 | Classroom | 299 | 19 |  | 1065 | 24 | 19 | Univent
303 | Classroom | 317 | 21 |  | 1127 | 25 | 21 | Univent
304 | Classroom | 344 | 22 |  | 1133 | 25 | 22 | Univent
305 | Classroom | 73 | 4 | Yes | 1109 | 25 | 25 | Univent
306 | Classroom | 483 | 32 |  | 1107 | 25 | 25 | Univent
- | IMC Library | 353 | 23 |  | 1641 | 37 | 23 | Univent
- | Music Classroom | 162 | 10 |  | 780 | 17 | 10 | Univent
- | Main Office | 303 | 20 |  | 889 | 20 | 20 | Univent
- | Principal | 359 | 23 |  | 479 | 10 | 10 | Univent
- | Lounge | 232 | 15 |  | 300 | 6 | 6 | Univent
- | Nurse | 148 | 9 |  | 300 | 6 | 6 | Univent
- | Art Classroom | 123 | 8 |  | 1107 | 25 | 8 | Univent
Taylor Annex
222 | Classroom |  | 0 |  | 750 | 17 | 0 | N/A
223 | Classroom |  | 0 |  | 625 | 14 | 0 | N/A
224 | Classroom |  | 0 |  | 675 | 15 | 0 | N/A
231 | Classroom |  | 0 |  | 700 | 15 | 0 | N/A
331 | Classroom |  | 0 |  | 700 | 15 | 0 | N/A
332 | Classroom |  | 0 |  | 750 | 17 | 0 | N/A
333 | Classroom |  | 0 |  | 675 | 15 | 0 | N/A
334 | Classroom |  | 0 |  | 625 | 14 | 0 | N/A
- | Auditorium/Gym/Ca |  | 0 |  | 2516 | 57 | 0 | N/A

## Tilden
Sheet Last Modified: | 2021-04-30
School: | Tilden Middle School
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom |  | 0 |  | 576 | 13 | 0 | House Fan
101 | Classroom |  | 0 |  | 624 | 14 | 0 | House Fan
103 | Classroom |  | 0 | Yes | 960 | 21 | 21 | House Fan
104 | Classroom |  | 0 |  | 1248 | 28 | 0 | House Fan
105 | Classroom |  | 0 | Yes | 1248 | 28 | 28 | House Fan
106 | Classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan
107 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan
109 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan
109A | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan
110 | Classroom |  | 0 | Yes | 616 | 14 | 14 | House Fan
202 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan
203 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan
203A | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan
204 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan
205 | Nurse's office |  | 0 | Yes | 384 | 8 | 8 | House Fan
207A | Principal's Office |  | 0 | Yes | 560 | 12 | 12 | House Fan
207C | Counselor's Suite |  | 0 |  | 120 | 2 | 0 | House Fan
207D | Counselor's Suite |  | 0 | Yes | 120 | 2 | 2 | House Fan
207F | Counselor's Suite |  | 0 | Yes | 120 | 2 | 2 | House Fan
207G | Counselor's Suite |  | 0 | Yes | 120 | 2 | 2 | House Fan
207H | Counselor's Suite |  | 0 |  | 120 | 2 | 0 | House Fan
208 | Main Office |  | 0 | Yes | 560 | 12 | 12 | House Fan
209 | IMC |  | 0 | Yes | 1728 | 39 | 39 | House Fan
211 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan
212 | Classroom |  | 0 | Yes | 1152 | 26 | 26 | House Fan
213 | Classroom |  | 0 |  | 616 | 14 | 0 | House Fan
214 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan
214A | Classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan
215 | Classroom |  | 0 | Yes | 576 | 13 | 13 | House Fan
301 | Classroom |  | 0 |  | 576 | 13 | 0 | House Fan
302 | Carson Valley |  | 0 |  | 288 | 6 | 0 | House Fan
303 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan
303A | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan
304 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan
305 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan
306 | Classroom |  | 0 |  | 616 | 14 | 0 | House Fan
307 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan
308 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan
310 | Classroom |  | 0 |  | 480 | 10 | 0 | House Fan
311 | Classroom |  | 0 |  | 768 | 17 | 0 | House Fan
312 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan
313 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan
314 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan
315 | Dean of Students |  | 0 | Yes | 216 | 4 | 4 | House Fan
316 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan
318 | Classroom |  | 0 |  | 792 | 18 | 0 | House Fan
319 | Classroom |  | 0 |  | 832 | 18 | 0 | House Fan
401 | Classroom |  | 0 | Yes | 625 | 14 | 14 | House Fan
403A | Faculty Lounge |  | 0 | Yes | 792 | 18 | 18 | House Fan
404 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan
404A | Classroom |  | 0 | Yes | 120 | 2 | 2 | House Fan
405 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan
406 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan
407 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan
408 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan
410B | Staff Conference |  | 0 | Yes | 1232 | 28 | 28 | House Fan
411 | Classroom |  | 0 | Yes | 769 | 17 | 17 | House Fan
412 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan
414 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan
415 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan
416 | Classroom |  | 0 | Yes | 392 | 8 | 8 | House Fan
- | Cafeteria |  | 0 | Yes | 5150 | 117 | 117 | House Fan

## Trinidad
Sheet Last Modified: | 2021-03-30
School: | Trinidad Center
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Adult Restroom | 13.3 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Assistant Director's Office | 16 | 1 |  |  | 0 | 0 | Air Handling Unit
- | Boy's Restroom | 15.8 | 1 |  |  | 0 | 0 | Air Handling Unit
- | Computer Room | 30.5 | 2 |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Front Entrance | 34.3 | 2 |  |  | 0 | 0 | Air Handling Unit
- | Girl's Restroom | 18 | 1 |  |  | 0 | 0 | Air Handling Unit
- | Gym |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Hallway |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Head Receptionist's Office | 20.8 | 1 |  |  | 0 | 0 | Air Handling Unit
- | Kitchen | 49.5 | 3 |  |  | 0 | 0 | Air Handling Unit
- | Library |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Main Corridor (Hallway) | 0 | 0 |  |  | 0 | 0 | Air Handling Unit
- | Maintenance Office | 22 | 1 |  |  | 0 | 0 | Air Handling Unit
- | Rear Entrance | 19 | 1 |  |  | 0 | 0 | Air Handling Unit
1 | Classroom | 101 | 6 | Yes | 610 | 13 | 13 | Air Handling Unit
2 | Classroom | 95.3 | 6 | Yes | 610 | 13 | 13 | Air Handling Unit
3 | Classroom | 99.5 | 6 | Yes | 575 | 13 | 13 | Air Handling Unit
4 | Classroom | 112.3 | 7 | Yes | 575 | 13 | 13 | Air Handling Unit
5 | Classroom | 131.5 | 8 |  | 590 | 13 | 8 | Air Handling Unit
6 | Classroom |  | 0 | Yes | 629 | 14 | 14 | Air Handling Unit
7 | Storage |  | 0 | Yes | 609 | 13 | 13 | Air Handling Unit
8 | Storage |  | 0 |  |  | 0 | 0 | Air Handling Unit
9 | Storage |  | 0 |  |  | 0 | 0 | Air Handling Unit
10 | Roof Access |  | 0 |  |  | 0 | 0 | Air Handling Unit
- | Stairway |  | 0 |  |  | 0 | 0 | Air Handling Unit

## U School at Ferguson
Sheet Last Modified: | 2021-03-18
School: | The U School at Ferguson
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B10 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
B11 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
B12 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
110 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
111 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
112 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
113 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator
114 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator
115 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator
210 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
211 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
212 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
213 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator
214 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator
215 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator
310 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
311 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
312 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator
313 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator
314 | Classroom | 0 | 0 |  | 442 | 10 | 0 | Unit Ventilator
315 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator

## Vare-Washington
Sheet Last Modified: | 2021-04-06
School: | Vare-Washington Elementary School
Vendor: | EMCOR Fluidics | EMCOR Retest | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | classroom | 478 | 31 |  | 1040 | 23 | 23 | Unit Ventilator
102 | classroom | 251 | 16 | Yes | 936 | 21 | 21 | Unit Ventilator
103 | classroom | 267 | 17 |  | 780 | 17 | 17 | Unit Ventilator
104 | classroom | 331 | 22 |  | 780 | 17 | 17 | Unit Ventilator
105 | classroom | 297 | 19 |  | 936 | 21 | 19 | Unit Ventilator
106 | classroom | 390 | 26 |  | 1040 | 23 | 23 | Unit Ventilator
107 | classroom | 210 | 14 | Yes | 780 | 17 | 17 | Unit Ventilator
108 | classroom | 319 | 21 |  | 767 | 17 | 17 | Unit Ventilator
109 | classroom | 313 | 20 |  | 767 | 17 | 17 | Unit Ventilator
110 | classroom | 594 | 39 |  | 1482 | 33 | 33 | Unit Ventilator
201 | Counselor | 380 | 25 |  | 684 | 15 | 15 | Unit Ventilator
202 | classroom | 326 | 21 |  | 832 | 18 | 18 | Unit Ventilator
203 | 4-6 Autistic Supp. | 316 | 21 |  | 832 | 18 | 18 | Unit Ventilator
204 | classroom | 310 | 20 |  | 832 | 18 | 18 | Unit Ventilator
205 | K-2 Autistic Supp. | 210 | 14 | Yes | 832 | 18 | 18 | Unit Ventilator
206 | classroom | 417 | 27 |  | 832 | 18 | 18 | Unit Ventilator
207 | classroom | 227 | 15 |  | 832 | 18 | 15 | Unit Ventilator
208A | 3-4 Autistic Supp. | 293 | 19 |  | 832 | 18 | 18 | Unit Ventilator
208B | K-2 Emotional Support | 297 | 19 |  | 725 | 16 | 16 | Unit Ventilator
210 | ESOL | 234 | 15 |  | 575 | 13 | 13 | Unit Ventilator
211 | ESOL/SBTL | 251 | 16 |  | 628 | 14 | 14 | Unit Ventilator
213 | classroom | 405 | 27 |  | 1092 | 24 | 24 | Unit Ventilator
214 | classroom | 322 | 21 |  | 468 | 10 | 10 | Unit Ventilator
301 | classroom | 258 | 17 |  | 780 | 17 | 17 | Unit Ventilator
302 | classroom | 291 | 19 |  | 780 | 17 | 17 | Unit Ventilator
303 | classroom | 217 | 14 | Yes | 780 | 17 | 17 | Unit Ventilator
304 | classroom | 234 | 15 |  | 780 | 17 | 15 | Unit Ventilator
305 | classroom | 287 | 19 |  | 780 | 17 | 17 | Unit Ventilator
306 | classroom | 323 | 21 |  | 690 | 15 | 15 | Unit Ventilator
307 | classroom | 217 | 14 | Yes | 780 | 17 | 17 | Unit Ventilator
308 | classroom | 269 | 17 |  | 988 | 22 | 17 | Unit Ventilator
309 | Psychologist / Climate Liaison | 185 | 12 |  | 598 | 13 | 12 | Unit Ventilator
310 | Math Interventionist | 211 | 14 |  | 624 | 14 | 14 | Unit Ventilator
311 | classroom | 189 | 12 | Yes | 624 | 14 | 14 | Unit Ventilator
312A | classroom | 295 | 19 |  | 1014 | 23 | 19 | Unit Ventilator
313 | classroom | 166 | 11 |  | 494 | 11 | 11 | Unit Ventilator
- | Gym | 305 | 20 |  | 4352 | 98 | 20 | Unit Ventilator
- | Library | 208 | 13 |  | 578 | 13 | 13 | Unit Ventilator
- | Lunch Room | 146 | 9 | Yes | 1292 | 29 | 29 | Unit Ventilator
- | Music | 748 | 49 |  | 1098 | 24 | 24 | Unit Ventilator
- | Main Office |  | 0 | Yes | 396 | 9 | 9 | Active Pure Unit
- | Princpal's Office |  | 0 | Yes | 350 | 7 | 7 | Active Pure Unit
- | Nurse's Office |  | 0 | Yes | 264 | 6 | 6 | Active Pure Unit

## Vare, EH
Sheet Last Modified: | 2021-03-12
School: | EH Vare
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
109 | - |  | 0 |  |  | 0 | 0
110 | - |  | 0 |  |  | 0 | 0

## Wagner
Sheet Last Modified: | 2021-04-21
School: | General Louis Wagner Middle School
Vendor: | EMCOR Fluidics | Exhaust Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101A | classroom | 312 | 20 |  | 552 | 12 | 12 | Air Handling Unit
101B | classroom | 376 | 25 |  | 506 | 11 | 11 | Air Handling Unit
102 | classroom | 644 | 42 |  | 888 | 20 | 20 | Air Handling Unit
103A | classroom | 1312 | 87 |  | 1344 | 30 | 30 | Air Handling Unit
105 | classroom | 527 | 35 |  | 878 | 19 | 19 | Air Handling Unit
106 | classroom | 713 | 47 |  | 883 | 20 | 20 | Air Handling Unit
107 | classroom | 635 | 42 |  | 705 | 16 | 16 | Air Handling Unit
108 | classroom | 586 | 39 |  | 916 | 20 | 20 | Air Handling Unit
111 | classroom | 536 | 35 |  | 360 | 8 | 8 | Air Handling Unit
112 | classroom | 585 | 39 |  | 720 | 16 | 16 | Air Handling Unit
201 | classroom | 973 | 64 |  | 711 | 16 | 16 | Air Handling Unit
202 | classroom | 907 | 60 |  | 677 | 15 | 15 | Air Handling Unit
203 | classroom | 306 | 20 |  | 697 | 15 | 15 | Air Handling Unit
204 | classroom | 600 | 40 |  | 657 | 14 | 14 | Air Handling Unit
205A | Counselor Office | 597 | 39 |  | 306 | 6 | 6 | Air Handling Unit
205B | Counselor Office | 690 | 46 |  | 306 | 6 | 6 | Air Handling Unit
209A | classroom | 496 | 33 |  | 2064 | 46 | 33 | Air Handling Unit
209B | classroom | 763 | 50 |  | 336 | 7 | 7 | Air Handling Unit
209C | classroom | 995 | 66 |  | 336 | 7 | 7 | Air Handling Unit
212 | classroom | 1030 | 68 |  | 859 | 19 | 19 | Air Handling Unit
213 | classroom | 870 | 58 |  | 656 | 14 | 14 | Air Handling Unit
214 | classroom | 446 | 29 |  | 714 | 16 | 16 | Air Handling Unit
215 | classroom | 240 | 16 |  | 659 | 14 | 14 | Air Handling Unit
216 | classroom | 2170 | 144 |  | 777 | 17 | 17 | Air Handling Unit
217 | classroom | 1626 | 108 |  | 743 | 16 | 16 | Air Handling Unit
218 | classroom | 197 | 13 |  | 645 | 14 | 13 | Air Handling Unit
219 | classroom | 1463 | 97 |  | 643 | 14 | 14 | Air Handling Unit
220 | classroom | 731 | 48 |  | 563 | 12 | 12 | Air Handling Unit
221 | classroom | 1653 | 110 |  | 779 | 17 | 17 | Air Handling Unit
222 | classroom | 667 | 44 |  | 670 | 15 | 15 | Air Handling Unit
225 | Dean | 272 | 18 |  | 348 | 7 | 7 | Air Handling Unit
226 | classroom | 671 | 44 |  | 654 | 14 | 14 | Air Handling Unit
301 | classroom | 1282 | 85 |  | 714 | 16 | 16 | Air Handling Unit
302 | classroom | 2224 | 148 |  | 670 | 15 | 15 | Air Handling Unit
303 | classroom | 2929 | 195 |  | 671 | 15 | 15 | Air Handling Unit
304A | classroom | 1335 | 89 |  | 984 | 22 | 22 | Air Handling Unit
305 | classroom | 3981 | 265 |  | 956 | 21 | 21 | Air Handling Unit
306 | classroom | 3461 | 230 |  | 783 | 17 | 17 | Air Handling Unit
307 | classroom | 996 | 66 |  | 912 | 20 | 20 | Air Handling Unit
308 | classroom | 1202 | 80 |  | 928 | 21 | 21 | Air Handling Unit
309 | classroom | 2171 | 144 |  | 847 | 19 | 19 | Air Handling Unit
310 | classroom | 2047 | 136 |  | 881 | 20 | 20 | Air Handling Unit
311A | classroom | 990 | 66 |  | 929 | 21 | 21 | Air Handling Unit
312 | classroom | 211 | 14 |  | 716 | 16 | 14 | Air Handling Unit
313 | classroom | 868 | 57 |  | 672 | 15 | 15 | Air Handling Unit
314 | classroom | 350 | 23 |  | 719 | 16 | 16 | Air Handling Unit
315 | classroom | 83 | 5 |  | 662 | 15 | 5 | Air Handling Unit
316 | classroom | 1078 | 71 |  | 778 | 17 | 17 | Air Handling Unit
317 | classroom | 1382 | 92 |  | 604 | 13 | 13 | Air Handling Unit
318 | classroom | 1811 | 120 |  | 610 | 13 | 13 | Air Handling Unit
319 | classroom | 3185 | 212 |  | 644 | 14 | 14 | Air Handling Unit
320 | classroom | 4504 | 300 |  | 738 | 16 | 16 | Air Handling Unit
321 | classroom | 3538 | 235 |  | 786 | 17 | 17 | Air Handling Unit
322 | classroom | 82 | 5 |  | 660 | 15 | 5 | Air Handling Unit
323 | classroom | 1074 | 71 |  | 324 | 7 | 7 | Air Handling Unit
324 | classroom | 909 | 60 |  | 659 | 14 | 14 | Air Handling Unit
325 | classroom | 1021 | 68 |  | 346 | 7 | 7 | Air Handling Unit
326 | classroom | 481 | 32 |  | 659 | 14 | 14 | Air Handling Unit
326 | Counselor Office | 513 | 34 |  | 306 | 6 | 6 | Air Handling Unit
- | Auditorium | 0 | 0 |  | 5460 | 124 | 0 | Air Handling Unit
- | Boy's Gym | 14624 | 974 |  | 4350 | 98 | 98 | Air Handling Unit
- | Cafeteria | 498 | 33 |  | 408 | 9 | 9 | Air Handling Unit
- | Computer Lab | 446 | 29 |  | 657 | 14 | 14 | Air Handling Unit
- | Conf. Room | 884 | 58 |  | 336 | 7 | 7 | Air Handling Unit
- | Kitchen | 5749 | 383 |  | 816 | 18 | 18 | Air Handling Unit
- | Kitchen- Freezer/Cooler Condenser Fan | 0 | 0 |  | 144 | 3 | 0 | Air Handling Unit
- | Lunch Room | 175 | 11 |  | 2040 | 46 | 11 | Air Handling Unit
- | Main Office | 632 | 42 |  | 531 | 12 | 12 | Air Handling Unit
Principal | Office |  | 0 | Yes | 259 | 5 | 5
Nurse | Office |  | 0 | Yes | 249 | 5 | 5
- | MEDIA LAB A | 304 | 20 |  | 60 | 1 | 1 | Air Handling Unit
- | MEDIA LAB B | 564 | 37 |  | 60 | 1 | 1 | Air Handling Unit
- | Staff Lounge | 421 | 28 |  | 657 | 14 | 14 | Air Handling Unit
- | VP Office | 1325 | 88 |  | 232 | 5 | 5 | Air Handling Unit
- | Gym- Weight Room A | 1230 | 82 |  | 181 | 4 | 4 | Air Handling Unit
- | Gym- Weight Room B | 1164 | 77 |  | 181 | 4 | 4 | Air Handling Unit

## Waring
Sheet Last Modified: | 2021-04-26
School: | Laura W. Waring Elementary School
Vendor: | EMCOR Fluidics | EMCOR Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 188 | 12 | Yes | 430 | 9 | 9 | Nesbitt Unit Ventilator
102 | Classroom | 118 | 7 | Yes | 872 | 19 | 19 | Nesbitt Unit Ventilator
103 | Classroom | 150 | 10 | Yes | 872 | 19 | 19 | Nesbitt Unit Ventilator
105 | Classroom | 180 | 12 | Yes | 789 | 17 | 17 | Nesbitt Unit Ventilator
106 | Classroom | 171 | 11 | Yes | 850 | 19 | 19 | Nesbitt Unit Ventilator
107 | Classroom | 226 | 15 |  | 850 | 19 | 15 | Nesbitt Unit Ventilator
108 | Classroom | 165 | 11 | Yes | 750 | 17 | 17 | Nesbitt Unit Ventilator
200 | Counselor's Room | 0 | 0 |  | 300 | 6 | 0 | Nesbitt Unit Ventilator
201 | Computer Room | 0 | 0 | Yes | 925 | 21 | 21 | Nesbitt Unit Ventilator
202 | Classroom | 87 | 5 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator
203 | Classroom | 274 | 18 |  | 888 | 20 | 18 | Nesbitt Unit Ventilator
204 | Classroom | 276 | 18 |  | 888 | 20 | 18 | Nesbitt Unit Ventilator
205 | Classroom | 311 | 20 |  | 850 | 19 | 19 | Nesbitt Unit Ventilator
206 | Classroom | 193 | 12 | Yes | 850 | 19 | 19 | Nesbitt Unit Ventilator
207 | Classroom | 152 | 10 | Yes | 850 | 19 | 19 | Nesbitt Unit Ventilator
208 | Classroom | 209 | 13 | Yes | 750 | 17 | 17 | Nesbitt Unit Ventilator
300 | Classroom | 0 | 0 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator
301 | Classroom | 212 | 14 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator
302 | Classroom | 105 | 7 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator
303 | Classroom | 133 | 8 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator
304 | Classroom | 255 | 17 |  | 888 | 20 | 17 | Nesbitt Unit Ventilator
305 | Classroom | 93 | 6 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator
306/307 | Classroom | 266 | 17 |  | 1850 | 42 | 17 | Nesbitt Unit Ventilator
308 | Classroom | 220 | 14 | Yes | 896 | 20 | 20 | Nesbitt Unit Ventilator
311 | Dining Room | 120 | 8 |  | 242 | 5 | 5 | Nesbitt Unit Ventilator
- | Cafeteria | 0 | 0 |  | 3477 | 79 | 0 | Nesbitt Unit Ventilator
- | Vestibule left of office | 0 | 0 |  | 96 | 2 | 0 | Nesbitt Unit Ventilator
- | Nurse |  | 0 |  | 231 | 5 | 0 | Nesbitt Unit Ventilator
- | Faculty Lounge | 57 | 3 |  | 228 | 5 | 3 | Nesbitt Unit Ventilator
- | Health Office | 0 | 0 | Yes | 231 | 5 | 5 | Nesbitt Unit Ventilator
- | Multi-Purpose Room | 457 | 30 |  | 1820 | 41 | 30 | Nesbitt Unit Ventilator
- | Main Office | 0 | 0 | Yes | 378 | 8 | 8 | Nesbitt Unit Ventilator
- | Principal's Office | 69 | 4 | Yes | 381 | 8 | 8 | Nesbitt Unit Ventilator

## Washington, George
Sheet Last Modified: | 2021-04-30
School: | George Washington High School
Vendor: | EMCOR | Meehan (Auditorium)
School: | George Washington High School Annex
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
1 | - | 370 | 24 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
2 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
3 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
4 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
5 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
6 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
7 | - | 348 | 23 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
8 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
9 | - | 412 | 27 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
10 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
11 | - | 451 | 30 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
12 | - | 0 | 0 |  | 775 | 17 | 0 | Carrier / Perimeter Heater
13 | - | 414 | 27 |  | 1209 | 27 | 27 | Carrier / Perimeter Heater
14 | - | 374 | 24 |  | 1209 | 27 | 24 | Carrier / Perimeter Heater
15 | - | 403 | 26 |  | 1209 | 27 | 26 | Carrier / Perimeter Heater
16 | - | 849 | 56 |  | 1911 | 43 | 43 | Carrier / Perimeter Heater
17 | - | 0 | 0 |  | 1240 | 28 | 0 | Carrier / Perimeter Heater
18 | - | 763 | 50 |  | 1911 | 43 | 43 | Carrier / Perimeter Heater
19 | - | 0 | 0 |  | 1302 | 29 | 0 | Carrier / Perimeter Heater
20 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
21 | - | 451 | 30 |  | 1240 | 28 | 28 | Carrier / Perimeter Heater
22 | - | 421 | 28 |  | 1209 | 27 | 27 | Carrier / Perimeter Heater
23 | - | 0 | 0 |  | 1240 | 28 | 0 | Carrier / Perimeter Heater
24 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
25 | - | 419 | 27 |  | 912 | 20 | 20 | Carrier / Perimeter Heater
26 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
27 | - | 0 | 0 |  | 912 | 20 | 0 | Carrier / Perimeter Heater
28 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
29 | - | 355 | 23 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
30 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
31 | - | 413 | 27 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
32 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
33 | - | 338 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
34 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
35 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
36 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
37 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
38 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
39 | - | 403 | 26 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
100 | - | 334 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
102 | - | 335 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
104 | Health Room |  | 0 |  | 1488 | 33 | 0
107 | - | 495 | 33 |  |  | 0 | 0 | Carrier / Perimeter Heater
108 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
109 | - | 357 | 23 |  | 744 | 16 | 16 | Carrier / Perimeter Heater
110 | - | 413 | 27 |  |  | 0 | 0 | Carrier / Perimeter Heater
111 | - | 370 | 24 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
112 | - | 398 | 26 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
113 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
114 | - | 427 | 28 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
115 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
116 | - | 368 | 24 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
117 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
118 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
119 | - | 368 | 24 |  |  | 0 | 0 | Carrier / Perimeter Heater
120 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
121 | - | 381 | 25 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
122 | - | 408 | 27 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
123 | - | 465 | 31 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
124 | - | 436 | 29 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
125 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
126 | - | 336 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
127 | - | 416 | 27 |  | 1102 | 25 | 25 | Carrier / Perimeter Heater
128 | - | 0 | 0 |  | 1280 | 29 | 0 | Carrier / Perimeter Heater
129 | - | 366 | 24 |  | 1073 | 24 | 24 | Carrier / Perimeter Heater
130 | - | 0 | 0 |  | 1280 | 29 | 0 | Carrier / Perimeter Heater
131 | - | 388 | 25 |  | 1160 | 26 | 25 | Carrier / Perimeter Heater
132 | - | 610 | 40 |  | 1092 | 24 | 24 | Carrier / Perimeter Heater
133 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
134 | - | 732 | 48 |  | 1092 | 24 | 24 | Carrier / Perimeter Heater
135 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
136 | - | 325 | 21 |  | 1092 | 24 | 21 | Carrier / Perimeter Heater
137 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
138 | - | 408 | 27 |  |  | 0 | 0 | Carrier / Perimeter Heater
139 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
140 | - | 424 | 28 |  |  | 0 | 0 | Carrier / Perimeter Heater
141 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
142 | - | 865 | 57 |  |  | 0 | 0 | Carrier / Perimeter Heater
143 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
144 | - | 308 | 20 |  | 832 | 18 | 18 | Carrier / Perimeter Heater
145 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
146 | - | 0 | 0 |  | 775 | 17 | 0 | Carrier / Perimeter Heater
147 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
148 | - | 242 | 16 |  | 775 | 17 | 16 | Carrier / Perimeter Heater
149 -155 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
156 | - | 926 | 61 |  | 814 | 18 | 18 | Carrier / Perimeter Heater
157 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
158 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
159 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
160 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
161 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
162 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
164 | - | 695 | 46 |  |  | 0 | 0 | Carrier / Perimeter Heater
200 | - | 485 | 32 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
201 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
202 | - | 417 | 27 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
203 | - | 397 | 26 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
204 | - | 337 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
205 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
206 | - | 424 | 28 |  |  | 0 | 0 | Carrier / Perimeter Heater
207 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
208 | - | 536 | 35 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
209 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
210 | - | 575 | 38 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
211 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
212 | - | 514 | 34 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
213 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
214 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
215 | - | 547 | 36 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
216 | - | 519 | 34 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
217 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
218 | - | 521 | 34 |  | 1536 | 34 | 34 | Carrier / Perimeter Heater
219 | - | 0 | 0 |  | 1536 | 34 | 0 | Carrier / Perimeter Heater
220 | - | 0 | 0 |  | 1536 | 34 | 0 | Carrier / Perimeter Heater
221 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
222 | - | 569 | 37 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
223 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
224 | - | 533 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
225 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
226 | - | 536 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
227 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
228 | - | 543 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
229 | - | 508 | 33 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
230 | - | 563 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
231 | - | 492 | 32 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
232 | - | 563 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
233 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
234 | - | 539 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
235 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
236 | - | 544 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
237 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
238 | - | 399 | 26 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
239 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
240 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater
241 | - | 344 | 22 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
242 | - | 450 | 30 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
243 | - | 455 | 30 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
244 | - | 428 | 28 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
245 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
246 | - | 423 | 28 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
300 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
301 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
302 | - | 542 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
303 | - | 539 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
304 | - | 591 | 39 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
305 | - | 556 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
306 | - | 561 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
307 | - | 592 | 39 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
308 | - | 263 | 17 |  | 792 | 18 | 17 | Carrier / Perimeter Heater
309 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
310 | - | 602 | 40 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
311 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
312 | - | 599 | 39 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
313 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
314 | - | 539 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
315 | - | 530 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
316 | - | 557 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
317 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
318 | - | 580 | 38 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
319 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
320 | - | 610 | 40 |  | 768 | 17 | 17 | Carrier / Perimeter Heater
321 | - | 551 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
322 | - | 554 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
323 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
324 | - | 591 | 39 |  | 960 | 21 | 21 | Carrier / Perimeter Heater
325 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
326 | - | 533 | 35 |  | 960 | 21 | 21 | Carrier / Perimeter Heater
327 | - | 554 | 36 |  | 960 | 21 | 21 | Carrier / Perimeter Heater
328 | - | 561 | 37 |  | 960 | 21 | 21 | Carrier / Perimeter Heater
329 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
330 | - | 572 | 38 |  | 960 | 21 | 21 | Carrier / Perimeter Heater
331 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
332 | - | 576 | 38 |  | 792 | 18 | 18 | Carrier / Perimeter Heater
333 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
334 | - | 506 | 33 |  | 960 | 21 | 21 | Carrier / Perimeter Heater
335 | - | 605 | 40 |  |  | 0 | 0 | Carrier / Perimeter Heater
336 | - | 559 | 37 |  | 960 | 21 | 21 | Carrier / Perimeter Heater
337 | - | 0 | 0 |  | 792 | 18 | 0 | Carrier / Perimeter Heater
338 | - | 0 | 0 |  | 792 | 18 | 0 | Carrier / Perimeter Heater
339 | - | 0 | 0 |  | 792 | 18 | 0 | Carrier / Perimeter Heater
Gymnasium | Gymnasium |  | 0 |  |  | 0 | 0
Auditorium | Auditorium | 17891 | 1192 |  | 10800 | 245 | 245 | Air Handling Unit
- | Beacon Left | 311 | 20 |  |  | 0 | 0 | Carrier / Perimeter Heater
- | Beacon Right | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
- | Cafeteria | 17015 | 1134 |  |  | 0 | 0 | Air Handling Unit
Center | - | 438 | 29 |  |  | 0 | 0 | Carrier / Perimeter Heater
Dean's Office | - | 437 | 29 |  |  | 0 | 0 | Carrier / Perimeter Heater
Library Left | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
Main Office | - | 394 | 26 |  | 2332 | 53 | 26 | Carrier / Perimeter Heater
Principle | - | 0 | 0 |  | 615 | 13 | 0 | Carrier / Perimeter Heater
Right | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater
- | Roster | 426 | 28 |  |  | 0 | 0 | Carrier / Perimeter Heater
- | Staff Cafeteria | 1328 | 88 |  |  | 0 | 0 | Make-up Air Unit
- | Student Cafeteria | 8507 | 567 |  | 12000 | 272 | 272 | Make-up Air Unit
Annex
408 Annex | Classroom |  | 0 | Yes | 858 | 19 | 19 | Air Handling Unit
409 Annex | Classroom |  | 0 | Yes | 858 | 19 | 19 | Air Handling Unit
410 Annex | Classroom |  | 0 | Yes | 858 | 19 | 19 | Air Handling Unit
412 Annex | Classroom |  | 0 | Yes |  | 0 | 0 | Air Handling Unit
Kitchen Annex | Kitchen |  | 0 | Yes |  | 0 | 0 | Air Handling Unit
Recceration room | - |  | 0 |  | 3780 | 85 | 85
Health Suite/ 11 rms | - |  | 0 |  | 77 | 1 | 1
Health Suite/ 2 rms | - |  | 0 |  | 80 | 1 | 1

## Washington, Grover
Sheet Last Modified: | 2021-04-14
School: | Grover Washington Jr. Middle School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | CLASSROOM | 288 | 19 |  | 700 | 15 | 15 | Fan Coil Unit
101 | CLASSROOM | 207 | 13 | Yes | 700 | 15 | 15 | Fan Coil Unit
102 | CLASSROOM | 164 | 10 | Yes | 698 | 15 | 15 | Fan Coil Unit
102A | CLASSROOM | 185 | 12 |  | 160 | 3 | 3 | Fan Coil Unit
103 | CLASSROOM | 476 | 31 |  | 858 | 19 | 19 | Univent
104 | CLASSROOM | 595 | 39 |  | 783 | 17 | 17 | Univent
105 | CLASSROOM | 935 | 62 |  | 726 | 16 | 16 | Univent
106 | CLASSROOM | 421 | 28 |  | 726 | 16 | 16 | Univent
107 | CLASSROOM | 274 | 18 |  | 858 | 19 | 18 | Univent
108 | CLASSROOM | 395 | 26 |  | 858 | 19 | 19 | Univent
109 | CLASSROOM | 573 | 38 |  | 858 | 19 | 19 | Univent
110 | CLASSROOM | 310 | 20 |  | 858 | 19 | 19 | Univent
112 | CLASSROOM | 377 | 25 |  | 858 | 19 | 19 | Univent
113 | CLASSROOM | 392 | 26 |  | 312 | 7 | 7 | Univent
114 | CLASSROOM | 361 | 24 |  | 858 | 19 | 19 | Univent
115 | CLASSROOM | 292 | 19 |  | 726 | 16 | 16 | Univent
116 | CLASSROOM | 749 | 49 |  | 726 | 16 | 16 | Univent
117 | CLASSROOM | 763 | 50 |  | 726 | 16 | 16 | Univent
118 | CLASSROOM | 757 | 50 |  | 726 | 16 | 16 | Univent
119 | CLASSROOM | 396 | 26 |  | 858 | 19 | 19 | Univent
120 | CLASSROOM | 304 | 20 |  | 858 | 19 | 19 | Univent
121 | CLASSROOM | 370 | 24 |  | 858 | 19 | 19 | Univent
122 | CLASSROOM | 314 | 20 |  | 858 | 19 | 19 | Univent
201 | 2ND FLOOR C WING OFFICE | 211 | 14 |  | 312 | 7 | 7 | Univent
202 | CLASSROOM | 601 | 40 |  | 858 | 19 | 19 | Univent
203 | CLASSROOM | 580 | 38 |  | 858 | 19 | 19 | Univent
204 | CLASSROOM | 304 | 20 |  | 858 | 19 | 19 | Univent
205 | CLASSROOM | 285 | 19 |  | 858 | 19 | 19 | Univent
206 | CLASSROOM | 406 | 27 |  | 783 | 17 | 17 | Univent
207 | CLASSROOM | 456 | 30 |  | 726 | 16 | 16 | Univent
208 | CLASSROOM | 561 | 37 |  | 1584 | 36 | 36 | Univent
209 | CLASSROOM | 320 | 21 |  | 858 | 19 | 19 | Univent
210 | CLASSROOM | 388 | 25 |  | 858 | 19 | 19 | Univent
211 | CLASSROOM | 348 | 23 |  | 858 | 19 | 19 | Univent
212 | CLASSROOM | 318 | 21 |  | 858 | 19 | 19 | Univent
213 | CLASSROOM | 307 | 20 |  | 1248 | 28 | 20 | Univent
214 | CLASSROOM | 286 | 19 | Yes | 1144 | 26 | 26 | Univent
215 | CLASSROOM | 693 | 46 |  | 1170 | 26 | 26 | Univent
216 | CLASSROOM | 370 | 24 |  | 783 | 17 | 17 | Univent
217 | CLASSROOM | 306 | 20 |  | 726 | 16 | 16 | Univent
218 | CLASSROOM | 314 | 20 |  | 783 | 17 | 17 | Univent
219 | CLASSROOM | 332 | 22 |  | 858 | 19 | 19 | Univent
220 | CLASSROOM | 407 | 27 |  | 858 | 19 | 19 | Univent
221 | 2ND FLOOR D WING OFFICE | 181 | 12 |  | 312 | 7 | 7 | Univent
301 | CLASSROOM | 112 | 7 | Yes | 858 | 19 | 19 | Fan Coil Unit
302 | CLASSROOM | 339 | 22 |  | 858 | 19 | 19 | Univent
303 | CLASSROOM | 0 | 0 | Yes | 858 | 19 | 19 | Univent
304 | CLASSROOM | 231 | 15 |  | 858 | 19 | 15 | Univent
305 | CLASSROOM | 385 | 25 |  | 858 | 19 | 19 | Univent
306 | CLASSROOM | 353 | 23 |  | 783 | 17 | 17 | Univent
307 | CLASSROOM | 316 | 21 |  | 726 | 16 | 16 | Univent
308 | CLASSROOM | 306 | 20 |  | 1584 | 36 | 20 | Univent
309 | CLASSROOM | 486 | 32 |  | 858 | 19 | 19 | Univent
310 | CLASSROOM | 283 | 18 |  | 858 | 19 | 18 | Univent
311 | CLASSROOM | 265 | 17 |  | 858 | 19 | 17 | Univent
312 | CLASSROOM | 389 | 25 |  | 858 | 19 | 19 | Univent
313 | CLASSROOM | 355 | 23 |  | 858 | 19 | 19 | Univent
314 | CLASSROOM | 305 | 20 | Yes | 1144 | 26 | 26 | Univent
315 | CLASSROOM | 1003 | 66 |  | 1170 | 26 | 26 | Univent
316 | CLASSROOM | 363 | 24 |  | 783 | 17 | 17 | Univent
317 | CLASSROOM | 81 | 5 | Yes | 858 | 19 | 19 | Univent
318 | CLASSROOM | 510 | 34 | Yes | 858 | 19 | 19 | Univent
319 | CLASSROOM | 463 | 30 |  | 858 | 19 | 19 | Univent
320 | CLASSROOM | 0 | 0 | Yes | 858 | 19 | 19 | Univent
- | GYMNASIUM | 900 | 60 |  | 6370 | 144 | 60 | Rooftop Unit
- | CAFETERIA | 3339 | 222 |  | 5160 | 117 | 117 | Rooftop Unit
- | AUDITORIUM | 2146 | 143 |  | 7008 | 159 | 143 | Rooftop Unit
- | KITCHEN HOOD | 8665 | 577 |  | 1584 | 36 | 36 | Rooftop Unit
- | 1ST FLOOR BACK CORR. | 255 | 17 |  | 800 | 18 | 17 | Fan Coil Unit
- | 1ST FLOOR CIRCLE HALL | 220 | 14 |  | 1246 | 28 | 14 | Fan Coil Unit
- | 1ST FLOOR CORR INFRONT OF CAFÉ | 209 | 13 |  | 1008 | 22 | 13 | Fan Coil Unit
- | 1ST FLOOR D WING OFFICE | 149 | 9 |  | 312 | 7 | 7 | Fan Coil Unit
- | 1ST FLOOR ENTRANCE CORR. | 360 | 24 |  | 1053 | 23 | 23 | Fan Coil Unit
- | 1ST FLOOR FRONT CORR. | 1074 | 71 |  | 1008 | 22 | 22 | Fan Coil Unit
- | 1ST FLOOR FRONT HALL | 562 | 37 |  | 1540 | 35 | 35 | Fan Coil Unit
- | 1ST FLOOR OFFICES | 493 | 32 |  | 1888 | 42 | 32 | Fan Coil Unit
- | 2ND / 1ST FLOOR D WING CORR | 380 | 25 |  | 1616 | 36 | 25 | Fan Coil Unit
- | 2ND FLOOR C WING CLUSTER OFFICE | 1861 | 124 |  | 888 | 20 | 20 | Fan Coil Unit
- | 2ND FLOOR C WING CONF. ROOM | 107 | 7 |  | 810 | 18 | 7 | Fan Coil Unit
- | 2ND FLOOR CIRCLE HALL | 136 | 9 |  | 1246 | 28 | 9 | Fan Coil Unit
- | 2ND FLOOR D WING SHOP | 97 | 6 |  | 408 | 9 | 6 | Fan Coil Unit
- | 3RD FLOOR C WING CORR. | 660 | 44 |  | 1616 | 36 | 36 | Fan Coil Unit
- | 3RD FLOOR CIRCLE HALL | 137 | 9 |  | 1246 | 28 | 9 | Fan Coil Unit
- | 3RD FLOOR D WING CORR. | 501 | 33 |  | 1616 | 36 | 33 | Fan Coil Unit
- | 3RD FLOOR D WING OFFICE | 167 | 11 |  | 312 | 7 | 7 | Fan Coil Unit
- | 3RD FLOOR SHOP | 81 | 5 |  | 408 | 9 | 5 | Fan Coil Unit
- | BUILDING ENGINEER | 79 | 5 |  | 156 | 3 | 3 | Fan Coil Unit
- | FACULTY BREAK ROOM | 188 | 12 |  | 648 | 14 | 12 | Fan Coil Unit
- | GYM LOCKER ROOMS | 254 | 16 |  | 532 | 12 | 12 | Fan Coil Unit
- | GYM TEACHER | 144 | 9 |  | 280 | 6 | 6 | Fan Coil Unit
- | INSTRUMENT MUSIC | 0 | 0 | Yes | 1147 | 26 | 26 | Fan Coil Unit
- | IT Room | 268 | 17 |  | 396 | 9 | 9 | Fan Coil Unit
- | KITCHEN OFFICE | 164 | 10 |  | 156 | 3 | 3 | Fan Coil Unit
- | LIBRARY | 769 | 51 |  | 3864 | 87 | 51 | Fan Coil Unit
- | LIBRARY STORAGE | 184 | 12 |  | 396 | 9 | 9 | Fan Coil Unit
- | MUSIC PRACTICE B | 174 | 11 |  | 135 | 3 | 3 | Fan Coil Unit
- | MUSIC PRACTICE C | 272 | 18 |  | 135 | 3 | 3 | Fan Coil Unit
- | MUSIC PRATICE A | 126 | 8 |  | 135 | 3 | 3 | Fan Coil Unit
- | VOCAL MUSIC | 0 | 0 | Yes | 1221 | 27 | 27 | Fan Coil Unit

## Washington, Martha
Sheet Last Modified: | 2021-03-22
School: | Martha Washington Elementary-Middle School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 808 | 53 |  | 782 | 17 | 17 | House Fan
102 | Classroom | 1564 | 104 |  | 920 | 20 | 20 | House Fan
103 | Classroom | 540 | 36 |  | 667 | 15 | 15 | House Fan
104 | Classroom | 250 | 16 |  | 667 | 15 | 15 | House Fan
106 | Classroom | 529 | 35 |  | 667 | 15 | 15 | House Fan
107 | Classroom | 370 | 24 |  | 690 | 15 | 15 | House Fan
108 | Classroom | 279 | 18 |  | 667 | 15 | 15 | House Fan
109 | Classroom | 525 | 35 |  | 667 | 15 | 15 | House Fan
110 | - |  | 0 |  | 667 | 15 | 0 | Univent
111 | - |  | 0 | Yes | 667 | 15 | 15 | Univent
112 | - |  | 0 | Yes | 667 | 15 | 15 | Univent
113 | Classroom |  | 0 | Yes | 667 | 15 | 15 | Univent
201 | Classroom | 1290 | 86 |  | 667 | 15 | 15 | House Fan
202 | Classroom | 990 | 66 |  | 667 | 15 | 15 | House Fan
203 | Classroom | 425 | 28 |  | 759 | 17 | 17 | House Fan
204 | Classroom | 442 | 29 |  | 713 | 16 | 16 | House Fan
205 | Classroom | 345 | 23 |  | 621 | 14 | 14 | House Fan
206 | Classroom | 829 | 55 |  | 667 | 15 | 15 | House Fan
207 | Classroom | 479 | 31 |  | 660 | 15 | 15 | House Fan
208 | Classroom | 489 | 32 |  | 667 | 15 | 15 | House Fan
209 | Classroom | 394 | 26 |  | 667 | 15 | 15 | House Fan
211 | - |  | 0 | Yes | 667 | 15 | 15 | Univent
212 | - |  | 0 | Yes | 667 | 15 | 15 | Univent
301 | Classroom | 551 | 36 |  | 667 | 15 | 15 | House Fan
302 | Classroom | 850 | 56 |  | 667 | 15 | 15 | House Fan
303 | Classroom | 453 | 30 |  | 667 | 15 | 15 | House Fan
304 | Classroom | 236 | 15 |  | 1215 | 27 | 15 | House Fan
305 | Classroom | 62 | 4 |  | 644 | 14 | 4 | House Fan
306 | Classroom | 807 | 53 |  | 667 | 15 | 15 | House Fan
307 | Classroom | 649 | 43 |  | 667 | 15 | 15 | House Fan
308 | Classroom | 506 | 33 |  | 667 | 15 | 15 | House Fan
309 | Classroom | 826 | 55 |  | 667 | 15 | 15 | House Fan
310 | Classroom | 139 | 9 |  | 667 | 15 | 9 | House Fan
- | Main Office |  | 0 | Yes | 420 | 9 | 9 | Radiator
- | Principal's Office |  | 0 | Yes | 234 | 5 | 5 | Radiator
- | Nurse's Office |  | 0 | Yes | 180 | 4 | 4 | Radiator
- | BE's Office | 543 | 36 |  | 782 | 17 | 17 | House Fan
- | Lunch Room A | 1542 | 102 |  | 792 | 18 | 18 | House Fan
- | Lunch Room B | 1570 | 104 |  | 1540 | 35 | 35 | House Fan
G2 | - |  | 0 | Yes | 667 | 15 | 15 | Univent

## Webster
Sheet Last Modified: | 2021-04-23
School: | John H. Webster Elementary School
Vendor: | Devine Brothers | Devine Retest
School: | John H. Webster Elementary School- Little School House
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Webster Main Building
100 | Classroom | 1169 | 77 |  | 656 | 14 | 14 | Univent
101 | Classroom | 593 | 39 |  | 1263 | 28 | 28 | Univent
102 | Classroom | 435 | 29 |  | 721 | 16 | 16 | Univent
103 | Classroom | 1197 | 79 |  | 1062 | 24 | 24 | Univent
104 | Classroom | 251 | 16 |  | 897 | 20 | 16 | Univent
105 | Classroom | 310 | 20 |  | 531 | 12 | 12 | Univent
106 | Classroom | 477 | 31 |  | 949 | 21 | 21 | Univent
108 | Office | 49 | 3 |  | 226 | 5 | 3 | Air Handling Unit
110 | Classroom | 358 | 23 |  | 1365 | 31 | 23 | Air Handling Unit
111 | Classroom | 312 | 20 |  | 1160 | 26 | 20 | Air Handling Unit
112 | STS Classroom | 449 | 29 |  | 141 | 3 | 3 | Air Handling Unit
113 | Classroom | 280 | 18 |  | 1157 | 26 | 18 | Air Handling Unit
114 | Classroom | 290 | 19 |  | 1418 | 32 | 19 | Air Handling Unit
200 | Classroom | 503 | 33 |  | 761 | 17 | 17 | Univent
201 | Classroom | 369 | 24 |  | 597 | 13 | 13 | Univent
202 | Classroom | 403 | 26 |  | 475 | 10 | 10 | Univent
203 | Classroom | 444 | 29 |  | 772 | 17 | 17 | Univent
204 | Classroom | 285 | 19 |  | 532 | 12 | 12 | Univent
205 | Classroom | 329 | 21 |  | 823 | 18 | 18 | Univent
206 | Classroom | 438 | 29 |  | 480 | 10 | 10 | Univent
207 | Classroom | 108 | 7 | Yes | 648 | 14 | 14 | Univent
208 | Classroom | 352 | 23 |  | 540 | 12 | 12 | Univent
209 | Classroom | 387 | 25 |  | 537 | 12 | 12 | Univent
300 | Classroom | 161 | 10 |  | 789 | 17 | 10 | Univent
301 | Classroom | 313 | 20 |  | 729 | 16 | 16 | Univent
302 | Classroom | 447 | 29 |  | 473 | 10 | 10 | Univent
303 | Classroom | 137 | 9 | Yes | 690 | 15 | 15 | Univent
304 | Classroom | 324 | 21 |  | 667 | 15 | 15 | Univent
305 | Classroom | 321 | 21 |  | 794 | 18 | 18 | Univent
306 | Classroom | 223 | 14 |  | 559 | 12 | 12 | Univent
307 | Classroom | 171 | 11 |  | 790 | 17 | 11 | Univent
308 | Classroom | 265 | 17 |  | 662 | 15 | 15 | Univent
309 | Classroom | 360 | 24 |  | 567 | 12 | 12 | Univent
311 | Classroom | 0 | 0 | Yes | 775 | 17 | 17 | Univent
312 | Classroom | 397 | 26 |  | 573 | 13 | 13 | Univent
- | 2nd & 3rd corridors | 251 | 16 |  |  | 0 | 0 | Air Handling Unit
- | Administration | 637 | 42 |  | 244 | 5 | 5 | Air Handling Unit
- | Auditorium | 2708 | 180 |  | 3216 | 73 | 73 | Air Handling Unit
- | Cafeteria | 2800 | 186 |  | 3216 | 73 | 73 | Air Handling Unit
- | Child Care | 1704 | 113 |  | 1115 | 25 | 25 | Air Handling Unit
- | Conference Office | 98 | 6 |  | 236 | 5 | 5 | Air Handling Unit
- | Copy Room Office | 44 | 2 |  | 178 | 4 | 2 | Air Handling Unit
- | Gym | 0 | 0 |  | 4403 | 100 | 0 | Air Handling Unit
- | IMC |  | 0 | Yes | 1363 | 30 | 30 | Univent
- | Kitchen Make Up | 1547 | 103 |  | 352 | 8 | 8 | Air Handling Unit
- | Main Office | 201 | 13 |  | 244 | 5 | 5 | Air Handling Unit
- | Mrs. Freeland's Office | 30 | 2 |  | 123 | 2 | 2 | Air Handling Unit
- | Music Room | 1406 | 93 |  | 696 | 15 | 15 | Air Handling Unit
- | Nurse's Office | 87 | 5 |  | 412 | 9 | 5 | Air Handling Unit
- | Principal's Office | 65 | 4 |  | 270 | 6 | 4 | Air Handling Unit
- | Vice Principal's Office | 54 | 3 |  | 130 | 2 | 2 | Air Handling Unit
Webster LSH
1 | Classroom | 441 | 29 |  | 971 | 22 | 22 | Blower Coil Unit
2 | Classroom | 189 | 12 | Yes | 1012 | 23 | 23 | Blower Coil Unit
3 | Classroom | 449 | 29 |  | 1016 | 23 | 23 | Blower Coil Unit
4 | Classroom | 195 | 13 | Yes | 1017 | 23 | 23 | Blower Coil Unit
5 | Classroom |  | 0 | Yes | 914 | 20 | 20 | Blower Coil Unit
6 | Classroom |  | 0 | Yes | 1040 | 23 | 23 | Blower Coil Unit
7 | Classroom |  | 0 | Yes | 1003 | 22 | 22 | Blower Coil Unit
8 | Classroom |  | 0 | Yes | 1024 | 23 | 23 | Blower Coil Unit
9 | Classroom | 162 | 10 | Yes | 975 | 22 | 22 | Blower Coil Unit
10 | Classroom | 164 | 10 | Yes | 982 | 22 | 22 | Blower Coil Unit
11 | Classroom | 188 | 12 | Yes | 1012 | 23 | 23 | Blower Coil Unit
- | Student Toilets | 171 | 11 |  | 292 | 6 | 6 | Blower Coil Unit
- | Custodial Closet |  | 0 |  | 58 | 1 | 0 | Fan Coil Unit
- | Faculty Room |  | 0 |  | 156 | 3 | 0 | Fan Coil Unit
- | Multi Purpose Room | 2361 | 157 |  | 1714 | 38 | 38 | Blower Coil Unit
- | Office Area | 409 | 27 |  | 274 | 6 | 6 | Blower Coil Unit
- | Staff Toilets |  | 0 |  | 58 | 1 | 0 | Blower Coil Unit
- | Storage & Closet |  | 0 |  | 200 | 4 | 0 | Blower Coil Unit

## Welsh
Sheet Last Modified: | 2021-04-13
School: | John Welsh Elementary School
Vendor: | Devine Brothers | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 573 | 38 |  | 1122 | 25 | 25 | Univent
102 | Classroom | 641 | 42 |  | 1030 | 23 | 23 | Univent
103 | Classroom | 311 | 20 |  | 650 | 14 | 14 | Univent
104 | Faculty Lounge | 774 | 51 |  | 750 | 17 | 17 | Univent
105 | Classroom | 307 | 20 |  | 586 | 13 | 13 | Univent
106 | Classroom | 674 | 44 |  | 760 | 17 | 17 | Univent
200 | Classroom | 301 | 20 |  | 825 | 18 | 18 | Univent
201 | Classroom | 336 | 22 |  | 825 | 18 | 18 | Univent
202 | Classroom | 333 | 22 |  | 825 | 18 | 18 | Univent
203 | Classroom | 574 | 38 |  | 825 | 18 | 18 | Univent
204 | Classroom | 356 | 23 |  | 825 | 18 | 18 | Univent
205 | Classroom | 380 | 25 |  | 825 | 18 | 18 | Univent
206 | Classroom | 405 | 27 |  | 825 | 18 | 18 | Univent
209 | Classroom | 330 | 22 |  | 825 | 18 | 18 | Univent
210 | Library | 642 | 42 |  | 1218 | 27 | 27 | Univent
211 | Classroom | 320 | 21 |  | 825 | 18 | 18 | Univent
212 | Classroom | 610 | 40 |  | 825 | 18 | 18 | Univent
300 | Classroom | 858 | 57 |  | 830 | 18 | 18 | Univent
301A | Classroom | 341 | 22 |  | 393 | 8 | 8 | Univent
301B | Classroom |  | 0 | Yes | 393 | 8 | 8 | Univent
302 | Classroom | 887 | 59 |  | 830 | 18 | 18 | Univent
303 | Classroom | 341 | 22 |  | 830 | 18 | 18 | Univent
304 | Classroom | 790 | 52 |  | 830 | 18 | 18 | Univent
305 | Classroom | 885 | 59 |  | 830 | 18 | 18 | Univent
306 | Classroom | 590 | 39 |  | 423 | 9 | 9 | Univent
308 | Classroom | 420 | 28 |  | 411 | 9 | 9 | Univent
309 | Classroom | 454 | 30 |  | 830 | 18 | 18 | Univent
310 | Classroom | 705 | 47 |  | 830 | 18 | 18 | Univent
311 | Classroom | 890 | 59 |  | 830 | 18 | 18 | Univent
312 | Classroom | 798 | 53 |  | 830 | 18 | 18 | Univent
400 | Classroom | 346 | 23 |  | 825 | 18 | 18 | Univent
401 | Classroom | 874 | 58 |  | 825 | 18 | 18 | Univent
402 | Classroom | 801 | 53 |  | 825 | 18 | 18 | Univent
403 | Classroom | 852 | 56 |  | 825 | 18 | 18 | Univent
404 | Classroom | 368 | 24 |  | 825 | 18 | 18 | Univent
405 | Classroom | 820 | 54 |  | 825 | 18 | 18 | Univent
406 | Classroom | 328 | 21 |  | 425 | 9 | 9 | Univent
408 | Classroom | 426 | 28 |  | 410 | 9 | 9 | Univent
409 | Classroom | 417 | 27 |  | 825 | 18 | 18 | Univent
410 | Classroom | 558 | 37 |  | 825 | 18 | 18 | Univent
411 | Classroom | 897 | 59 |  | 825 | 18 | 18 | Univent
412 | Classroom | 0 | 0 |  | 403 | 9 | 0 | Univent
412A | Classroom | 820 | 54 |  | 403 | 9 | 9 | Univent
- | Main Office | 438 | 29 |  | 1038 | 23 | 23 | Univent
- | Auditorium | 0 | 0 |  | 3868 | 87 | 0 | Air Handling Unit
- | Gym | 4931 | 328 |  | 3509 | 79 | 79 | Air Handling Unit

## West Phila HS
Sheet Last Modified: | 2021-04-30
School: | New West Philadelphia High School
Vendor: | Chadwick
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
107 | Nurse Office |  | 0 |  | 264 | 6 | 0 | Air Handing Unit
107A | Nurse Exam Room |  | 0 |  | 149 | 3 | 0 | Air Handing Unit
107B | Nurse Suite |  | 0 |  | 100 | 2 | 0 | Air Handing Unit
107C | Nurse Suite |  | 0 |  | 110 | 2 | 0 | Air Handing Unit
101C | Maker Room |  | 0 | Yes | 1268 | 28 | 28 | Air Handing Unit
200 | - | 145 | 9 |  | 875 | 19 | 9 | Univent
201 | Classroom | 190 | 12 |  | 539 | 12 | 12 | Univent
202 | - | 308 | 20 |  | 895 | 20 | 20 | Univent
203 | - | 165 | 11 |  | 899 | 20 | 11 | Univent
204 | - | 398 | 26 |  | 900 | 20 | 20 | Univent
205 | - | 105 | 7 |  | 877 | 19 | 7 | Univent
206 | - | 344 | 22 |  | 898 | 20 | 20 | Univent
207 | - | 315 | 21 |  | 877 | 19 | 19 | Univent
208 | - | 281 | 18 |  | 937 | 21 | 18 | Univent
216 | - | 176 | 11 |  | 1330 | 30 | 11 | Univent
300 | - | 210 | 14 |  | 878 | 19 | 14 | Univent
301 | - | 0 | 0 |  | 544 | 12 | 0 | Univent
302 | - | 470 | 31 |  | 898 | 20 | 20 | Univent
303 | - | 205 | 13 |  | 900 | 20 | 13 | Univent
304 | - | 235 | 15 |  | 900 | 20 | 15 | Univent
305 | - |  | 0 |  | 874 | 19 | 0 | Univent
306 | - | 190 | 12 |  | 896 | 20 | 12 | Univent
307 | Classroom |  | 0 | Yes | 1387 | 31 | 31 | Univent
308 | - | 230 | 15 |  | 897 | 20 | 15 | Univent
309 | Classroom |  | 0 | Yes | 1357 | 30 | 30 | Univent
310 | - | 115 | 7 |  | 898 | 20 | 7 | Univent
311 | - |  | 0 |  | 900 | 20 | 0 | Univent
312 | - | 625 | 41 |  | 872 | 19 | 19 | Univent
313 | - |  | 0 |  | 877 | 19 | 0 | Univent
315 | - | 425 | 28 |  | 876 | 19 | 19 | Univent
316 | - | 190 | 12 |  | 399 | 9 | 9 | Univent
317 | - | 205 | 13 |  | 902 | 20 | 13 | Univent
318 | - | 365 | 24 |  | 1274 | 28 | 24 | Univent
319 | - | 195 | 13 |  | 899 | 20 | 13 | Univent
320 | - |  | 0 |  | 876 | 19 | 0 | Univent
321 | - | 425 | 28 |  | 894 | 20 | 20 | Univent
Gymnasium | Gymnasium | 0 | 0 |  | 6370 | 144 | 0 | Univent
Gymnasium | Gymnasium | 0 | 0 | Yes | 10648 | 242 | 242 | Univent

## Widener
Sheet Last Modified: | 2021-04-13
School: | Widener Memorial Elementary School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
2 | - | 1283 | 85 |  | 2800 | 63 | 63 | Carrier / Perimeter Heater
3 | - | 500 | 33 |  | 1344 | 30 | 30 | Carrier / Perimeter Heater
4 | - | 70 | 4 |  | 1332 | 30 | 4 | Carrier / Perimeter Heater
5 | - | 146 | 9 |  | 527 | 11 | 9 | Carrier / Perimeter Heater
6 | - | 38 | 2 |  | 744 | 16 | 2 | Carrier / Perimeter Heater
7 | - | 70 | 4 |  | 912 | 20 | 4 | Carrier / Perimeter Heater
8 | - | 317 | 21 |  | 460 | 10 | 10 | Carrier / Perimeter Heater
9 | - | 311 | 20 |  | 480 | 10 | 10 | Carrier / Perimeter Heater
10 | - | 291 | 19 |  | 504 | 11 | 11 | Carrier / Perimeter Heater
11 | - | 290 | 19 |  | 504 | 11 | 11 | Carrier / Perimeter Heater
12 | - | 292 | 19 |  | 744 | 16 | 16 | Carrier / Perimeter Heater
13 | - | 210 | 14 |  | 759.5 | 17 | 14 | Carrier / Perimeter Heater
14 | - | 244 | 16 |  | 759.5 | 17 | 16 | Carrier / Perimeter Heater
15 | - | 224 | 14 |  | 759.5 | 17 | 14 | Carrier / Perimeter Heater
16 | - | 225 | 15 |  | 759.5 | 17 | 15 | Carrier / Perimeter Heater
17 | - | 260 | 17 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater
18 | - | 304 | 20 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater
19 | - | 0 | 0 | Yes | 759.5 | 17 | 17 | Carrier / Perimeter Heater
20 | - | 356 | 23 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater
21 | - | 271 | 18 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater
22 | - | 282 | 18 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater
23 | - | 275 | 18 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater
24 | - | 0 | 0 | Yes | 759.5 | 17 | 17 | Carrier / Perimeter Heater
25 | - | 192 | 12 |  | 1014 | 23 | 12 | Carrier / Perimeter Heater
26 | - | 2008 | 133 |  | 891 | 20 | 20 | Air Handling Unit
27 | - | 416 | 27 |  | 619.5 | 14 | 14 | Air Handling Unit
28 | - | 416 | 27 |  | 925 | 21 | 21 | Air Handling Unit
31A | - | 0 | 0 | Yes | 190 | 4 | 4 | Carrier / Perimeter Heater
31B | Nurse's Office | 0 | 0 | Yes | 196 | 4 | 4 | Carrier / Perimeter Heater
32 | - | 0 | 0 |  | 272 | 6 | 0 | Carrier / Perimeter Heater
33 | - | 396 | 26 |  | 1271 | 28 | 26 | Carrier / Perimeter Heater
34 | - | 622 | 41 |  | 1470 | 33 | 33 | Carrier / Perimeter Heater
35A | - | 265 | 17 |  | 720 | 16 | 16 | Carrier / Perimeter Heater
35B | - | 222 | 14 |  | 1107 | 25 | 14 | Carrier / Perimeter Heater
35C | - | 0 | 0 | Yes | 364 | 8 | 8 | Carrier / Perimeter Heater
36 | - | 0 | 0 |  | 1288 | 29 | 0 | Carrier / Perimeter Heater
37 | - | 235 | 15 |  | 600 | 13 | 13 | Carrier / Perimeter Heater
38 | - | 257 | 17 |  | 600 | 13 | 13 | Carrier / Perimeter Heater
39 | - | 88 | 5 |  | 462 | 10 | 5 | Carrier / Perimeter Heater
40 | - | 115 | 7 |  | 472 | 10 | 7 | Carrier / Perimeter Heater
41 | - | 235 | 15 |  | 702 | 15 | 15 | Carrier / Perimeter Heater
46 | Small Cafeteria | 182 | 12 |  | 1347 | 30 | 12 | Carrier / Perimeter Heater
47 | - | 75 | 5 | Yes | 315 | 7 | 7 | Carrier / Perimeter Heater
48 | - | 90 | 6 |  | 817 | 18 | 6 | Carrier / Perimeter Heater
103 | - | 290 | 19 |  | 840 | 19 | 19 | Carrier / Perimeter Heater
104 | - | 310 | 20 |  | 840 | 19 | 19 | Carrier / Perimeter Heater
105 | - | 410 | 27 |  | 810 | 18 | 18 | Carrier / Perimeter Heater
106 | - | 300 | 20 |  | 868 | 19 | 19 | Carrier / Perimeter Heater
107 | - | 530 | 35 |  | 850 | 19 | 19 | Carrier / Perimeter Heater
108 | - | 489 | 32 |  | 840 | 19 | 19 | Carrier / Perimeter Heater
109 | - | 40 | 2 | Yes | 840 | 19 | 19 | Carrier / Perimeter Heater
110 | - | 550 | 36 |  | 840 | 19 | 19 | Carrier / Perimeter Heater
101 | - | 430 | 28 |  | 1271 | 28 | 28 | Carrier / Perimeter Heater
102A | - | 124 | 8 |  | 140 | 3 | 3 | Carrier / Perimeter Heater
102B | - | 165 | 11 |  | 140 | 3 | 3 | Carrier / Perimeter Heater
111A | - | 98 | 6 |  | 140 | 3 | 3 | Carrier / Perimeter Heater
111B | - | 110 | 7 |  | 140 | 3 | 3 | Carrier / Perimeter Heater
112 | - | 905 | 60 |  | 1271 | 28 | 28 | Carrier / Perimeter Heater
- | Auditorium | 1042 | 69 |  | 4087 | 92 | 69 | Air Handling Unit
- | Cafeteria | 918 | 61 |  | 2720 | 61 | 61 | Carrier / Perimeter Heater
- | Computer Lab | 320 | 21 | Yes | 943 | 21 | 21 | Air Handling Unit
- | Food Service "A & B" | 0 | 0 |  | 1320 | 30 | 0 | Carrier / Perimeter Heater
- | Game Room | 577 | 38 |  | 675 | 15 | 15 | Carrier / Perimeter Heater
- | GYM | 174 | 11 |  | 3721 | 84 | 11 | Air Handling Unit
- | Kitchen | 3011 | 200 |  | 1191 | 27 | 27 | Make-Up Air Unit
- | Music Room | 2765 | 184 |  | 2040 | 46 | 46 | Air Handling Unit
- | Pool | 0 | 0 |  | 7467 | 169 | 0 | Air Handling Unit

## Willard
Sheet Last Modified: | 2021-04-30
School: | Frances E. Willard Elementary School
Vendor: | Devine | Main Building Retest
School: | Willard Annex
Vendor: | EMCOR Fluidics | EMCOR Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Willard Main Building
100A | OFFICE | 39 | 2 |  | 181 | 4 | 2 | Air Handling Unit
100B | OFFICE | 31 | 2 |  | 121 | 2 | 2 | Air Handling Unit
100C | OFFICE | 39 | 2 |  | 43 | 0 | 0 | Air Handling Unit
100D | OFFICE | 37 | 2 |  | 121 | 2 | 2 | Air Handling Unit
100E | OFFICE | 35 | 2 |  | 120 | 2 | 2 | Air Handling Unit
100F | OFFICE | 51 | 3 |  | 345 | 7 | 3 | Air Handling Unit
100G | Conference | 85 | 5 |  | 279 | 6 | 5 | Air Handling Unit
100H | BREAK ROOM | 70 | 4 |  | 145 | 3 | 3 | Air Handling Unit
100I | OFFICE | 76 | 5 |  | 210 | 4 | 4 | Air Handling Unit
101 | Classroom | 310 | 20 |  | 984 | 22 | 20 | Univent and Air Handling Unit
102 | Classroom | 304 | 20 |  | 1059 | 24 | 20 | Univent and Air Handling Unit
103 | Classroom | 321 | 21 |  | 889 | 20 | 20 | Univent and Air Handling Unit
104 | Classroom | 282 | 18 |  | 1086 | 24 | 18 | Univent and Air Handling Unit
105 | Classroom | 295 | 19 |  | 677 | 15 | 15 | Univent and Air Handling Unit
106 | Classroom | 331 | 22 |  | 800 | 18 | 18 | Univent and Air Handling Unit
107 | Nurse OFFICE | 35 | 2 |  | 277 | 6 | 2 | Fan Coil
107A | OFFICE | 45 | 3 |  | 161 | 3 | 3 | Fan Coil
107C | OFFICE | 14 | 0 |  | 150 | 3 | 0 | Air Handling Unit
107D | OFFICE | 26 | 1 |  | 103 | 2 | 1 | Air Handling Unit
107G | COMPUTER LAB | 298 | 19 |  | 1033 | 23 | 19 | Univent
109 | Classroom | 282 | 18 |  | 802 | 18 | 18 | Univent and Air Handling Unit
110 | Classroom | 282 | 18 |  | 818 | 18 | 18 | Univent and Air Handling Unit
111 | Classroom | 295 | 19 |  | 818 | 18 | 18 | Univent and Air Handling Unit
112 | Classroom | 306 | 20 |  | 813 | 18 | 18 | Univent and Air Handling Unit
113 | Classroom | 305 | 20 |  | 813 | 18 | 18 | Univent and Air Handling Unit
114 | Classroom | 280 | 18 |  | 815 | 18 | 18 | Univent and Air Handling Unit
115 | Classroom | 293 | 19 |  | 815 | 18 | 18 | Univent and Air Handling Unit
116 | Classroom | 302 | 20 |  | 813 | 18 | 18 | Univent and Air Handling Unit
117 | Classroom | 295 | 19 |  | 813 | 18 | 18 | Univent and Air Handling Unit
121 | Classroom | 381 | 25 |  | 1059 | 24 | 24 | Univent and Air Handling Unit
122 | Music Room | 328 | 21 |  | 1189 | 27 | 21 | Univent
123 | Classroom | 392 | 26 |  | 1061 | 24 | 24 | Univent and Air Handling Unit
126 | Staff Lounge | 397 | 26 |  | 419 | 9 | 9 | Univent and Air Handling Unit
128 | Workroom | 154 | 10 |  | 285 | 6 | 6 | Air Handling Unit
132 | BE Office | 78 | 5 |  | 135 | 3 | 3 | Air Handling Unit
200E | IMC | 60 | 4 |  | 80 | 1 | 1 | Air Handling Unit
200F | CONF ROOM | 325 | 21 |  | 352 | 8 | 8 | Univent
201 | Classsroom | 425 | 28 |  | 814 | 18 | 18 | Univent and Air Handling Unit
202 | Classsroom | 530 | 35 |  | 814 | 18 | 18 | Univent and Air Handling Unit
203 | Classsroom | 394 | 26 |  | 814 | 18 | 18 | Univent and Air Handling Unit
204 | Classsroom | 517 | 34 |  | 814 | 18 | 18 | Univent and Air Handling Unit
205 | Classsroom | 432 | 28 |  | 810 | 18 | 18 | Univent and Air Handling Unit
206 | Classsroom | 407 | 27 |  | 812 | 18 | 18 | Univent and Air Handling Unit
207 | Classsroom | 368 | 24 |  | 685 | 15 | 15 | Univent and Air Handling Unit
208 | ART | 479 | 31 |  | 1059 | 24 | 24 | Univent
209 | Classsroom | 379 | 25 |  | 807 | 18 | 18 | Univent and Air Handling Unit
210 | Classsroom | 382 | 25 |  | 820 | 18 | 18 | Univent and Air Handling Unit
211 | Classsroom | 389 | 25 |  | 821 | 18 | 18 | Univent and Air Handling Unit
212 | Classsroom | 375 | 25 |  | 814 | 18 | 18 | Univent and Air Handling Unit
213 | Classsroom | 392 | 26 |  | 814 | 18 | 18 | Univent and Air Handling Unit
214 | Classsroom | 382 | 25 |  | 811 | 18 | 18 | Univent and Air Handling Unit
215 | Classsroom | 420 | 28 |  | 811 | 18 | 18 | Univent and Air Handling Unit
216 | Classsroom | 301 | 20 |  | 811 | 18 | 18 | Univent and Air Handling Unit
217 | Classsroom | 411 | 27 |  | 811 | 18 | 18 | Univent and Air Handling Unit
221 | Classroom | 301 | 20 |  | 658 | 14 | 14 | Univent
223 | Classroom | 357 | 23 |  | 887 | 20 | 20 | Univent and Air Handling Unit
224 | Classroom | 585 | 39 |  | 1410 | 32 | 32 | Univent and Air Handling Unit
225 | Classroom | 175 | 11 |  | 1267 | 28 | 11 | Univent and Air Handling Unit
- | Auditorium | 3411 | 227 |  | 2755 | 62 | 62 | Air Handling Unit
- | Cafeteria | 2559 | 170 |  | 5041 | 114 | 114 | Air Handling Unit
- | Gym | 2627 | 175 |  | 5960 | 135 | 135 | Air Handling Unit
- | LIBRARY | 514 | 34 |  | 2639 | 59 | 34 | Air Handling Unit
- | Lobby | 1166 | 77 |  | 3402 | 77 | 77 | Air Handling Unit
- | Main Office | 236 | 15 |  | 1165 | 26 | 15 | Air Handling Unit
Willard Annex
#1 | Classroom | 334 | 22 |  | 828 | 18 | 18 | Rooftop Unit
#2 | Classroom | 534 | 35 |  | 828 | 18 | 18 | Rooftop Unit
#3 | Classroom | 667 | 44 |  | 828 | 18 | 18 | Rooftop Unit
#4 | Classroom | 595 | 39 |  | 828 | 18 | 18 | Rooftop Unit
#5 | Classroom | 453 | 30 |  | 828 | 18 | 18 | Rooftop Unit
#6 | Classroom | 1118 | 74 |  | 828 | 18 | 18 | Rooftop Unit
- | Admin Desk/Office | 402 | 26 |  | 180 | 4 | 4 | Rooftop Unit
- | Entrance Hallway | 93 | 6 |  | N/A | 0 | 0 | Rooftop Unit
- | Kitchen | 123 | 8 |  | 180 | 4 | 4 | Rooftop Unit
- | Office Space | 29 | 1 |  | 200 | 4 | 1 | Rooftop Unit
- | Play Area | 2452 | 163 |  | 1228 | 27 | 27 | Rooftop Unit
- | Principals Office | 257 | 17 |  | 120 | 2 | 2 | Rooftop Unit
- | BE Office | 362 | 24 |  | 195 | 4 | 4 | Rooftop Unit
- | Health/Teachers Lounge | 0 | 0 |  | 240 | 5 | 0 | Univent

## Wilson
Sheet Last Modified: | 2021-04-30
School: | Woodrow Wilson Middle School
Vendor: | Capital
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 693 | 46 |  | 1080 | 24 | 24 | Air Handling Unit
102 | Classroom | 429 | 28 |  | 853 | 19 | 19 | Air Handling Unit
103 | Classroom | 962 | 64 |  | 672 | 15 | 15 | Air Handling Unit
104 | Room |  | 0 |  | 616 | 14 | 0 | Air Handling Unit
105 | Classroom | 540 | 36 |  | 1038 | 23 | 23 | Air Handling Unit
107 | Classroom | 882 | 58 |  | 968 | 22 | 22 | Air Handling Unit
108 | Room |  | 0 |  | 352 | 8 | 0 | Air Handling Unit
109 | Classroom | 506 | 33 |  | 374 | 8 | 8 | Air Handling Unit
110 | Room |  | 0 |  | 660 | 15 | 0 | Air Handling Unit
111 | Classroom | 277 | 18 |  | 812 | 18 | 18 | Air Handling Unit
112 | Classroom | 271 | 18 |  | 954 | 21 | 18 | Air Handling Unit
116 | Classroom | 143 | 9 |  | 697 | 15 | 9 | Air Handling Unit
117 | Classroom | 191 | 12 |  | 697 | 15 | 12 | Air Handling Unit
118 | Classroom | 146 | 9 |  | 697 | 15 | 9 | Air Handling Unit
119 | Classroom | 98 | 6 |  | 349 | 7 | 6 | Air Handling Unit
201 | Classroom | 0 | 0 | Yes | 727 | 16 | 16 | Air Handling Unit
202 | Classroom | 338 | 22 |  | 687 | 15 | 15 | Air Handling Unit
203 | Classroom | 451 | 30 |  | 726 | 16 | 16 | Air Handling Unit
204 | Office |  | 0 | Yes | 160 | 3 | 3 | Air Handling Unit
205 | Classroom | 311 | 20 |  | 348 | 7 | 7 | Air Handling Unit
206 | Classroom | 452 | 30 |  | 324 | 7 | 7 | Air Handling Unit
207 | Room |  | 0 |  | 308 | 7 | 0 | Air Handling Unit
208-C | Main Office |  | 0 |  | 572 | 13 | 0 | Air Handling Unit
209 | Classroom | 765 | 51 |  | 901 | 20 | 20 | Air Handling Unit
210 | Classroom | 394 | 26 |  | 1034 | 23 | 23 | Air Handling Unit
211 | Classroom | 356 | 23 |  | 849 | 19 | 19 | Air Handling Unit
212 | Classroom | 318 | 21 |  | 867 | 19 | 19 | Air Handling Unit
213 | Classroom | 213 | 14 |  | 687 | 15 | 14 | Air Handling Unit
214 | Classroom | 596 | 39 |  | 727 | 16 | 16 | Air Handling Unit
215 | Classroom | 1059 | 70 |  | 668 | 15 | 15 | Air Handling Unit
216 | Classroom | 1311 | 87 |  | 791 | 17 | 17 | Air Handling Unit
217 | Classroom | 1097 | 73 |  | 682 | 15 | 15 | Air Handling Unit
218 | Classroom | 810 | 54 |  | 702 | 15 | 15 | Air Handling Unit
219 | Classroom | 1352 | 90 |  | 700 | 15 | 15 | Air Handling Unit
220 | Classroom | 1207 | 80 |  | 682 | 15 | 15 | Air Handling Unit
221 | Classroom | 897 | 59 |  | 791 | 17 | 17 | Air Handling Unit
222 | Classroom | 608 | 40 |  | 668 | 15 | 15 | Air Handling Unit
223 | Classroom | 305 | 20 |  | 347 | 7 | 7 | Air Handling Unit
224 | Room |  | 0 |  | 308 | 7 | 0 | Air Handling Unit
226 | Classroom | 86 | 5 |  | 216 | 4 | 4 | Air Handling Unit
227 | Classroom | 163 | 10 |  | 347 | 7 | 7 | Air Handling Unit
228 | Classroom | 208 | 13 |  | 694 | 15 | 13 | Air Handling Unit
245 | Room |  | 0 | Yes | 87 | 1 | 1 | Air Handling Unit
246 | Room |  | 0 | Yes | 82 | 1 | 1 | Air Handling Unit
247 | Room |  | 0 | Yes | 110 | 2 | 2 | Air Handling Unit
301 | Classroom | 813 | 54 |  | 727 | 16 | 16 | Air Handling Unit
302 | Classroom | 439 | 29 |  | 684 | 15 | 15 | Air Handling Unit
303 | Classroom | 605 | 40 |  | 697 | 15 | 15 | Air Handling Unit
304 | Classroom | 552 | 36 |  | 972 | 22 | 22 | Air Handling Unit
305 | Classroom | 518 | 34 |  | 914 | 20 | 20 | Air Handling Unit
306 | Classroom | 497 | 33 |  | 898 | 20 | 20 | Air Handling Unit
307 | Classroom | 781 | 52 |  | 965 | 21 | 21 | Air Handling Unit
308 | Classroom | 466 | 31 |  | 833 | 18 | 18 | Air Handling Unit
309 | Classroom | 735 | 49 |  | 894 | 20 | 20 | Air Handling Unit
309-A | Room |  | 0 |  | 220 | 5 | 0 | Air Handling Unit
310 | Classroom | 765 | 51 |  | 924 | 21 | 21 | Air Handling Unit
311 | Classroom | 1322 | 88 |  | 958 | 21 | 21 | Air Handling Unit
312 | Classroom | 660 | 44 |  | 728 | 16 | 16 | Air Handling Unit
313 | Classroom | 403 | 26 |  | 313 | 7 | 7 | Air Handling Unit
1900-11-09 | Classroom | 1020 | 68 |  | 314 | 7 | 7 | Air Handling Unit
315 | Classroom | 1082 | 72 |  | 668 | 15 | 15 | Air Handling Unit
316 | Classroom | 1750 | 116 |  | 791 | 17 | 17 | Air Handling Unit
317 | Classroom | 2057 | 137 |  | 685 | 15 | 15 | Air Handling Unit
318 | Classroom | 1824 | 121 |  | 699 | 15 | 15 | Air Handling Unit
319 | Classroom | 1263 | 84 |  | 699 | 15 | 15 | Air Handling Unit
320 | Classroom | 642 | 42 |  | 684 | 15 | 15 | Air Handling Unit
321 | Classroom | 658 | 43 |  | 791 | 17 | 17 | Air Handling Unit
322 | Classroom | 508 | 33 |  | 668 | 15 | 15 | Air Handling Unit
323 | Classroom | 282 | 18 |  | 347 | 7 | 7 | Air Handling Unit
324 | Classroom | 127 | 8 |  | 694 | 15 | 8 | Air Handling Unit
327 | Room |  | 0 |  | 264 | 6 | 0 | Air Handling Unit
328 | Classroom | 107 | 7 |  | 694 | 15 | 7 | Air Handling Unit
401 | Room |  | 0 |  | 264 | 6 | 0 | Rooftop Unit
401A | Room |  | 0 |  | 572 | 13 | 0 | Rooftop Unit
402 | Room |  | 0 |  | 836 | 19 | 0 | Rooftop Unit
403 | Room |  | 0 |  | 1056 | 24 | 0 | Rooftop Unit
404 | Room |  | 0 |  | 1188 | 27 | 0 | Rooftop Unit
406 | Room |  | 0 |  | 44 | 1 | 0 | Rooftop Unit
407 | Room |  | 0 |  | 44 | 1 | 0 | Rooftop Unit
408 | Room |  | 0 |  | 44 | 1 | 0 | Rooftop Unit
409 | Room |  | 0 |  | 132 | 3 | 0 | Rooftop Unit
410 | Counselor's Office |  | 0 | Yes | 165 | 3 | 3 | Rooftop Unit
- | Auditorium |  | 0 |  | 3740 | 85 | 0 | Air Handling Unit
- | Gym 1 |  | 0 |  | 2816 | 64 | 0 | Air Handling Unit
- | Gym 2 |  | 0 |  | 2816 | 64 | 0 | Air Handling Unit
- | Lunchroom 1 |  | 0 |  | 2640 | 60 | 0 | Air Handling Unit
- | Lunchroom 2 |  | 0 |  | 2596 | 59 | 0 | Air Handling Unit

## Wister
Sheet Last Modified: | 2021-03-29
School: | Wister Elementary School
Vendor: | Mastery Charter Property Management
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 307 | 20 |  |  | 0 | 0 | Unit Ventilator
101 | Classroom | 319 | 21 |  |  | 0 | 0 | Unit Ventilator
103 | Classroom | 148 | 9 |  |  | 0 | 0 | Unit Ventilator
106 | Lounge | 202 | 13 |  |  | 0 | 0 | Unit Ventilator
107A | Main Office | 0 | 0 |  |  | 0 | 0 | Unit Ventilator
108 | Classroom | 316 | 21 |  | 1134 | 25 | 21 | Unit Ventilator
109 | Classroom | 313 | 20 |  | 1094 | 24 | 20 | Unit Ventilator
110 | Storage | 215 | 14 |  |  | 0 | 0 | Unit Ventilator
111 | Classroom | 339 | 22 |  | 1414 | 32 | 22 | Unit Ventilator
200 | Classroom | 309 | 20 |  |  | 0 | 0 | Unit Ventilator
201 | Office | 162 | 10 |  |  | 0 | 0 | Unit Ventilator
202 | Classroom | 138 | 9 |  |  | 0 | 0 | Unit Ventilator
203 | Classroom | 311 | 20 |  |  | 0 | 0 | Unit Ventilator
204 | Classroom | 271 | 18 |  |  | 0 | 0 | Unit Ventilator
205 | Classroom | 144 | 9 |  |  | 0 | 0 | Unit Ventilator
206 | Classroom | 304 | 20 |  |  | 0 | 0 | Unit Ventilator
207 | Classroom | 304 | 20 |  |  | 0 | 0 | Unit Ventilator
208 | Classroom | 308 | 20 |  |  | 0 | 0 | Unit Ventilator
209C | Classroom | 337 | 22 |  |  | 0 | 0 | Unit Ventilator
210 | Classroom | 319 | 21 |  |  | 0 | 0 | Unit Ventilator
211 | Classroom | 302 | 20 |  |  | 0 | 0 | Unit Ventilator
212 | Classroom | 313 | 20 |  |  | 0 | 0 | Unit Ventilator
213 | Classroom | 331 | 22 |  |  | 0 | 0 | Unit Ventilator
214 | Classroom | 349 | 23 |  |  | 0 | 0 | Unit Ventilator
300 | Classroom | 299 | 19 |  |  | 0 | 0 | Unit Ventilator
301 | Office | 129 | 8 |  |  | 0 | 0 | Unit Ventilator
302 | Classroom | 153 | 10 |  |  | 0 | 0 | Unit Ventilator
303 | Classroom | 308 | 20 |  |  | 0 | 0 | Unit Ventilator
304 | Classroom | 330 | 22 |  |  | 0 | 0 | Unit Ventilator
305 | Classroom | 332 | 22 |  |  | 0 | 0 | Unit Ventilator
306 | Classroom | 311 | 20 |  |  | 0 | 0 | Unit Ventilator
307 | Classroom | 312 | 20 |  |  | 0 | 0 | Unit Ventilator
- | Auditorium | 2036 | 135 |  |  | 0 | 0 | AHU
- | Gym | 1544 | 102 |  |  | 0 | 0 | AHU

## Workshop School
Sheet Last Modified: | 2021-03-17
School: | Sustainability Workshop School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Corridor | 7 | 0 |  | 533 | 12 | 0 | VAV
102 | Closet | 6 | 0 |  | 45 | 1 | 0 | VAV
105 | Nurses Office / Classroom |  | 0 |  | 150 | 3 | 0 | HU
106 | Woodshop | 43 | 2 |  | 1003 | 22 | 2 | HU
110 | Classroom | 23 | 1 |  | 884 | 20 | 1 | VAV
111 | Auto Service | 0 | 0 |  | 1761 | 40 | 0 | HU and Univent
111 | Classroom |  | 0 |  | 756 | 17 | 0 | Univent
112 | Training Classroom | 0 | 0 |  | 459 | 10 | 0 | HU and Univent
114 | Tool Storage | 0 | 0 |  | 450 | 10 | 0 | HU and Univent
117 | Body Shop | 0 | 0 |  | 2944 | 66 | 0 | HU
121 | Classroom |  | 0 |  | 729 | 16 | 0 | Univent
200 | Corridor | 33 | 2 |  | 1868 | 42 | 2 | VAV
201 | Classroom | 42 | 2 |  | 740 | 16 | 2 | VAV
206 | Main Office | 7 | 0 |  | 234 | 5 | 0 | VAV
207 | Office | 6 | 0 |  | 192 | 4 | 0 | VAV
208 | Principle Office | 5 | 0 |  | 80 | 1 | 0 | VAV
209 | Copy Room | 12 | 0 |  | 132 | 3 | 0 | VAV
210 | Classroom | 25 | 1 |  | 748 | 17 | 1 | VAV
210-C | Counselors office in front of classroom 210 | 2 | 0 |  | NA | 0 | 0 | VAV
212 | Mechanical room |  | 0 |  | 620 | 14 | 0 | AHU
212 | Classroom | 366 | 24 |  | 720 | 16 | 16 | VAV
213 | Classroom | 1829 | 121 |  | 691 | 15 | 15 | VAV
214 | Classroom | 837 | 55 |  | 761 | 17 | 17 | VAV
215 | Classroom | 839 | 55 |  | 961 | 21 | 21 | VAV
215A | Classroom | 96 | 6 |  | NA | 0 | 0 | VAV
216 | Classroom | 655 | 43 |  | 1012 | 23 | 23 | VAV
219 | Corridor Bathroom | 40 | 2 |  | 48 | 1 | 1 | VAV
- | Automotive Classroom | 0 | 0 |  | NA | 0 | 0 | HU and Univent
- | Body Shop Classroom | 0 | 0 |  | NA | 0 | 0 | Univent
- | Cafeteria Bathroom | 41 | 2 |  | 49 | 1 | 1 | VAV
- | Cafeteria | 402 | 26 |  | 2550 | 57 | 26 | RTU
- | Computer Lab | 60 | 4 |  | 312 | 7 | 4 | HU
- | Kitchen | 0 | 0 |  | 504 | 11 | 0 | MUA
- | Mr. Boyd Office | 185 | 12 |  | 152 | 3 | 3 | VAV and RETURN DUCT
- | Mr. Tobias Office | 185 | 12 |  | 80 | 1 | 1 | VAV
- | Mrs. Walker Office | 138 | 9 |  | 80 | 1 | 1 | VAV
- | Ms. Phoebe Office | 188 | 12 |  | 91 | 2 | 2 | VAV
- | Nurse Room | 0 | 0 |  | NA | 0 | 0 | HU and Univent
- | Storage / Office | 15 | 1 |  | 120 | 2 | 1 | RTU
- | Woodshop Office | 43 | 2 |  | NA | 0 | 0 | HU
- | Woodshop Saw | 24 | 1 |  | NA | 0 | 0 | HU

## Wright
Sheet Last Modified: | 2021-04-30
School: | Richard R. Wright Elementary School
Vendor: | Goldner | Goldner Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Art Room | 280 | 18 | Yes | 1400 | 31 | 31 | Unit Ventilator
108-A | 1st Floor Gymnasium Office | 5 | 0 |  | 100 | 2 | 0 | Air Handling Unit
112-A | 1st Floor Music Practice | 10 | 0 |  | 100 | 2 | 0 | Air Handling Unit
112-B | 1st Floor Music Practice | 19 | 1 |  | 100 | 2 | 1 | Air Handling Unit
114 | Classroom | 334 | 22 | Yes | 1360 | 30 | 30 | Unit Ventilator
115 | Classroom | 358 | 23 | Yes | 1360 | 30 | 30 | Unit Ventilator
118 | Nurse area | 0 | 0 | Yes | 378 | 8 | 8 | Unit Ventilator
119 | Nurse area | 0 | 0 | Yes | 216 | 4 | 4 | Unit Ventilator
120 | Classroom | 273 | 18 | Yes | 1360 | 30 | 30 | Unit Ventilator
121 | Classroom | 435 | 29 |  | 1360 | 30 | 29 | Unit Ventilator
122 | Classroom | 273 | 18 | Yes | 1360 | 30 | 30 | Unit Ventilator
201 | Classroom | 342 | 22 | Yes | 1610 | 36 | 36 | Unit Ventilator
202 | Classroom | 634 | 42 |  | 1702 | 38 | 38 | Unit Ventilator
203 | Classroom | 349 | 23 | Yes | 1120 | 25 | 25 | Unit Ventilator
204 | Classroom | 358 | 23 |  |  | 0 | 0 | Unit Ventilator
205 | Classroom | 482 | 32 |  | 870 | 19 | 19 | Unit Ventilator
206 | Classroom | 499 | 33 |  | 812 | 18 | 18 | Unit Ventilator
207 | Classroom | 460 | 30 |  | 870 | 19 | 19 | Unit Ventilator
208 | Classroom | 232 | 15 | Yes | 841 | 19 | 19 | Unit Ventilator
209 | Classroom | 341 | 22 |  |  | 0 | 0 | Unit Ventilator
210 | Classroom | 413 | 27 |  | 899 | 20 | 20 | Unit Ventilator
211 | Classroom | 270 | 18 | Yes | 1715 | 38 | 38 | Unit Ventilator
212 | Classroom | 434 | 28 | Yes | 1911 | 43 | 43 | Unit Ventilator
213 | Classroom | 310 | 20 | Yes | 1715 | 38 | 38 | Unit Ventilator
214 | Classroom | 799 | 53 |  | 1786 | 40 | 40 | Unit Ventilator
215 | Classroom | 325 | 21 |  | 870 | 19 | 19 | Unit Ventilator
216 | Classroom | 296 | 19 | Yes | 930 | 21 | 21 | Unit Ventilator
217 | Classroom | 568 | 37 |  | 870 | 19 | 19 | Unit Ventilator
218 | Classroom | 415 | 27 |  | 870 | 19 | 19 | Unit Ventilator
219 | Classroom | 289 | 19 |  | 870 | 19 | 19 | Unit Ventilator
220 | Classroom | 278 | 18 |  | 870 | 19 | 18 | Unit Ventilator
221 | Classroom | 339 | 22 |  | 899 | 20 | 20 | Unit Ventilator
222 | Classroom | 372 | 24 |  | 784 | 17 | 17 | Unit Ventilator
223 | Classroom | 369 | 24 | Yes | 1739 | 39 | 39 | Unit Ventilator
224 | Classroom | 284 | 18 | Yes | 1739 | 39 | 39 | Unit Ventilator
225 | Room | 211 | 14 |  | 196 | 4 | 4 | Air Handling Unit
227 | Room | 119 | 7 |  | 196 | 4 | 4 | Air Handling Unit
- | 1st Floor Conference Room | 89 | 5 |  | 108 | 2 |  | Air Handling Unit
- | 1st Floor Counselor's Office | 17 | 1 |  | 100 | 2 |  | Air Handling Unit
- | 1st Floor Engineer's Office | 30 | 2 |  | 36 | 0 |  | Air Handling Unit
- | 1st Floor Entry Hallway | 79 | 5 |  | 140 | 3 |  | Air Handling Unit
- | 1st Floor CSC Office | 4 | 0 |  | 100 | 2 |  | Air Handling Unit
- | 1st Floor IT Room | 10 | 0 |  | 100 | 2 |  | Air Handling Unit
- | 1st Floor Main Office | 98 | 6 |  | 144 | 3 |  | Air Handling Unit
- | 1st Floor Office Storage | 0 | 0 |  | 160 | 3 |  | Air Handling Unit
- | 1st Floor Prinicpal's Office | 23 | 1 |  | 140 | 3 |  | Air Handling Unit
- | 1st Floor Psychologist's Office | 14 | 0 |  | 140 | 3 |  | Air Handling Unit
- | 1st Floor Small Kitchen | 56 | 3 |  | 84 | 1 |  | Air Handling Unit
- | 1st Floor Staff Lounge | 447 | 29 |  | 1556 | 35 | 29 | Unit Ventilator
- | 2nd Floor Computer Storage | 44 | 2 |  | 196 | 4 | 2 | Air Handling Unit
- | 2nd Floor Library | 2489 | 165 |  | 556 | 12 | 12 | Air Handling Unit
- | 2nd Floor Library Lounge | 131 | 8 |  | 192 | 4 | 4 | Air Handling Unit
- | 2nd Floor Library Storage | 109 | 7 |  | 336 | 7 | 7 | Air Handling Unit
- | 2nd Floor Office space | 250 | 16 |  | 216 | 4 | 4 | Unit Ventilator
- | 2nd Floor Storage space | 358 | 23 |  | 432 | 9 | 9 | Unit Ventilator
- | Cafetorium | 4622 | 308 |  | 4730 | 107 | 107 | Air Handling Unit
- | Gym | 890 | 59 |  | 5644 | 128 | 59 | Air Handling Unit

## Ziegler
Sheet Last Modified: | 2021-05-03
School: | William H. Ziegler Elementary School
Vendor: | Chadwick | Chadwick Part 2 | Chadwick Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
102 | Classroom | 147 | 9 |  | 140 | 3 | 3 | Unit Ventilator
103 | Classroom | 309 | 20 |  | 836 | 19 | 19 | Unit Ventilator
104 | Classroom | 346 | 23 |  | 836 | 19 | 19 | Unit Ventilator
105 | Classroom | 296 | 19 |  | 836 | 19 | 19 | Unit Ventilator
106 | Office/Classroom |  | 0 | Yes | 322 | 7 | 7 | Unit Ventilator
107 | Classroom | 161 | 10 | Yes | 638 | 14 | 14 | Unit Ventilator
108 | Nurse |  | 0 | Yes | 171 | 3 | 3 | Unit Ventilator
109 | Classroom |  | 0 | Yes | 696 | 15 | 15 | Unit Ventilator
111 | Classroom | 331 | 22 |  | 682 | 15 | 15 | Energy Recovery Unit
112 | Classroom | 300 | 20 |  | 682 | 15 | 15 | Energy Recovery Unit
113 | Classroom | 338 | 22 |  | 682 | 15 | 15 | Energy Recovery Unit
114 | Classroom | 301 | 20 |  | 682 | 15 | 15 | Energy Recovery Unit
115 | Classroom | 312 | 20 |  | 682 | 15 | 15 | Energy Recovery Unit
116 | Classroom | 318 | 21 |  | 682 | 15 | 15 | Energy Recovery Unit
117 | Classroom | 318 | 21 |  | 682 | 15 | 15 | Energy Recovery Unit
125 | Classroom | 294 | 19 |  | 600 | 13 | 13 | Energy Recovery Unit
201 | Classroom | 398 | 26 |  | 598 | 13 | 13 | Unit Ventilator
202 | Classroom | 511 | 34 |  | 644 | 14 | 14 | Unit Ventilator
203 | Classroom |  | 0 | Yes | 390 | 8 | 8 | Unit Ventilator
204 | Classroom | 417 | 27 |  | 780 | 17 | 17 | Unit Ventilator
205 | Classroom | 315 | 21 |  | 962 | 21 | 21 | Unit Ventilator
206 | Classroom | 110 | 7 | Yes | 644 | 14 | 14 | Unit Ventilator
207 | Classroom |  | 0 | Yes | 243 | 5 | 5 | Unit Ventilator
208 | Teacher's Lounge |  | 0 | Yes | 280 | 6 | 6 | Unit Ventilator
210 | Classroom | 147 | 9 | Yes | 644 | 14 | 14 | Unit Ventilator
212 | Classroom | 534 | 35 |  | 667 | 15 | 15 | Unit Ventilator
213 | Classroom | 332 | 22 |  | 682 | 15 | 15 | Energy Recovery Unit
214 | Classroom | 166 | 11 | Yes | 682 | 15 | 15 | Energy Recovery Unit
215 | Classroom | 281 | 18 |  | 682 | 15 | 15 | Energy Recovery Unit
216 | Classroom | 265 | 17 |  | 682 | 15 | 15 | Energy Recovery Unit
217 | Classroom | 261 | 17 |  | 682 | 15 | 15 | Energy Recovery Unit
218 | Classroom | 275 | 18 |  | 682 | 15 | 15 | Energy Recovery Unit
220 | Classroom | 269 | 17 |  | 748 | 17 | 17 | Energy Recovery Unit
- | Cafeteria | 2750 | 183 |  | 2736 | 62 | 62 | Air Handling Unit
- | Gymasium | 1073 | 71 |  | 3498 | 79 | 71 | Air Handling Unit
- | Hallway | 105 | 7 |  |  | 0 | 0 | Air Handling Unit
- | Library/IMC | 983 | 65 |  | 1953 | 44 | 44 | Air Handling Unit
- | Main Office |  | 0 | Yes | 456 | 10 | 10 | Unit Ventilator
- | Principal's Office |  | 0 | Yes | 198 | 4 | 4 | Unit Ventilator
- | Science Lab | 228 | 15 |  | 968 | 22 | 15 | Energy Recovery Unit